## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1703-23_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1703-23_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1703-23_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1703-23_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1703-23_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1703-23_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1703-23_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1703-23_0_5_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1703-23_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1703-23_0_5_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1703-23_0_5_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1703-23_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1703-23_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1703-23_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1703-23_0_5_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1703-23_0_5_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1703-23_0_5_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1703-23_0_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1703-23_0_5_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1703-23_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1703-23_0_5_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1703-23_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1703-23_0_5_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1703-23_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1703-23_0_5_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1703-23_0_5_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1703-23_0_5_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1703-23_0_5_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1703-23_0_5_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1703-23_0_5_node_152 | 0.4 | n |  | TRUE
30 | bus_LV_1703-23_0_5_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1703-23_0_5_node_150 | 0.4 | n |  | TRUE
32 | bus_LV_1703-23_0_5_node_148 | 0.4 | n |  | TRUE
33 | bus_LV_1703-23_0_5_node_151 | 0.4 | n |  | TRUE
34 | bus_LV_1703-23_0_5_node_147 | 0.4 | n |  | TRUE
35 | bus_LV_1703-23_0_5_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_1703-23_0_5_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_1703-23_0_5_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1703-23_0_5_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1703-23_0_5_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_1703-23_0_5_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_1703-23_0_5_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1703-23_0_5_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_1703-23_0_5_node_149 | 0.4 | n |  | TRUE
44 | bus_LV_1703-23_0_5_node_69 | 0.4 | n |  | TRUE
45 | bus_LV_1703-23_0_5_node_68 | 0.4 | n |  | TRUE
46 | bus_LV_1703-23_0_5_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_1703-23_0_5_node_81 | 0.4 | n |  | TRUE
48 | bus_LV_1703-23_0_5_node_83 | 0.4 | n |  | TRUE
49 | bus_LV_1703-23_0_5_node_119 | 0.4 | n |  | TRUE
50 | bus_LV_1703-23_0_5_node_129 | 0.4 | n |  | TRUE
51 | bus_LV_1703-23_0_5_node_84 | 0.4 | n |  | TRUE
52 | bus_LV_1703-23_0_5_node_133 | 0.4 | n |  | TRUE
53 | bus_LV_1703-23_0_5_node_132 | 0.4 | n |  | TRUE
54 | bus_LV_1703-23_0_5_node_67 | 0.4 | n |  | TRUE
55 | bus_LV_1703-23_0_5_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_1703-23_0_5_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_1703-23_0_5_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_1703-23_0_5_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_1703-23_0_5_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_1703-23_0_5_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_1703-23_0_5_node_62 | 0.4 | n |  | TRUE
62 | bus_LV_1703-23_0_5_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_1703-23_0_5_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_1703-23_0_5_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_1703-23_0_5_node_76 | 0.4 | n |  | TRUE
66 | bus_LV_1703-23_0_5_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_1703-23_0_5_node_90 | 0.4 | n |  | TRUE
68 | bus_LV_1703-23_0_5_node_91 | 0.4 | n |  | TRUE
69 | bus_LV_1703-23_0_5_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1703-23_0_5_node_87 | 0.4 | n |  | TRUE
71 | bus_LV_1703-23_0_5_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_1703-23_0_5_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_1703-23_0_5_node_94 | 0.4 | n |  | TRUE
74 | bus_LV_1703-23_0_5_node_93 | 0.4 | n |  | TRUE
75 | bus_LV_1703-23_0_5_node_109 | 0.4 | n |  | TRUE
76 | bus_LV_1703-23_0_5_node_108 | 0.4 | n |  | TRUE
77 | bus_LV_1703-23_0_5_node_115 | 0.4 | n |  | TRUE
78 | bus_LV_1703-23_0_5_node_116 | 0.4 | n |  | TRUE
79 | bus_LV_1703-23_0_5_node_113 | 0.4 | n |  | TRUE
80 | bus_LV_1703-23_0_5_node_112 | 0.4 | n |  | TRUE
81 | bus_LV_1703-23_0_5_node_111 | 0.4 | n |  | TRUE
82 | bus_LV_1703-23_0_5_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_1703-23_0_5_node_86 | 0.4 | n |  | TRUE
84 | bus_LV_1703-23_0_5_node_51 | 0.4 | n |  | TRUE
85 | bus_LV_1703-23_0_5_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_1703-23_0_5_node_54 | 0.4 | n |  | TRUE
87 | bus_LV_1703-23_0_5_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_1703-23_0_5_node_57 | 0.4 | n |  | TRUE
89 | bus_LV_1703-23_0_5_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_1703-23_0_5_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_1703-23_0_5_node_88 | 0.4 | n |  | TRUE
92 | bus_LV_1703-23_0_5_node_89 | 0.4 | n |  | TRUE
93 | bus_LV_1703-23_0_5_node_100 | 0.4 | n |  | TRUE
94 | bus_LV_1703-23_0_5_node_97 | 0.4 | n |  | TRUE
95 | bus_LV_1703-23_0_5_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_1703-23_0_5_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_1703-23_0_5_node_72 | 0.4 | n |  | TRUE
98 | bus_LV_1703-23_0_5_node_73 | 0.4 | n |  | TRUE
99 | bus_LV_1703-23_0_5_node_74 | 0.4 | n |  | TRUE
100 | bus_LV_1703-23_0_5_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_1703-23_0_5_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_1703-23_0_5_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_1703-23_0_5_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_1703-23_0_5_node_120 | 0.4 | n |  | TRUE
105 | bus_LV_1703-23_0_5_node_117 | 0.4 | n |  | TRUE
106 | bus_LV_1703-23_0_5_node_130 | 0.4 | n |  | TRUE
107 | bus_LV_1703-23_0_5_node_142 | 0.4 | n |  | TRUE
108 | bus_LV_1703-23_0_5_node_140 | 0.4 | n |  | TRUE
109 | bus_LV_1703-23_0_5_node_131 | 0.4 | n |  | TRUE
110 | bus_LV_1703-23_0_5_node_114 | 0.4 | n |  | TRUE
111 | bus_LV_1703-23_0_5_node_107 | 0.4 | n |  | TRUE
112 | bus_LV_1703-23_0_5_node_98 | 0.4 | n |  | TRUE
113 | bus_LV_1703-23_0_5_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_1703-23_0_5_node_153 | 0.4 | n |  | TRUE
115 | bus_LV_1703-23_0_5_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_1703-23_0_5_node_105 | 0.4 | n |  | TRUE
117 | bus_LV_1703-23_0_5_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_1703-23_0_5_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_1703-23_0_5_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_1703-23_0_5_node_104 | 0.4 | n |  | TRUE
121 | bus_LV_1703-23_0_5_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_1703-23_0_5_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_1703-23_0_5_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_1703-23_0_5_node_124 | 0.4 | n |  | TRUE
125 | bus_LV_1703-23_0_5_node_125 | 0.4 | n |  | TRUE
126 | bus_LV_1703-23_0_5_node_118 | 0.4 | n |  | TRUE
127 | bus_LV_1703-23_0_5_node_123 | 0.4 | n |  | TRUE
128 | bus_LV_1703-23_0_5_node_127 | 0.4 | n |  | TRUE
129 | bus_LV_1703-23_0_5_node_128 | 0.4 | n |  | TRUE
130 | bus_LV_1703-23_0_5_node_126 | 0.4 | n |  | TRUE
131 | bus_LV_1703-23_0_5_node_134 | 0.4 | n |  | TRUE
132 | bus_LV_1703-23_0_5_node_135 | 0.4 | n |  | TRUE
133 | bus_LV_1703-23_0_5_node_144 | 0.4 | n |  | TRUE
134 | bus_LV_1703-23_0_5_node_141 | 0.4 | n |  | TRUE
135 | bus_LV_1703-23_0_5_node_136 | 0.4 | n |  | TRUE
136 | bus_LV_1703-23_0_5_node_138 | 0.4 | n |  | TRUE
137 | bus_LV_1703-23_0_5_node_137 | 0.4 | n |  | TRUE
138 | bus_LV_1703-23_0_5_node_139 | 0.4 | n |  | TRUE
139 | bus_LV_1703-23_0_5_node_143 | 0.4 | n |  | TRUE
140 | bus_LV_1703-23_0_5_node_145 | 0.4 | n |  | TRUE
141 | bus_LV_1703-23_0_5_node_146 | 0.4 | n |  | TRUE
142 | bus_MV_435_1_node_78 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1703-23_0_5_load_0 | 0 | 0.0021882 | 0.00054842 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1703-23_0_5_load_1 | 1 | 0.00403 | 0.00101 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1703-23_0_5_load_2 | 2 | 0.00087791 | 0.00022003 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1703-23_0_5_load_3 | 3 | 0.0029661 | 0.00074339 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1703-23_0_5_load_4 | 4 | 0.00066776 | 0.00016736 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1703-23_0_5_load_5 | 5 | 0.0016642 | 0.00041708 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1703-23_0_5_load_7 | 6 | 0.0015763 | 0.00039507 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1703-23_0_5_load_6 | 8 | 0.00024748 | 6.2024e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1703-23_0_5_load_28 | 9 | 0.004988 | 0.0012501 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1703-23_0_5_load_10 | 12 | 8.1707e-05 | 2.0478e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1703-23_0_5_load_18 | 15 | 0.00054838 | 0.00013744 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1703-23_0_5_load_25 | 16 | 0.00028955 | 7.2567e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1703-23_0_5_load_22 | 17 | 0.00024557 | 6.1545e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1703-23_0_5_load_19 | 18 | 0.00043795 | 0.00010976 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1703-23_0_5_load_11 | 19 | 0.00072509 | 0.00018173 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1703-23_0_5_load_12 | 20 | 0.0015235 | 0.00038182 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1703-23_0_5_load_14 | 21 | 0.0002887 | 7.2354e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1703-23_0_5_load_15 | 22 | 0.00025972 | 6.5091e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1703-23_0_5_load_16 | 23 | 0.00010151 | 2.5441e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1703-23_0_5_load_17 | 24 | 0.00017777 | 4.4552e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1703-23_0_5_load_21 | 25 | 0.00090924 | 0.00022788 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1703-23_0_5_load_24 | 27 | 0.00068907 | 0.0001727 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1703-23_0_5_load_26 | 28 | 0.0091643 | 0.0022968 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1703-23_0_5_load_152 | 29 | 0.0017439 | 0.00043707 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1703-23_0_5_load_150 | 31 | 0.0092843 | 0.0023269 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1703-23_0_5_load_148 | 32 | 0.009344 | 0.0023418 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1703-23_0_5_load_151 | 33 | 0.0044181 | 0.0011073 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1703-23_0_5_load_147 | 34 | 0.010177 | 0.0025507 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1703-23_0_5_load_31 | 35 | 0.002169 | 0.00054361 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1703-23_0_5_load_32 | 36 | 0.0013615 | 0.00034123 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1703-23_0_5_load_34 | 38 | 0.001002 | 0.00025112 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1703-23_0_5_load_40 | 40 | 0.0018461 | 0.00046267 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1703-23_0_5_load_149 | 43 | 0.0085688 | 0.0021475 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1703-23_0_5_load_68 | 45 | 0.00069649 | 0.00017456 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1703-23_0_5_load_41 | 46 | 0.0026297 | 0.00065907 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1703-23_0_5_load_81 | 47 | 0.0018106 | 0.00045379 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1703-23_0_5_load_129 | 50 | 0.0099751 | 0.0025 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1703-23_0_5_load_132 | 53 | 0.0071883 | 0.0018015 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1703-23_0_5_load_67 | 54 | 0.0010369 | 0.00025986 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1703-23_0_5_load_42 | 55 | 0.0028791 | 0.00072158 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1703-23_0_5_load_43 | 56 | 0.00174 | 0.00043607 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1703-23_0_5_load_45 | 57 | 0.001825 | 0.0004574 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1703-23_0_5_load_55 | 58 | 0.0022256 | 0.00055778 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1703-23_0_5_load_61 | 60 | 0.0020466 | 0.00051294 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1703-23_0_5_load_62 | 61 | 0.0043179 | 0.0010822 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1703-23_0_5_load_59 | 62 | 0.0018299 | 0.0004586 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1703-23_0_5_load_56 | 63 | 0.0016388 | 0.00041073 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1703-23_0_5_load_91 | 68 | 0.053263 | 0.013349 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1703-23_0_5_load_110 | 71 | 0.0034614 | 0.00086752 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1703-23_0_5_load_58 | 72 | 0.0020823 | 0.00052188 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1703-23_0_5_load_94 | 73 | 0.013379 | 0.0033531 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1703-23_0_5_load_93 | 74 | 0.057602 | 0.014436 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1703-23_0_5_load_109 | 75 | 0.0095866 | 0.0024026 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1703-23_0_5_load_108 | 76 | 0.0012846 | 0.00032196 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1703-23_0_5_load_115 | 77 | 0.0018532 | 0.00046446 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1703-23_0_5_load_113 | 79 | 0.010165 | 0.0025477 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1703-23_0_5_load_111 | 81 | 0.0087287 | 0.0021876 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1703-23_0_5_load_78 | 82 | 0.010203 | 0.0025572 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1703-23_0_5_load_86 | 83 | 0.0069606 | 0.0017445 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1703-23_0_5_load_51 | 84 | 0.00099084 | 0.00024833 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1703-23_0_5_load_54 | 86 | 0.00056839 | 0.00014245 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1703-23_0_5_load_66 | 87 | 0.0017717 | 0.00044403 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1703-23_0_5_load_57 | 88 | 0.0021037 | 0.00052725 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1703-23_0_5_load_70 | 89 | 0.0017942 | 0.00044968 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1703-23_0_5_load_77 | 90 | 0.0042967 | 0.0010768 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1703-23_0_5_load_88 | 91 | 0.010586 | 0.0026531 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1703-23_0_5_load_100 | 93 | 0.0039226 | 0.0009831 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1703-23_0_5_load_97 | 94 | 0.0046173 | 0.0011572 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1703-23_0_5_load_71 | 95 | 0.0016616 | 0.00041644 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1703-23_0_5_load_82 | 96 | 0.0012716 | 0.00031869 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1703-23_0_5_load_72 | 97 | 0.0016548 | 0.00041473 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1703-23_0_5_load_74 | 99 | 0.0050295 | 0.0012605 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1703-23_0_5_load_75 | 100 | 0.011626 | 0.0029136 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1703-23_0_5_load_85 | 102 | 0.0091838 | 0.0023017 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1703-23_0_5_load_79 | 103 | 0.0099909 | 0.0025039 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1703-23_0_5_load_120 | 104 | 0.0032441 | 0.00081306 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1703-23_0_5_load_117 | 105 | 0.0085144 | 0.0021339 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1703-23_0_5_load_130 | 106 | 0.0061315 | 0.0015367 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1703-23_0_5_load_142 | 107 | 0.005259 | 0.001318 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1703-23_0_5_load_140 | 108 | 0.0018145 | 0.00045475 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1703-23_0_5_load_131 | 109 | 0.0043946 | 0.0011014 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1703-23_0_5_load_114 | 110 | 0.009992 | 0.0025042 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1703-23_0_5_load_107 | 111 | 0.0033107 | 0.00082975 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1703-23_0_5_load_98 | 112 | 0.014875 | 0.0037281 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1703-23_0_5_load_153 | 114 | 0.0071563 | 0.0017935 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1703-23_0_5_load_105 | 116 | 0.0069592 | 0.0017441 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1703-23_0_5_load_101 | 117 | 0.0035884 | 0.00089933 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1703-23_0_5_load_102 | 118 | 0.0020282 | 0.00050831 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1703-23_0_5_load_106 | 121 | 0.0048445 | 0.0012142 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1703-23_0_5_load_121 | 122 | 0.0018345 | 0.00045976 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1703-23_0_5_load_122 | 123 | 0.0019612 | 0.00049153 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1703-23_0_5_load_124 | 124 | 0.009932 | 0.0024892 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1703-23_0_5_load_125 | 125 | 0.0026625 | 0.00066729 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1703-23_0_5_load_123 | 127 | 0.0025348 | 0.00063529 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1703-23_0_5_load_128 | 129 | 0.002147 | 0.00053809 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1703-23_0_5_load_126 | 130 | 0.0058436 | 0.0014645 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1703-23_0_5_load_134 | 131 | 0.0027783 | 0.00069631 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1703-23_0_5_load_135 | 132 | 0.0028582 | 0.00071633 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1703-23_0_5_load_136 | 135 | 0.0022771 | 0.00057069 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1703-23_0_5_load_138 | 136 | 0.002274 | 0.00056991 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1703-23_0_5_load_137 | 137 | 0.0025248 | 0.00063278 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1703-23_0_5_load_139 | 138 | 0.0025315 | 0.00063444 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1703-23_0_5_load_145 | 140 | 0.0020158 | 0.0005052 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1703-23_0_5_load_146 | 141 | 0.009029 | 0.0022629 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 105 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1703-23_0_5_line_0 |  | 0 | 1 | 0.055206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1703-23_0_5_line_1 |  | 0 | 2 | 0.072037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1703-23_0_5_line_2 |  | 1 | 3 | 0.031061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1703-23_0_5_line_3 |  | 2 | 4 | 0.002097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1703-23_0_5_line_4 |  | 3 | 5 | 0.00026702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1703-23_0_5_line_5 |  | 4 | 6 | 0.01142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1703-23_0_5_line_6 |  | 5 | 7 | 0.10707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1703-23_0_5_line_7 |  | 6 | 8 | 0.027779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1703-23_0_5_line_8 |  | 7 | 9 | 0.012597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1703-23_0_5_line_9 |  | 7 | 10 | 0.054903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1703-23_0_5_line_10 |  | 8 | 11 | 0.023476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1703-23_0_5_line_11 |  | 9 | 29 | 0.033909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1703-23_0_5_line_12 |  | 10 | 30 | 0.088348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1703-23_0_5_line_13 |  | 10 | 31 | 0.0079656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1703-23_0_5_line_14 |  | 11 | 12 | 0.0045487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1703-23_0_5_line_15 |  | 12 | 16 | 0.021595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1703-23_0_5_line_16 |  | 13 | 14 | 0.025674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1703-23_0_5_line_17 |  | 13 | 15 | 0.013079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1703-23_0_5_line_18 |  | 14 | 16 | 0.019885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1703-23_0_5_line_19 |  | 14 | 17 | 0.011308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1703-23_0_5_line_20 |  | 15 | 18 | 0.0049316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1703-23_0_5_line_21 |  | 17 | 25 | 0.019581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1703-23_0_5_line_22 |  | 18 | 24 | 0.013898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1703-23_0_5_line_23 |  | 19 | 20 | 0.0036902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1703-23_0_5_line_24 |  | 20 | 21 | 0.013804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1703-23_0_5_line_25 |  | 21 | 22 | 0.012365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1703-23_0_5_line_26 |  | 22 | 23 | 0.010334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1703-23_0_5_line_27 |  | 23 | 24 | 0.0062024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1703-23_0_5_line_28 |  | 25 | 26 | 0.15215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1703-23_0_5_line_29 |  | 26 | 27 | 0.074289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1703-23_0_5_line_30 |  | 27 | 28 | 0.0090518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1703-23_0_5_line_31 |  | 30 | 32 | 0.0044735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1703-23_0_5_line_32 |  | 31 | 33 | 0.011086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1703-23_0_5_line_33 |  | 32 | 34 | 0.038608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1703-23_0_5_line_34 |  | 33 | 41 | 0.032952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1703-23_0_5_line_35 |  | 34 | 141 | 0.018832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1703-23_0_5_line_36 |  | 35 | 36 | 0.00032851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1703-23_0_5_line_37 |  | 35 | 37 | 0.014614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1703-23_0_5_line_38 |  | 36 | 38 | 0.024796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1703-23_0_5_line_39 |  | 37 | 39 | 0.33311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1703-23_0_5_line_40 |  | 38 | 40 | 0.00064516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1703-23_0_5_line_41 |  | 39 | 44 | 0.052927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1703-23_0_5_line_42 |  | 39 | 45 | 0.051636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1703-23_0_5_line_43 |  | 40 | 46 | 0.014931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1703-23_0_5_line_44 |  | 41 | 42 | 0.025424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1703-23_0_5_line_45 |  | 42 | 43 | 0.035986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1703-23_0_5_line_46 |  | 44 | 47 | 0.053044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1703-23_0_5_line_47 |  | 45 | 54 | 0.014515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1703-23_0_5_line_48 |  | 47 | 96 | 0.014818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1703-23_0_5_line_49 |  | 48 | 49 | 0.033561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1703-23_0_5_line_50 |  | 48 | 50 | 0.014591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1703-23_0_5_line_51 |  | 49 | 104 | 0.033672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1703-23_0_5_line_52 |  | 49 | 105 | 0.039225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1703-23_0_5_line_53 |  | 50 | 106 | 0.032941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1703-23_0_5_line_54 |  | 51 | 52 | 0.007747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1703-23_0_5_line_55 |  | 51 | 53 | 0.032252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_1703-23_0_5_line_56 |  | 52 | 107 | 0.026188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1703-23_0_5_line_57 |  | 52 | 108 | 0.0043377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1703-23_0_5_line_58 |  | 53 | 109 | 0.00084912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1703-23_0_5_line_59 |  | 54 | 86 | 0.013512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1703-23_0_5_line_60 |  | 55 | 56 | 0.014538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1703-23_0_5_line_61 |  | 56 | 57 | 0.0089672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1703-23_0_5_line_62 |  | 57 | 58 | 0.019104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1703-23_0_5_line_63 |  | 58 | 63 | 0.0028951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1703-23_0_5_line_64 |  | 59 | 60 | 0.039104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1703-23_0_5_line_65 |  | 59 | 61 | 0.015843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1703-23_0_5_line_66 |  | 59 | 62 | 0.014408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1703-23_0_5_line_67 |  | 60 | 64 | 0.014917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1703-23_0_5_line_68 |  | 61 | 65 | 0.023151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1703-23_0_5_line_69 |  | 62 | 72 | 0.025546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1703-23_0_5_line_70 |  | 63 | 64 | 0.017402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1703-23_0_5_line_71 |  | 64 | 87 | 0.0054808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1703-23_0_5_line_72 |  | 65 | 90 | 0.0020266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1703-23_0_5_line_73 |  | 65 | 82 | 0.023564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1703-23_0_5_line_74 |  | 66 | 67 | 0.068667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1703-23_0_5_line_75 |  | 66 | 68 | 0.0015854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1703-23_0_5_line_76 |  | 67 | 73 | 0.021579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1703-23_0_5_line_77 |  | 67 | 74 | 0.014482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1703-23_0_5_line_78 |  | 69 | 70 | 0.0068381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1703-23_0_5_line_79 |  | 69 | 71 | 0.031597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1703-23_0_5_line_80 |  | 70 | 91 | 0.051404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_1703-23_0_5_line_81 |  | 70 | 92 | 0.035282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1703-23_0_5_line_82 |  | 70 | 83 | 0.017893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1703-23_0_5_line_83 |  | 71 | 76 | 0.021719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1703-23_0_5_line_84 |  | 72 | 88 | 0.027076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1703-23_0_5_line_85 |  | 73 | 113 | 0.011036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1703-23_0_5_line_86 |  | 74 | 91 | 0.053235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_1703-23_0_5_line_87 |  | 75 | 76 | 0.01282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1703-23_0_5_line_88 |  | 77 | 78 | 0.032097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1703-23_0_5_line_89 |  | 78 | 105 | 0.0067135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1703-23_0_5_line_90 |  | 78 | 126 | 0.007535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1703-23_0_5_line_91 |  | 79 | 80 | 0.028631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1703-23_0_5_line_92 |  | 80 | 110 | 0.020054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1703-23_0_5_line_93 |  | 80 | 102 | 0.0025336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1703-23_0_5_line_94 |  | 81 | 82 | 0.0088259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1703-23_0_5_line_95 |  | 84 | 85 | 0.011702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1703-23_0_5_line_96 |  | 85 | 86 | 0.010332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1703-23_0_5_line_97 |  | 87 | 89 | 0.021655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1703-23_0_5_line_98 |  | 89 | 95 | 0.013608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1703-23_0_5_line_99 |  | 90 | 103 | 0.031843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1703-23_0_5_line_100 |  | 92 | 93 | 0.0038562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_1703-23_0_5_line_101 |  | 92 | 94 | 0.021029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1703-23_0_5_line_102 |  | 93 | 111 | 0.019816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_1703-23_0_5_line_103 |  | 94 | 112 | 0.05507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1703-23_0_5_line_104 |  | 95 | 97 | 0.0083698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1703-23_0_5_line_105 |  | 96 | 99 | 0.0073868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1703-23_0_5_line_106 |  | 98 | 99 | 0.0097282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1703-23_0_5_line_107 |  | 98 | 100 | 0.016458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1703-23_0_5_line_108 |  | 100 | 101 | 0.014782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1703-23_0_5_line_109 |  | 101 | 102 | 0.021542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1703-23_0_5_line_110 |  | 101 | 103 | 0.025152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1703-23_0_5_line_111 |  | 104 | 128 | 0.012987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_1703-23_0_5_line_112 |  | 106 | 120 | 0.010077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_1703-23_0_5_line_113 |  | 107 | 133 | 0.025301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_1703-23_0_5_line_114 |  | 108 | 134 | 0.042117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1703-23_0_5_line_115 |  | 109 | 120 | 0.010495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_1703-23_0_5_line_116 |  | 110 | 124 | 0.00094111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1703-23_0_5_line_117 |  | 111 | 116 | 0.041365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_1703-23_0_5_line_118 |  | 113 | 115 | 0.022209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1703-23_0_5_line_119 |  | 114 | 115 | 0.048868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1703-23_0_5_line_120 |  | 116 | 119 | 0.011953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_1703-23_0_5_line_121 |  | 117 | 118 | 0.017113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_1703-23_0_5_line_122 |  | 117 | 119 | 0.0061813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_1703-23_0_5_line_123 |  | 118 | 120 | 0.0014356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_1703-23_0_5_line_124 |  | 121 | 122 | 0.0015475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1703-23_0_5_line_125 |  | 122 | 123 | 0.0021985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1703-23_0_5_line_126 |  | 123 | 126 | 0.035523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1703-23_0_5_line_127 |  | 124 | 125 | 0.030332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1703-23_0_5_line_128 |  | 125 | 130 | 0.0048437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1703-23_0_5_line_129 |  | 126 | 127 | 0.014441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1703-23_0_5_line_130 |  | 128 | 129 | 0.0036717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1703-23_0_5_line_131 |  | 128 | 130 | 0.019153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
132 | LV_1703-23_0_5_line_132 |  | 129 | 131 | 0.009887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1703-23_0_5_line_133 |  | 131 | 132 | 0.0084665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1703-23_0_5_line_134 |  | 132 | 135 | 0.0094542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1703-23_0_5_line_135 |  | 133 | 141 | 0.0028111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_1703-23_0_5_line_136 |  | 134 | 139 | 0.035346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1703-23_0_5_line_137 |  | 135 | 136 | 0.012079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1703-23_0_5_line_138 |  | 136 | 137 | 0.012106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1703-23_0_5_line_139 |  | 137 | 138 | 0.013009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1703-23_0_5_line_140 |  | 139 | 140 | 0.040916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1703-23_0_5_trafo_117 | 0.63 MVA 20/0.4 kV | 142 | 105 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2674482.4931 | 1224958.7117 | 2674535.8144 | 1224973.0139
1 | 2674482.4931 | 1224958.7117 | 2674463.8692 | 1224953.7163 | 2674454.7376 | 1224953.3463 | 2674443.3617 | 1224957.2177 | 2674422.1344 | 1224969.1602 | 2674414.9713 | 1224970.2346
2 | 2674535.8144 | 1224973.0139 | 2674552.3112 | 1224977.4388 | 2674565.9028 | 1224980.7175
3 | 2674414.9713 | 1224970.2346 | 2674412.8975 | 1224970.5456 | 2674412.8975 | 1224970.5456
4 | 2674566.1624 | 1224980.7801 | 2674565.9028 | 1224980.7175
5 | 2674401.4888 | 1224970.0483 | 2674412.8975 | 1224970.5456
6 | 2674672.288 | 1224994.9318 | 2674566.167 | 1224980.7812 | 2674566.1624 | 1224980.7801
7 | 2674401.4888 | 1224970.0483 | 2674373.7362 | 1224968.8384
8 | 2674672.288 | 1224994.9318 | 2674670.2473 | 1225007.3629
9 | 2674672.288 | 1224994.9318 | 2674678.1466 | 1224995.7169 | 2674693.6302 | 1224998.0238 | 2674689.6626 | 1225017.5314 | 2674702.1955 | 1225022.3585
10 | 2674350.2821 | 1224967.817 | 2674356.3974 | 1224968.0825 | 2674373.7362 | 1224968.8384
11 | 2674660.9116 | 1225038.7602 | 2674665.8435 | 1225034.1881 | 2674670.2473 | 1225007.3629
12 | 2674776.9663 | 1225010.4226 | 2674773.2096 | 1225008.3074 | 2674760.8655 | 1225004.1385 | 2674717.6028 | 1224999.9481 | 2674716.5397 | 1225004.3043 | 2674702.1955 | 1225022.3585
13 | 2674702.1955 | 1225022.3585 | 2674700.0115 | 1225030.0189
14 | 2674350.2821 | 1224967.817 | 2674345.7912 | 1224967.0942
15 | 2674324.5773 | 1224963.1174 | 2674332.7575 | 1224964.9964 | 2674345.7912 | 1224967.0942
16 | 2674306.8215 | 1224954.5323 | 2674309.9714 | 1224963.9779 | 2674310.4556 | 1224970.7328 | 2674308.3832 | 1224979.4349
17 | 2674308.3832 | 1224979.4349 | 2674298.5239 | 1224988.0281
18 | 2674306.8215 | 1224954.5323 | 2674319.8068 | 1224962.0216 | 2674324.5773 | 1224963.1174
19 | 2674306.8215 | 1224954.5323 | 2674298.0066 | 1224947.4498
20 | 2674298.5239 | 1224988.0281 | 2674294.8062 | 1224991.2685
21 | 2674298.0066 | 1224947.4498 | 2674282.7425 | 1224935.1857
22 | 2674284.3304 | 1225000.4008 | 2674287.7328 | 1224997.4336 | 2674294.8062 | 1224991.2685
23 | 2674247.947 | 1225029.0409 | 2674251.0279 | 1225027.0097
24 | 2674251.0279 | 1225027.0097 | 2674261.4434 | 1225020.1428 | 2674262.4985 | 1225019.3352
25 | 2674271.8679 | 1225011.2696 | 2674263.4873 | 1225018.5784 | 2674262.4985 | 1225019.3352
26 | 2674279.6559 | 1225004.4775 | 2674271.8679 | 1225011.2696
27 | 2674279.6559 | 1225004.4775 | 2674284.3304 | 1225000.4008
28 | 2674209.3295 | 1224807.0856 | 2674213.2669 | 1224823.3121 | 2674216.6848 | 1224847.1482 | 2674220.6955 | 1224859.9289 | 2674227.7427 | 1224871.2019 | 2674270.9772 | 1224925.7327 | 2674282.7425 | 1224935.1857
29 | 2674209.3295 | 1224807.0856 | 2674254.384 | 1224799.6758 | 2674256.7978 | 1224811.6138 | 2674264.1362 | 1224826.3363
30 | 2674268.1742 | 1224834.4375 | 2674264.1362 | 1224826.3363
31 | 2674776.9663 | 1225010.4226 | 2674780.5162 | 1225013.1449
32 | 2674700.0115 | 1225030.0189 | 2674698.5947 | 1225034.9883 | 2674696.1019 | 1225040.3563
33 | 2674808.7105 | 1225039.4314 | 2674804.4227 | 1225034.9616 | 2674788.0804 | 1225018.9457 | 2674780.5162 | 1225013.1449
34 | 2674685.5587 | 1225071.4489 | 2674687.9938 | 1225060.4722 | 2674692.3217 | 1225048.4963 | 2674696.1019 | 1225040.3563
35 | 2674821.7474 | 1225053.0218 | 2674808.7105 | 1225039.4314
36 | 2674523.8039 | 1225345.8724 | 2674523.6503 | 1225346.1628
37 | 2674516.8164 | 1225359.0802 | 2674523.6503 | 1225346.1628
38 | 2674535.2993 | 1225323.9027 | 2674529.6369 | 1225334.8469 | 2674523.8039 | 1225345.8724
39 | 2674516.8164 | 1225359.0802 | 2674485.0919 | 1225341.2158 | 2674487.3166 | 1225330.0473 | 2674493.4572 | 1225318.5721 | 2674500.1786 | 1225293.4174 | 2674505.5057 | 1225286.9798 | 2674528.0735 | 1225242.9887 | 2674545.5118 | 1225230.232 | 2674551.0984 | 1225227.9004 | 2674567.5057 | 1225223.0026 | 2674582.5548 | 1225221.2233 | 2674601.0155 | 1225212.1931 | 2674619.6146 | 1225201.2078 | 2674622.8136 | 1225200.036 | 2674625.592 | 1225200.36 | 2674629.4723 | 1225203.4996 | 2674634.3625 | 1225206.5184 | 2674639.086 | 1225205.2991 | 2674649.7591 | 1225194.5702 | 2674634.118 | 1225233.8668 | 2674635.1668 | 1225240.9179
40 | 2674535.5958 | 1225323.3297 | 2674535.2993 | 1225323.9027
41 | 2674667.8062 | 1225199.1885 | 2674635.1668 | 1225240.9179
42 | 2674635.1668 | 1225240.9179 | 2674620.7581 | 1225259.3384 | 2674604.2809 | 1225282.2845
43 | 2674542.4568 | 1225310.0688 | 2674535.5958 | 1225323.3297
44 | 2674705.0795 | 1225087.3377 | 2674700.0998 | 1225081.1711 | 2674692.7189 | 1225075.4414 | 2674685.5587 | 1225071.4489
45 | 2674705.0795 | 1225087.3377 | 2674709.7433 | 1225096.3133 | 2674713.1368 | 1225099.5802 | 2674716.5341 | 1225100.7347 | 2674729.7233 | 1225102.1901 | 2674733.8872 | 1225103.2765
46 | 2674667.8062 | 1225199.1885 | 2674669.727 | 1225212.2657 | 2674665.9971 | 1225229.7638 | 2674666.8857 | 1225236.2793 | 2674670.5156 | 1225238.2261 | 2674678.6941 | 1225238.9959 | 2674681.7117 | 1225238.7763
47 | 2674595.8144 | 1225294.0749 | 2674604.2809 | 1225282.2845
48 | 2674681.7117 | 1225238.7763 | 2674689.3788 | 1225238.2183 | 2674696.411 | 1225237.0358
49 | 2674821.1233 | 1225175.609 | 2674821.4127 | 1225152.5974 | 2674823.8366 | 1225146.1458 | 2674824.0871 | 1225142.5021
50 | 2674824.0871 | 1225142.5021 | 2674829.541 | 1225145.3058 | 2674837.7235 | 1225143.1617
51 | 2674821.1233 | 1225175.609 | 2674814.1171 | 1225174.4535 | 2674813.191 | 1225173.9415 | 2674810.1743 | 1225173.281 | 2674808.1783 | 1225172.8334 | 2674807.4704 | 1225176.6714 | 2674803.0069 | 1225175.9037 | 2674794.1357 | 1225174.7471 | 2674791.2034 | 1225174.1062
52 | 2674821.1233 | 1225175.609 | 2674825.7456 | 1225180.0256 | 2674823.5531 | 1225184.9568 | 2674824.6971 | 1225191.053 | 2674834.3517 | 1225209.9637
53 | 2674837.7235 | 1225143.1617 | 2674848.0027 | 1225140.4681 | 2674849.1246 | 1225140.4822 | 2674852.8337 | 1225144.576 | 2674867.4221 | 1225138.859
54 | 2674860.7608 | 1225090.6177 | 2674856.5995 | 1225097.1586
55 | 2674856.5995 | 1225097.1586 | 2674865.2948 | 1225106.8744 | 2674872.5318 | 1225124.6729
56 | 2674860.7608 | 1225090.6177 | 2674850.0068 | 1225082.4215 | 2674841.2279 | 1225073.2898
57 | 2674860.7608 | 1225090.6177 | 2674862.9005 | 1225086.8444
58 | 2674872.5318 | 1225124.6729 | 2674872.8517 | 1225125.4595
59 | 2674587.9332 | 1225305.0503 | 2674595.8144 | 1225294.0749
60 | 2674632.9657 | 1225371.8069 | 2674638.3106 | 1225358.2869
61 | 2674641.6075 | 1225349.9478 | 2674638.3106 | 1225358.2869
62 | 2674641.6075 | 1225349.9478 | 2674648.6311 | 1225332.1817
63 | 2674648.6311 | 1225332.1817 | 2674649.6955 | 1225329.4894
64 | 2674706.3683 | 1225333.0721 | 2674669.9763 | 1225318.7642
65 | 2674706.3683 | 1225333.0721 | 2674711.9973 | 1225318.2623
66 | 2674706.3683 | 1225333.0721 | 2674701.4321 | 1225346.6079
67 | 2674656.0934 | 1225313.306 | 2674669.9763 | 1225318.7642
68 | 2674720.2226 | 1225296.6218 | 2674711.9973 | 1225318.2623
69 | 2674692.6797 | 1225370.6083 | 2674701.4321 | 1225346.6079
70 | 2674656.0934 | 1225313.306 | 2674649.6955 | 1225329.4894
71 | 2674656.0934 | 1225313.306 | 2674657.9918 | 1225308.1645
72 | 2674720.2226 | 1225296.6218 | 2674720.9242 | 1225294.7205
73 | 2674720.2226 | 1225296.6218 | 2674742.589 | 1225304.0371
74 | 2675006.4528 | 1225303.4814 | 2675009.3032 | 1225301.0936 | 2675018.6504 | 1225284.9228 | 2675017.4495 | 1225278.5479 | 2675021.1087 | 1225273.3573 | 2675039.7368 | 1225269.1337 | 2675038.4081 | 1225254.8631
75 | 2675006.4528 | 1225303.4814 | 2675005.2358 | 1225304.4976
76 | 2675038.4081 | 1225254.8631 | 2675059.9275 | 1225253.2587
77 | 2675038.4081 | 1225254.8631 | 2675023.9732 | 1225256.0291
78 | 2674915.2362 | 1225262.1944 | 2674919.5525 | 1225262.0041 | 2674919.68 | 1225264.5185
79 | 2674915.2362 | 1225262.1944 | 2674903.366 | 1225253.5615 | 2674887.4172 | 1225247.9127
80 | 2674919.68 | 1225264.5185 | 2674933.1595 | 1225263.3652 | 2674970.9115 | 1225260.3155
81 | 2674914.5392 | 1225229.6418 | 2674917.1305 | 1225243.0166 | 2674919.5525 | 1225262.0041 | 2674919.68 | 1225264.5185
82 | 2674919.68 | 1225264.5185 | 2674920.7857 | 1225282.3773
83 | 2674871.9584 | 1225232.8416 | 2674883.8059 | 1225245.6991 | 2674887.4172 | 1225247.9127
84 | 2674683.4032 | 1225396.0456 | 2674692.6797 | 1225370.6083
85 | 2675070.9334 | 1225252.4382 | 2675059.9275 | 1225253.2587
86 | 2675023.9732 | 1225256.0291 | 2674970.9115 | 1225260.3155
87 | 2674871.9584 | 1225232.8416 | 2674859.9699 | 1225232.4016 | 2674859.8865 | 1225233.2206
88 | 2674839.0532 | 1225213.6373 | 2674840.3442 | 1225220.1023 | 2674836.8807 | 1225245.3702
89 | 2674839.0532 | 1225213.6373 | 2674836.0033 | 1225213.1987 | 2674834.3517 | 1225209.9637
90 | 2674837.5844 | 1225206.2473 | 2674839.0532 | 1225213.6373
91 | 2674765.1886 | 1225247.7651 | 2674792.7816 | 1225255.4042
92 | 2674765.1886 | 1225247.7651 | 2674768.6624 | 1225228.0143
93 | 2674765.1886 | 1225247.7651 | 2674762.736 | 1225247.1294
94 | 2674742.589 | 1225304.0371 | 2674750.9665 | 1225306.8145
95 | 2674581.9066 | 1225313.4429 | 2674583.7384 | 1225323.3502 | 2674583.0335 | 1225324.8162
96 | 2674581.9066 | 1225313.4429 | 2674587.9332 | 1225305.0503
97 | 2674657.9918 | 1225308.1645 | 2674665.4925 | 1225287.8504
98 | 2674665.4925 | 1225287.8504 | 2674670.2059 | 1225275.085
99 | 2674720.9242 | 1225294.7205 | 2674725.5519 | 1225282.1791 | 2674732.4676 | 1225265.0476
100 | 2674914.5392 | 1225229.6418 | 2674913.1193 | 1225226.0566
101 | 2674914.5392 | 1225229.6418 | 2674925.0364 | 1225225.0931 | 2674930.4981 | 1225217.2117
102 | 2674905.823 | 1225207.6332 | 2674913.1193 | 1225226.0566
103 | 2674930.4981 | 1225217.2117 | 2674937.7082 | 1225206.8072 | 2674958.3068 | 1225176.78 | 2674961.2719 | 1225171.5656
104 | 2674673.105 | 1225267.2333 | 2674670.2059 | 1225275.085
105 | 2674696.411 | 1225237.0358 | 2674703.6955 | 1225235.8109
106 | 2674711.5185 | 1225240.5199 | 2674705.6833 | 1225235.4766 | 2674703.6955 | 1225235.8109
107 | 2674711.5185 | 1225240.5199 | 2674727.7047 | 1225237.5433
108 | 2674741.8828 | 1225241.724 | 2674727.7047 | 1225237.5433
109 | 2674741.8828 | 1225241.724 | 2674762.736 | 1225247.1294
110 | 2674741.8828 | 1225241.724 | 2674732.4676 | 1225265.0476
111 | 2674778.2364 | 1225173.5799 | 2674790.6274 | 1225173.9803 | 2674791.2034 | 1225174.1062
112 | 2674876.804 | 1225135.1823 | 2674867.4221 | 1225138.859
113 | 2674823.6934 | 1225055.0504 | 2674841.2279 | 1225073.2898
114 | 2674883.764 | 1225050.2581 | 2674867.1965 | 1225079.2689 | 2674862.9005 | 1225086.8444
115 | 2674876.804 | 1225135.1823 | 2674876.0098 | 1225133.2266 | 2674872.8517 | 1225125.4595
116 | 2674768.6624 | 1225228.0143 | 2674768.8254 | 1225227.0874
117 | 2674905.823 | 1225207.6332 | 2674899.608 | 1225191.9401 | 2674890.5404 | 1225169.1952
118 | 2675070.9334 | 1225252.4382 | 2675093.1456 | 1225250.7839
119 | 2675093.1456 | 1225250.7839 | 2675141.8783 | 1225247.1458
120 | 2674886.1141 | 1225158.0924 | 2674890.5404 | 1225169.1952
121 | 2674883.787 | 1225152.3659 | 2674877.3445 | 1225136.5123
122 | 2674886.1141 | 1225158.0924 | 2674883.787 | 1225152.3659
123 | 2674876.804 | 1225135.1823 | 2674877.3445 | 1225136.5123
124 | 2674846.5115 | 1225176.4932 | 2674847.8447 | 1225175.7077
125 | 2674846.5115 | 1225176.4932 | 2674844.6173 | 1225177.6092
126 | 2674837.5844 | 1225206.2473 | 2674833.6851 | 1225195.5801 | 2674833.7777 | 1225183.9958 | 2674844.6173 | 1225177.6092
127 | 2674768.8254 | 1225227.0874 | 2674774.0796 | 1225197.214
128 | 2674774.9186 | 1225192.4435 | 2674774.0796 | 1225197.214
129 | 2674837.5844 | 1225206.2473 | 2674851.9544 | 1225204.8159
130 | 2674778.2364 | 1225173.5799 | 2674774.7775 | 1225172.3481
131 | 2674778.2364 | 1225173.5799 | 2674774.9186 | 1225192.4435
132 | 2674774.7775 | 1225172.3481 | 2674765.4635 | 1225169.0311
133 | 2674765.4635 | 1225169.0311 | 2674763.6086 | 1225168.3705 | 2674758.8344 | 1225163.9632 | 2674758.8344 | 1225163.9632
134 | 2674749.5339 | 1225165.6607 | 2674758.8344 | 1225163.9632
135 | 2674823.6934 | 1225055.0504 | 2674821.7474 | 1225053.0218
136 | 2674883.764 | 1225050.2581 | 2674901.0107 | 1225058.247 | 2674913.9391 | 1225064.7584 | 2674915.6097 | 1225065.7579
137 | 2674740.9823 | 1225173.0132 | 2674745.6119 | 1225166.3765 | 2674749.5339 | 1225165.6607
138 | 2674740.9823 | 1225173.0132 | 2674738.1923 | 1225177.0126 | 2674735.1883 | 1225183.5881
139 | 2674727.4412 | 1225193.9333 | 2674733.9902 | 1225186.2104 | 2674735.1883 | 1225183.5881
140 | 2674915.6097 | 1225065.7579 | 2674902.5457 | 1225091.088 | 2674900.0579 | 1225091.7683 | 2674891.2912 | 1225087.3086

## bus_geodata
| x | y | coords
0 | 2674482.4931 | 1224958.7117
1 | 2674535.8144 | 1224973.0139
2 | 2674414.9713 | 1224970.2346
3 | 2674565.9028 | 1224980.7175
4 | 2674412.8975 | 1224970.5456
5 | 2674566.1624 | 1224980.7801
6 | 2674401.4888 | 1224970.0483
7 | 2674672.288 | 1224994.9318
8 | 2674373.7362 | 1224968.8384
9 | 2674670.2473 | 1225007.3629
10 | 2674702.1955 | 1225022.3585
11 | 2674350.2821 | 1224967.817
12 | 2674345.7912 | 1224967.0942
13 | 2674308.3832 | 1224979.4349
14 | 2674306.8215 | 1224954.5323
15 | 2674298.5239 | 1224988.0281
16 | 2674324.5773 | 1224963.1174
17 | 2674298.0066 | 1224947.4498
18 | 2674294.8062 | 1224991.2685
19 | 2674247.947 | 1225029.0409
20 | 2674251.0279 | 1225027.0097
21 | 2674262.4985 | 1225019.3352
22 | 2674271.8679 | 1225011.2696
23 | 2674279.6559 | 1225004.4775
24 | 2674284.3304 | 1225000.4008
25 | 2674282.7425 | 1224935.1857
26 | 2674209.3295 | 1224807.0856
27 | 2674264.1362 | 1224826.3363
28 | 2674268.1742 | 1224834.4375
29 | 2674660.9116 | 1225038.7602
30 | 2674776.9663 | 1225010.4226
31 | 2674700.0115 | 1225030.0189
32 | 2674780.5162 | 1225013.1449
33 | 2674696.1019 | 1225040.3563
34 | 2674808.7105 | 1225039.4314
35 | 2674523.6503 | 1225346.1628
36 | 2674523.8039 | 1225345.8724
37 | 2674516.8164 | 1225359.0802
38 | 2674535.2993 | 1225323.9027
39 | 2674635.1668 | 1225240.9179
40 | 2674535.5958 | 1225323.3297
41 | 2674685.5587 | 1225071.4489
42 | 2674705.0795 | 1225087.3377
43 | 2674733.8872 | 1225103.2765
44 | 2674667.8062 | 1225199.1885
45 | 2674604.2809 | 1225282.2845
46 | 2674542.4568 | 1225310.0688
47 | 2674681.7117 | 1225238.7763
48 | 2674824.0871 | 1225142.5021
49 | 2674821.1233 | 1225175.609
50 | 2674837.7235 | 1225143.1617
51 | 2674856.5995 | 1225097.1586
52 | 2674860.7608 | 1225090.6177
53 | 2674872.5318 | 1225124.6729
54 | 2674595.8144 | 1225294.0749
55 | 2674632.9657 | 1225371.8069
56 | 2674638.3106 | 1225358.2869
57 | 2674641.6075 | 1225349.9478
58 | 2674648.6311 | 1225332.1817
59 | 2674706.3683 | 1225333.0721
60 | 2674669.9763 | 1225318.7642
61 | 2674711.9973 | 1225318.2623
62 | 2674701.4321 | 1225346.6079
63 | 2674649.6955 | 1225329.4894
64 | 2674656.0934 | 1225313.306
65 | 2674720.2226 | 1225296.6218
66 | 2675006.4528 | 1225303.4814
67 | 2675038.4081 | 1225254.8631
68 | 2675005.2358 | 1225304.4976
69 | 2674915.2362 | 1225262.1944
70 | 2674919.68 | 1225264.5185
71 | 2674887.4172 | 1225247.9127
72 | 2674692.6797 | 1225370.6083
73 | 2675059.9275 | 1225253.2587
74 | 2675023.9732 | 1225256.0291
75 | 2674859.8865 | 1225233.2206
76 | 2674871.9584 | 1225232.8416
77 | 2674836.8807 | 1225245.3702
78 | 2674839.0532 | 1225213.6373
79 | 2674792.7816 | 1225255.4042
80 | 2674765.1886 | 1225247.7651
81 | 2674750.9665 | 1225306.8145
82 | 2674742.589 | 1225304.0371
83 | 2674920.7857 | 1225282.3773
84 | 2674583.0335 | 1225324.8162
85 | 2674581.9066 | 1225313.4429
86 | 2674587.9332 | 1225305.0503
87 | 2674657.9918 | 1225308.1645
88 | 2674683.4032 | 1225396.0456
89 | 2674665.4925 | 1225287.8504
90 | 2674720.9242 | 1225294.7205
91 | 2674970.9115 | 1225260.3155
92 | 2674914.5392 | 1225229.6418
93 | 2674913.1193 | 1225226.0566
94 | 2674930.4981 | 1225217.2117
95 | 2674670.2059 | 1225275.085
96 | 2674696.411 | 1225237.0358
97 | 2674673.105 | 1225267.2333
98 | 2674711.5185 | 1225240.5199
99 | 2674703.6955 | 1225235.8109
100 | 2674727.7047 | 1225237.5433
101 | 2674741.8828 | 1225241.724
102 | 2674762.736 | 1225247.1294
103 | 2674732.4676 | 1225265.0476
104 | 2674791.2034 | 1225174.1062
105 | 2674834.3517 | 1225209.9637
106 | 2674867.4221 | 1225138.859
107 | 2674841.2279 | 1225073.2898
108 | 2674862.9005 | 1225086.8444
109 | 2674872.8517 | 1225125.4595
110 | 2674768.6624 | 1225228.0143
111 | 2674905.823 | 1225207.6332
112 | 2674961.2719 | 1225171.5656
113 | 2675070.9334 | 1225252.4382
114 | 2675141.8783 | 1225247.1459
115 | 2675093.1456 | 1225250.7839
116 | 2674890.5404 | 1225169.1952
117 | 2674883.787 | 1225152.3659
118 | 2674877.3445 | 1225136.5123
119 | 2674886.1141 | 1225158.0924
120 | 2674876.804 | 1225135.1823
121 | 2674847.8447 | 1225175.7077
122 | 2674846.5115 | 1225176.4932
123 | 2674844.6173 | 1225177.6092
124 | 2674768.8254 | 1225227.0874
125 | 2674774.0796 | 1225197.214
126 | 2674837.5844 | 1225206.2473
127 | 2674851.9544 | 1225204.8159
128 | 2674778.2364 | 1225173.5799
129 | 2674774.7775 | 1225172.3481
130 | 2674774.9186 | 1225192.4435
131 | 2674765.4635 | 1225169.0311
132 | 2674758.8344 | 1225163.9632
133 | 2674823.6934 | 1225055.0504
134 | 2674883.764 | 1225050.2581
135 | 2674749.5339 | 1225165.6607
136 | 2674740.9823 | 1225173.0132
137 | 2674735.1883 | 1225183.5881
138 | 2674727.4412 | 1225193.9333
139 | 2674915.6097 | 1225065.7579
140 | 2674891.2912 | 1225087.3086
141 | 2674821.7474 | 1225053.0218
142 | 2674839.0532 | 1225213.6373

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97644 | -0.45378 | 0.0021882 | 0.00054842
1 | 0.97752 | -0.43259 | 0.00403 | 0.00101
2 | 0.97518 | -0.47861 | 0.00087791 | 0.00022003
3 | 0.97825 | -0.41841 | 0.0029661 | 0.00074339
4 | 0.97514 | -0.4793 | 0.00066776 | 0.00016736
5 | 0.97825 | -0.41828 | 0.0016642 | 0.00041708
6 | 0.97496 | -0.48292 | 0.0015763 | 0.00039507
7 | 0.98121 | -0.36057 | 0 | 0
8 | 0.97455 | -0.49092 | 0.00024748 | 6.2024e-05
9 | 0.98113 | -0.36211 | 0.004988 | 0.0012501
10 | 0.98307 | -0.32444 | 0 | 0
11 | 0.97421 | -0.49758 | 0 | 0
12 | 0.97415 | -0.49887 | 8.1707e-05 | 2.0478e-05
13 | 0.97346 | -0.5124 | 0 | 0
14 | 0.97356 | -0.51048 | 0 | 0
15 | 0.97341 | -0.51338 | 0.00054838 | 0.00013744
16 | 0.97384 | -0.50497 | 0.00028955 | 7.2567e-05
17 | 0.97344 | -0.51278 | 0.00024557 | 6.1545e-05
18 | 0.9734 | -0.5137 | 0.00043795 | 0.00010976
19 | 0.97325 | -0.51655 | 0.00072509 | 0.00018173
20 | 0.97325 | -0.5165 | 0.0015235 | 0.00038182
21 | 0.97328 | -0.51593 | 0.0002887 | 7.2354e-05
22 | 0.97331 | -0.51535 | 0.00025972 | 6.5091e-05
23 | 0.97334 | -0.51482 | 0.00010151 | 2.5441e-05
24 | 0.97336 | -0.51449 | 0.00017777 | 4.4552e-05
25 | 0.97325 | -0.51666 | 0.00090924 | 0.00022788
26 | 0.97185 | -0.5443 | 0 | 0
27 | 0.97116 | -0.55782 | 0.00068907 | 0.0001727
28 | 0.97109 | -0.55935 | 0.0091643 | 0.0022968
29 | 0.98108 | -0.36318 | 0.0017439 | 0.00043707
30 | 0.98547 | -0.27779 | 0 | 0
31 | 0.9829 | -0.32764 | 0.0092843 | 0.0023269
32 | 0.98553 | -0.27662 | 0.009344 | 0.0023418
33 | 0.98277 | -0.33024 | 0.0044181 | 0.0011073
34 | 0.98614 | -0.26484 | 0.010177 | 0.0025507
35 | 0.97848 | -0.41473 | 0.002169 | 0.00054361
36 | 0.97848 | -0.41478 | 0.0013615 | 0.00034123
37 | 0.97861 | -0.41234 | 0 | 0
38 | 0.97836 | -0.41725 | 0.001002 | 0.00025112
39 | 0.98139 | -0.35784 | 0 | 0
40 | 0.97835 | -0.4173 | 0.0018461 | 0.00046267
41 | 0.98251 | -0.33534 | 0 | 0
42 | 0.98231 | -0.33927 | 0 | 0
43 | 0.98202 | -0.34485 | 0.0085688 | 0.0021475
44 | 0.98199 | -0.34605 | 0 | 0
45 | 0.98123 | -0.36092 | 0.00069649 | 0.00017456
46 | 0.97832 | -0.41802 | 0.0026297 | 0.00065907
47 | 0.98259 | -0.33424 | 0.0018106 | 0.00045379
48 | 0.99302 | -0.13244 | 0 | 0
49 | 0.99556 | -0.08412 | 0 | 0
50 | 0.99192 | -0.15353 | 0.0099751 | 0.0025
51 | 0.98778 | -0.2331 | 0 | 0
52 | 0.98761 | -0.23643 | 0 | 0
53 | 0.9885 | -0.21923 | 0.0071883 | 0.0018015
54 | 0.98119 | -0.3616 | 0.0010369 | 0.00025986
55 | 0.9784 | -0.41641 | 0.0028791 | 0.00072158
56 | 0.97843 | -0.41565 | 0.00174 | 0.00043607
57 | 0.97847 | -0.4149 | 0.001825 | 0.0004574
58 | 0.97859 | -0.41265 | 0.0022256 | 0.00055778
59 | 0.97971 | -0.39059 | 0 | 0
60 | 0.97901 | -0.40427 | 0.0020466 | 0.00051294
61 | 0.98008 | -0.38333 | 0.0043179 | 0.0010822
62 | 0.97963 | -0.39217 | 0.0018299 | 0.0004586
63 | 0.97861 | -0.4122 | 0.0016388 | 0.00041073
64 | 0.97878 | -0.40893 | 0 | 0
65 | 0.98072 | -0.37091 | 0 | 0
66 | 0.97356 | -0.51035 | 0 | 0
67 | 0.97696 | -0.44333 | 0 | 0
68 | 0.97348 | -0.5119 | 0.053263 | 0.013349
69 | 0.98281 | -0.32909 | 0 | 0
70 | 0.9829 | -0.32732 | 0 | 0
71 | 0.9824 | -0.33726 | 0.0034614 | 0.00086752
72 | 0.97953 | -0.39411 | 0.0020823 | 0.00052188
73 | 0.97655 | -0.45142 | 0.013379 | 0.0033531
74 | 0.97796 | -0.42383 | 0.057602 | 0.014436
75 | 0.98206 | -0.34375 | 0.0095866 | 0.0024026
76 | 0.98218 | -0.34153 | 0.0012846 | 0.00032196
77 | 0.99987 | -0.0025622 | 0.0018532 | 0.00046446
78 | 0.99992 | -0.001525 | 0 | 0
79 | 0.98569 | -0.27399 | 0.010165 | 0.0025477
80 | 0.98596 | -0.26877 | 0 | 0
81 | 0.98023 | -0.3804 | 0.0087287 | 0.0021876
82 | 0.9803 | -0.379 | 0.010203 | 0.0025572
83 | 0.98279 | -0.32957 | 0.0069606 | 0.0017445
84 | 0.98116 | -0.36237 | 0.00099084 | 0.00024833
85 | 0.98117 | -0.36217 | 0 | 0
86 | 0.98118 | -0.36198 | 0.00056839 | 0.00014245
87 | 0.97874 | -0.40962 | 0.0017717 | 0.00044403
88 | 0.97948 | -0.39515 | 0.0021037 | 0.00052725
89 | 0.97864 | -0.41163 | 0.0017942 | 0.00044968
90 | 0.98081 | -0.36913 | 0.0042967 | 0.0010768
91 | 0.98121 | -0.3603 | 0.010586 | 0.0026531
92 | 0.98424 | -0.30137 | 0 | 0
93 | 0.9844 | -0.2982 | 0.0039226 | 0.0009831
94 | 0.98386 | -0.30875 | 0.0046173 | 0.0011572
95 | 0.9786 | -0.41245 | 0.0016616 | 0.00041644
96 | 0.98279 | -0.33046 | 0.0012716 | 0.00031869
97 | 0.97858 | -0.41271 | 0.0016548 | 0.00041473
98 | 0.98308 | -0.32482 | 0 | 0
99 | 0.98289 | -0.32841 | 0.0050295 | 0.0012605
100 | 0.98339 | -0.31876 | 0.011626 | 0.0029136
101 | 0.98382 | -0.31022 | 0 | 0
102 | 0.98571 | -0.2735 | 0.0091838 | 0.0023017
103 | 0.98236 | -0.33871 | 0.0099909 | 0.0025039
104 | 0.99429 | -0.10832 | 0.0032441 | 0.00081306
105 | 1 | 0 | -0.51286 | -0.13131
106 | 0.9895 | -0.19985 | 0.0061315 | 0.0015367
107 | 0.98705 | -0.24726 | 0.005259 | 0.001318
108 | 0.98759 | -0.23673 | 0.0018145 | 0.00045475
109 | 0.98852 | -0.21883 | 0.0043946 | 0.0011014
110 | 0.98807 | -0.22779 | 0.009992 | 0.0025042
111 | 0.98526 | -0.28157 | 0.0033107 | 0.00082975
112 | 0.98311 | -0.32351 | 0.014875 | 0.0037281
113 | 0.97648 | -0.45287 | 0 | 0
114 | 0.97601 | -0.46217 | 0.0071563 | 0.0017935
115 | 0.97633 | -0.45577 | 0 | 0
116 | 0.98709 | -0.24636 | 0.0069592 | 0.0017441
117 | 0.98791 | -0.23039 | 0.0035884 | 0.00089933
118 | 0.98871 | -0.21508 | 0.0020282 | 0.00050831
119 | 0.98763 | -0.23583 | 0 | 0
120 | 0.98878 | -0.21378 | 0 | 0
121 | 0.99955 | -0.0087333 | 0.0048445 | 0.0012142
122 | 0.99955 | -0.0086026 | 0.0018345 | 0.00045976
123 | 0.99957 | -0.0083464 | 0.0019612 | 0.00049153
124 | 0.98818 | -0.2257 | 0.009932 | 0.0024892
125 | 0.99194 | -0.15336 | 0.0026625 | 0.00066729
126 | 0.99984 | -0.0029932 | 0 | 0
127 | 0.99981 | -0.0036315 | 0.0025348 | 0.00063529
128 | 0.99381 | -0.11749 | 0 | 0
129 | 0.99375 | -0.11862 | 0.002147 | 0.00053809
130 | 0.99255 | -0.14163 | 0.0058436 | 0.0014645
131 | 0.99361 | -0.12128 | 0.0027783 | 0.00069631
132 | 0.99352 | -0.12314 | 0.0028582 | 0.00071633
133 | 0.98654 | -0.25714 | 0 | 0
134 | 0.98751 | -0.23825 | 0 | 0
135 | 0.99344 | -0.12474 | 0.0022771 | 0.00057069
136 | 0.99335 | -0.12631 | 0.002274 | 0.00056991
137 | 0.9933 | -0.12739 | 0.0025248 | 0.00063278
138 | 0.99327 | -0.12797 | 0.0025315 | 0.00063444
139 | 0.98745 | -0.23952 | 0 | 0
140 | 0.98737 | -0.241 | 0.0020158 | 0.0005052
141 | 0.98648 | -0.25824 | 0.009029 | 0.0022629
142 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.02107 | -0.0053013 | 0.021092 | 0.0053142 | 2.1354e-05 | 1.2975e-05 | 0.032117 | 0.032116 | 0.032117 | 0.97644 | -0.45378 | 0.97752 | -0.43259 | 8.8233
1 | 0.018882 | 0.0047529 | -0.01886 | -0.0047394 | 2.2379e-05 | 1.3423e-05 | 0.028782 | 0.028782 | 0.028782 | 0.97644 | -0.45378 | 0.97518 | -0.47861 | 7.9073
2 | -0.025122 | -0.0063243 | 0.025139 | 0.0063348 | 1.7043e-05 | 1.0518e-05 | 0.038251 | 0.038251 | 0.038251 | 0.97752 | -0.43259 | 0.97825 | -0.41841 | 10.5085
3 | 0.017982 | 0.0045194 | -0.017981 | -0.0045191 | 5.9224e-07 | 3.5287e-07 | 0.027443 | 0.027443 | 0.027443 | 0.97518 | -0.47861 | 0.97514 | -0.4793 | 7.5392
4 | -0.028105 | -0.0070782 | 0.028105 | 0.0070783 | 1.8311e-07 | 1.1384e-07 | 0.042763 | 0.042763 | 0.042763 | 0.97825 | -0.41841 | 0.97825 | -0.41828 | 11.748
5 | 0.017313 | 0.0043517 | -0.01731 | -0.0043499 | 2.99e-06 | 1.7712e-06 | 0.026424 | 0.026424 | 0.026424 | 0.97514 | -0.4793 | 0.97496 | -0.48292 | 7.2593
6 | -0.029769 | -0.0074954 | 0.029852 | 0.0075467 | 8.2368e-05 | 5.1367e-05 | 0.045294 | 0.045294 | 0.045294 | 0.97825 | -0.41828 | 0.98121 | -0.36057 | 12.4434
7 | 0.015734 | 0.0039549 | -0.015728 | -0.0039514 | 6.0093e-06 | 3.4997e-06 | 0.024018 | 0.024018 | 0.024018 | 0.97496 | -0.48292 | 0.97455 | -0.49092 | 6.5984
8 | 0.0067325 | 0.001687 | -0.006732 | -0.0016868 | 4.9244e-07 | 1.5606e-07 | 0.01021 | 0.01021 | 0.01021 | 0.98121 | -0.36057 | 0.98113 | -0.36211 | 2.8049
9 | -0.036584 | -0.0092337 | 0.036647 | 0.0092736 | 6.3425e-05 | 3.9897e-05 | 0.055503 | 0.055503 | 0.055503 | 0.98121 | -0.36057 | 0.98307 | -0.32444 | 15.2482
10 | 0.015481 | 0.0038893 | -0.015476 | -0.0038865 | 4.9201e-06 | 2.8564e-06 | 0.02364 | 0.02364 | 0.02364 | 0.97455 | -0.49092 | 0.97421 | -0.49758 | 6.4946
11 | 0.001744 | 0.0004367 | -0.0017439 | -0.00043707 | 8.8959e-08 | -3.7128e-07 | 0.0026449 | 0.002645 | 0.002645 | 0.98113 | -0.36211 | 0.98108 | -0.36318 | 0.72666
12 | -0.05893 | -0.014861 | 0.059062 | 0.014943 | 0.0001319 | 8.2168e-05 | 0.089232 | 0.089231 | 0.089232 | 0.98307 | -0.32444 | 0.98547 | -0.27779 | 12.2571
13 | 0.022282 | 0.0055873 | -0.022279 | -0.0055852 | 3.3982e-06 | 2.0739e-06 | 0.033729 | 0.033729 | 0.033729 | 0.98307 | -0.32444 | 0.9829 | -0.32764 | 9.2661
14 | 0.015476 | 0.0038865 | -0.015475 | -0.0038859 | 9.533e-07 | 5.5348e-07 | 0.02364 | 0.02364 | 0.02364 | 0.97421 | -0.49758 | 0.97415 | -0.49887 | 6.4946
15 | 0.015393 | 0.0038655 | -0.015389 | -0.0038629 | 4.4781e-06 | 2.5972e-06 | 0.023516 | 0.023516 | 0.023516 | 0.97415 | -0.49887 | 0.97384 | -0.50497 | 6.4604
16 | -0.0040632 | -0.0010176 | 0.0040636 | 0.0010175 | 3.7136e-07 | -8.1546e-08 | 0.0062107 | 0.0062106 | 0.0062107 | 0.97346 | -0.5124 | 0.97356 | -0.51048 | 1.7062
17 | 0.0040632 | 0.0010176 | -0.004063 | -0.0010176 | 1.8918e-07 | -4.1512e-08 | 0.0062107 | 0.0062107 | 0.0062107 | 0.97346 | -0.5124 | 0.97341 | -0.51338 | 1.7062
18 | -0.015095 | -0.003788 | 0.015099 | 0.0037903 | 3.9699e-06 | 2.2934e-06 | 0.023073 | 0.023073 | 0.023073 | 0.97356 | -0.51048 | 0.97384 | -0.50497 | 6.3388
19 | 0.011031 | 0.0027705 | -0.01103 | -0.0027698 | 1.2058e-06 | 6.3111e-07 | 0.016863 | 0.016863 | 0.016863 | 0.97356 | -0.51048 | 0.97344 | -0.51278 | 4.6327
20 | 0.0035146 | 0.0008802 | -0.0035146 | -0.00088023 | 5.3379e-08 | -2.7141e-08 | 0.0053724 | 0.0053725 | 0.0053725 | 0.97341 | -0.51338 | 0.9734 | -0.5137 | 1.476
21 | 0.010785 | 0.0027083 | -0.010783 | -0.0027073 | 1.996e-06 | 1.0341e-06 | 0.016488 | 0.016488 | 0.016488 | 0.97344 | -0.51278 | 0.97325 | -0.51666 | 4.5296
22 | 0.0030766 | 0.00077047 | -0.0030765 | -0.00077057 | 1.1527e-07 | -9.8973e-08 | 0.004703 | 0.0047031 | 0.0047031 | 0.9734 | -0.5137 | 0.97336 | -0.51449 | 1.292
23 | -0.00072509 | -0.00018173 | 0.0007251 | 0.00018168 | 1.7007e-09 | -4.4769e-08 | 0.0011086 | 0.0011086 | 0.0011086 | 0.97325 | -0.51655 | 0.97325 | -0.5165 | 0.30456
24 | -0.0022486 | -0.0005635 | 0.0022486 | 0.00056337 | 6.118e-08 | -1.3239e-07 | 0.0034379 | 0.0034378 | 0.0034379 | 0.97325 | -0.5165 | 0.97328 | -0.51593 | 0.94447
25 | -0.0025373 | -0.00063572 | 0.0025374 | 0.00063562 | 6.9775e-08 | -1.0902e-07 | 0.0038792 | 0.0038791 | 0.0038792 | 0.97328 | -0.51593 | 0.97331 | -0.51535 | 1.0657
26 | -0.0027971 | -0.00070071 | 0.0027972 | 0.00070062 | 7.0859e-08 | -8.3085e-08 | 0.0042762 | 0.0042761 | 0.0042762 | 0.97331 | -0.51535 | 0.97334 | -0.51482 | 1.1748
27 | -0.0028987 | -0.00072606 | 0.0028988 | 0.00072602 | 4.5672e-08 | -4.7861e-08 | 0.0044313 | 0.0044313 | 0.0044313 | 0.97334 | -0.51482 | 0.97336 | -0.51449 | 1.2174
28 | 0.0098734 | 0.0024794 | -0.0098604 | -0.002473 | 1.3006e-05 | 6.4356e-06 | 0.015097 | 0.015098 | 0.015098 | 0.97325 | -0.51666 | 0.97185 | -0.5443 | 4.1478
29 | 0.0098604 | 0.002473 | -0.0098541 | -0.0024698 | 6.3506e-06 | 3.1445e-06 | 0.015098 | 0.015098 | 0.015098 | 0.97185 | -0.5443 | 0.97116 | -0.55782 | 4.1479
30 | 0.009165 | 0.0022971 | -0.0091643 | -0.0022968 | 6.6937e-07 | 3.164e-07 | 0.014043 | 0.014043 | 0.014043 | 0.97116 | -0.55782 | 0.97109 | -0.55935 | 3.8579
31 | -0.059062 | -0.014943 | 0.059065 | 0.014945 | 3.3392e-06 | 1.9091e-06 | 0.089231 | 0.089231 | 0.089231 | 0.98547 | -0.27779 | 0.98553 | -0.27662 | 6.1285
32 | 0.012995 | 0.0032584 | -0.012993 | -0.0032575 | 1.609e-06 | 8.8926e-07 | 0.019673 | 0.019673 | 0.019673 | 0.9829 | -0.32764 | 0.98277 | -0.33024 | 5.4047
33 | -0.068409 | -0.017287 | 0.068448 | 0.01731 | 3.8652e-05 | 2.2768e-05 | 0.10334 | 0.10334 | 0.10334 | 0.98553 | -0.27662 | 0.98614 | -0.26484 | 7.0975
34 | 0.0085748 | 0.0021502 | -0.0085727 | -0.0021493 | 2.0831e-06 | 9.1575e-07 | 0.012984 | 0.012984 | 0.012984 | 0.98277 | -0.33024 | 0.98251 | -0.33534 | 3.5669
35 | -0.078625 | -0.01986 | 0.07865 | 0.019875 | 2.4874e-05 | 1.4958e-05 | 0.1187 | 0.11869 | 0.1187 | 0.98614 | -0.26484 | 0.98648 | -0.25824 | 8.1521
36 | 0.0068401 | 0.0017141 | -0.00684 | -0.0017141 | 1.3329e-08 | 4.4041e-09 | 0.010402 | 0.010402 | 0.010402 | 0.97848 | -0.41473 | 0.97848 | -0.41478 | 2.8576
37 | -0.0090091 | -0.0022577 | 0.0090101 | 0.0022581 | 1.0286e-06 | 4.7473e-07 | 0.0137 | 0.0137 | 0.0137 | 0.97848 | -0.41473 | 0.97861 | -0.41234 | 3.7638
38 | 0.0054785 | 0.0013728 | -0.0054779 | -0.0013727 | 6.4542e-07 | 1.0165e-07 | 0.0083313 | 0.0083314 | 0.0083314 | 0.97848 | -0.41478 | 0.97836 | -0.41725 | 2.2889
39 | -0.0090101 | -0.0022581 | 0.0090335 | 0.002269 | 2.3444e-05 | 1.0807e-05 | 0.0137 | 0.013699 | 0.0137 | 0.97861 | -0.41234 | 0.98139 | -0.35784 | 3.7638
40 | 0.0044759 | 0.0011216 | -0.0044759 | -0.0011216 | 1.1212e-08 | -9.26e-10 | 0.0068075 | 0.0068075 | 0.0068075 | 0.97836 | -0.41725 | 0.97835 | -0.4173 | 1.8702
41 | -0.012327 | -0.0030933 | 0.012334 | 0.003097 | 6.9342e-06 | 3.7687e-06 | 0.018692 | 0.018691 | 0.018692 | 0.98139 | -0.35784 | 0.98199 | -0.34605 | 5.1351
42 | 0.0032932 | 0.00082431 | -0.0032927 | -0.00082465 | 4.8273e-07 | -3.4339e-07 | 0.0049929 | 0.0049931 | 0.0049931 | 0.98139 | -0.35784 | 0.98123 | -0.36092 | 1.3717
43 | 0.0026298 | 0.00065894 | -0.0026297 | -0.00065907 | 8.9574e-08 | -1.3016e-07 | 0.0039997 | 0.0039998 | 0.0039998 | 0.97835 | -0.4173 | 0.97832 | -0.41802 | 1.0988
44 | 0.0085727 | 0.0021493 | -0.0085711 | -0.0021485 | 1.6072e-06 | 7.0671e-07 | 0.012984 | 0.012984 | 0.012984 | 0.98251 | -0.33534 | 0.98231 | -0.33927 | 3.567
45 | 0.0085711 | 0.0021485 | -0.0085688 | -0.0021475 | 2.275e-06 | 1.0006e-06 | 0.012984 | 0.012984 | 0.012984 | 0.98231 | -0.33927 | 0.98202 | -0.34485 | 3.567
46 | -0.012334 | -0.003097 | 0.012341 | 0.0031008 | 6.9493e-06 | 3.7761e-06 | 0.018691 | 0.018691 | 0.018691 | 0.98199 | -0.34605 | 0.98259 | -0.33424 | 5.135
47 | 0.0025962 | 0.00065009 | -0.0025961 | -0.00065022 | 8.4368e-08 | -1.2935e-07 | 0.0039369 | 0.003937 | 0.003937 | 0.98123 | -0.36092 | 0.98119 | -0.3616 | 1.0816
48 | -0.014151 | -0.0035546 | 0.014154 | 0.003556 | 2.5527e-06 | 1.446e-06 | 0.021433 | 0.021433 | 0.021433 | 0.98259 | -0.33424 | 0.98279 | -0.33046 | 5.8882
49 | -0.33043 | -0.084274 | 0.33121 | 0.084767 | 0.000773 | 0.00049298 | 0.49566 | 0.49566 | 0.49566 | 0.99302 | -0.13244 | 0.99556 | -0.08412 | 34.0429
50 | 0.33043 | 0.084274 | -0.3301 | -0.084059 | 0.00033608 | 0.00021434 | 0.49566 | 0.49567 | 0.49567 | 0.99302 | -0.13244 | 0.99192 | -0.15353 | 34.0429
51 | 0.16495 | 0.041984 | -0.16475 | -0.041863 | 0.00019223 | 0.00012128 | 0.24677 | 0.24677 | 0.24677 | 0.99556 | -0.08412 | 0.99429 | -0.10832 | 16.9483
52 | -0.49615 | -0.12675 | 0.49818 | 0.12805 | 0.002027 | 0.0012952 | 0.74243 | 0.74243 | 0.74243 | 0.99556 | -0.08412 | 1 | 0 | 50.9912
53 | 0.32012 | 0.081559 | -0.31941 | -0.081104 | 0.00071361 | 0.00045501 | 0.4807 | 0.4807 | 0.4807 | 0.99192 | -0.15353 | 0.9895 | -0.19985 | 33.0152
54 | 0.096878 | 0.024482 | -0.096863 | -0.024472 | 1.5484e-05 | 9.5132e-06 | 0.14601 | 0.14601 | 0.14601 | 0.98778 | -0.2331 | 0.98761 | -0.23643 | 10.0283
55 | -0.096878 | -0.024482 | 0.096943 | 0.024522 | 6.4463e-05 | 3.9604e-05 | 0.14601 | 0.14601 | 0.14601 | 0.98778 | -0.2331 | 0.9885 | -0.21923 | 10.0283
56 | 0.093032 | 0.023514 | -0.092984 | -0.023484 | 4.8288e-05 | 2.9564e-05 | 0.14024 | 0.14024 | 0.14024 | 0.98761 | -0.23643 | 0.98705 | -0.24726 | 9.632
57 | 0.0038307 | 0.00095868 | -0.0038307 | -0.00095871 | 5.418e-08 | -2.083e-08 | 0.0057712 | 0.0057713 | 0.0057713 | 0.98761 | -0.23643 | 0.98759 | -0.23673 | 1.5855
58 | -0.10413 | -0.026323 | 0.10413 | 0.026324 | 1.958e-06 | 1.2096e-06 | 0.15683 | 0.15683 | 0.15683 | 0.9885 | -0.21923 | 0.98852 | -0.21883 | 10.7715
59 | 0.0015593 | 0.00039036 | -0.0015592 | -0.00039051 | 2.8331e-08 | -1.5253e-07 | 0.0023645 | 0.0023646 | 0.0023646 | 0.98119 | -0.3616 | 0.98118 | -0.36198 | 0.64962
60 | -0.0028791 | -0.00072158 | 0.0028792 | 0.00072146 | 1.0453e-07 | -1.1569e-07 | 0.0043788 | 0.0043787 | 0.0043788 | 0.9784 | -0.41641 | 0.97843 | -0.41565 | 1.203
61 | -0.0046192 | -0.0011575 | 0.0046194 | 0.0011575 | 1.6594e-07 | -6.4241e-09 | 0.0070249 | 0.0070248 | 0.0070249 | 0.97843 | -0.41565 | 0.97847 | -0.4149 | 1.9299
62 | -0.0064444 | -0.0016149 | 0.0064451 | 0.0016151 | 6.8806e-07 | 2.0037e-07 | 0.0098003 | 0.0098002 | 0.0098003 | 0.97847 | -0.4149 | 0.97859 | -0.41265 | 2.6924
63 | -0.0086706 | -0.0021729 | 0.0086708 | 0.002173 | 1.8872e-07 | 8.4405e-08 | 0.013184 | 0.013184 | 0.013184 | 0.97859 | -0.41265 | 0.97861 | -0.4122 | 3.6221
64 | 0.019257 | 0.0048321 | -0.019245 | -0.0048245 | 1.2547e-05 | 7.5378e-06 | 0.029251 | 0.029251 | 0.029251 | 0.97971 | -0.39059 | 0.97901 | -0.40427 | 8.036
65 | -0.025274 | -0.0063396 | 0.025283 | 0.006345 | 8.7559e-06 | 5.4042e-06 | 0.038389 | 0.038389 | 0.038389 | 0.97971 | -0.39059 | 0.98008 | -0.38333 | 10.5465
66 | 0.0060168 | 0.0015075 | -0.0060164 | -0.0015074 | 4.5121e-07 | 1.0736e-07 | 0.0091384 | 0.0091385 | 0.0091385 | 0.97971 | -0.39059 | 0.97963 | -0.39217 | 2.5106
67 | 0.017198 | 0.0043116 | -0.017194 | -0.0043093 | 3.8225e-06 | 2.2589e-06 | 0.02614 | 0.02614 | 0.02614 | 0.97901 | -0.40427 | 0.97878 | -0.40893 | 7.1814
68 | -0.029601 | -0.0074271 | 0.029618 | 0.0074381 | 1.7537e-05 | 1.0932e-05 | 0.044945 | 0.044945 | 0.044945 | 0.98008 | -0.38333 | 0.98072 | -0.37091 | 12.3475
69 | 0.0041865 | 0.0010488 | -0.0041862 | -0.0010488 | 3.8739e-07 | -7.3675e-08 | 0.006359 | 0.0063591 | 0.0063591 | 0.97963 | -0.39217 | 0.97953 | -0.39411 | 1.747
70 | -0.01031 | -0.0025837 | 0.010311 | 0.0025845 | 1.6037e-06 | 8.0767e-07 | 0.015676 | 0.015676 | 0.015676 | 0.97861 | -0.4122 | 0.97878 | -0.40893 | 4.3067
71 | 0.0068832 | 0.0017248 | -0.006883 | -0.0017247 | 2.2506e-07 | 7.5157e-08 | 0.010464 | 0.010464 | 0.010464 | 0.97878 | -0.40893 | 0.97874 | -0.40962 | 2.8748
72 | -0.048559 | -0.012188 | 0.048563 | 0.01219 | 4.126e-06 | 2.615e-06 | 0.073683 | 0.073683 | 0.073683 | 0.98072 | -0.37091 | 0.98081 | -0.36913 | 20.2426
73 | 0.01894 | 0.0047495 | -0.018933 | -0.0047451 | 7.2978e-06 | 4.3734e-06 | 0.028738 | 0.028738 | 0.028738 | 0.98072 | -0.37091 | 0.9803 | -0.379 | 7.8951
74 | -0.053267 | -0.013351 | 0.053437 | 0.01346 | 0.00017068 | 0.00010838 | 0.081415 | 0.081415 | 0.081415 | 0.97356 | -0.51035 | 0.97696 | -0.44333 | 22.3668
75 | 0.053267 | 0.013351 | -0.053263 | -0.013349 | 3.9409e-06 | 2.5024e-06 | 0.081415 | 0.081415 | 0.081415 | 0.97356 | -0.51035 | 0.97348 | -0.5119 | 22.3668
76 | 0.020547 | 0.0051527 | -0.020539 | -0.0051479 | 7.9259e-06 | 4.8024e-06 | 0.031296 | 0.031296 | 0.031296 | 0.97696 | -0.44333 | 0.97655 | -0.45142 | 8.5978
77 | -0.073984 | -0.018613 | 0.074053 | 0.018656 | 6.899e-05 | 4.3972e-05 | 0.11271 | 0.11271 | 0.11271 | 0.97696 | -0.44333 | 0.97796 | -0.42383 | 30.9645
78 | -0.014341 | -0.0035969 | 0.014343 | 0.0035976 | 1.2091e-06 | 6.8717e-07 | 0.021714 | 0.021714 | 0.021714 | 0.98281 | -0.32909 | 0.9829 | -0.32732 | 5.9655
79 | 0.014341 | 0.0035969 | -0.014336 | -0.0035937 | 5.587e-06 | 3.1754e-06 | 0.021714 | 0.021715 | 0.021715 | 0.98281 | -0.32909 | 0.9824 | -0.33726 | 5.9655
80 | 0.14287 | 0.036143 | -0.14264 | -0.036001 | 0.00022569 | 0.00014184 | 0.21641 | 0.21641 | 0.21641 | 0.9829 | -0.32732 | 0.98121 | -0.3603 | 14.8632
81 | -0.16417 | -0.041485 | 0.16438 | 0.041614 | 0.00020452 | 0.0001291 | 0.24866 | 0.24866 | 0.24866 | 0.9829 | -0.32732 | 0.98424 | -0.30137 | 17.0784
82 | 0.0069613 | 0.0017447 | -0.0069606 | -0.0017445 | 7.4524e-07 | 2.5019e-07 | 0.010539 | 0.010539 | 0.010539 | 0.9829 | -0.32732 | 0.98279 | -0.32957 | 2.8953
83 | 0.010874 | 0.0027262 | -0.010872 | -0.0027251 | 2.2098e-06 | 1.1393e-06 | 0.016472 | 0.016472 | 0.016472 | 0.9824 | -0.33726 | 0.98218 | -0.34153 | 4.5252
84 | 0.0021038 | 0.00052697 | -0.0021037 | -0.00052725 | 1.0371e-07 | -2.7443e-07 | 0.0031959 | 0.003196 | 0.003196 | 0.97953 | -0.39411 | 0.97948 | -0.39515 | 0.87802
85 | 0.0071599 | 0.0017948 | -0.0071594 | -0.0017947 | 4.9262e-07 | 1.7721e-07 | 0.01091 | 0.01091 | 0.01091 | 0.97655 | -0.45142 | 0.97648 | -0.45287 | 2.9973
86 | -0.13166 | -0.033093 | 0.13206 | 0.033348 | 0.00040068 | 0.00025509 | 0.20036 | 0.20036 | 0.20036 | 0.97796 | -0.42383 | 0.98121 | -0.3603 | 27.5214
87 | -0.0095866 | -0.0024026 | 0.0095876 | 0.0024031 | 1.0143e-06 | 4.8694e-07 | 0.014525 | 0.014525 | 0.014525 | 0.98206 | -0.34375 | 0.98218 | -0.34153 | 3.9905
88 | -0.0018532 | -0.00046446 | 0.0018533 | 0.0004641 | 9.1549e-08 | -3.6241e-07 | 0.002758 | 0.0027578 | 0.002758 | 0.99987 | -0.0025622 | 0.99992 | -0.001525 | 0.75769
89 | -0.013032 | -0.0032661 | 0.013033 | 0.0032666 | 9.4679e-07 | 5.1788e-07 | 0.019393 | 0.019393 | 0.019393 | 0.99992 | -0.001525 | 1 | 0 | 5.3277
90 | 0.011178 | 0.002802 | -0.011177 | -0.0028016 | 7.8191e-07 | 4.0159e-07 | 0.016635 | 0.016635 | 0.016635 | 0.99992 | -0.001525 | 0.99984 | -0.0029932 | 4.57
91 | -0.010165 | -0.0025477 | 0.010168 | 0.002549 | 2.5285e-06 | 1.2532e-06 | 0.015346 | 0.015346 | 0.015346 | 0.98569 | -0.27399 | 0.98596 | -0.26877 | 4.2159
92 | -0.11466 | -0.02891 | 0.11489 | 0.029054 | 0.00022535 | 0.00014397 | 0.17311 | 0.17311 | 0.17311 | 0.98596 | -0.26877 | 0.98807 | -0.22779 | 47.5571
93 | 0.10449 | 0.026361 | -0.10447 | -0.026346 | 2.3647e-05 | 1.5102e-05 | 0.15776 | 0.15776 | 0.15776 | 0.98596 | -0.26877 | 0.98571 | -0.2735 | 43.3412
94 | -0.0087287 | -0.0021876 | 0.0087293 | 0.0021879 | 5.8109e-07 | 2.6063e-07 | 0.01325 | 0.01325 | 0.01325 | 0.98023 | -0.3804 | 0.9803 | -0.379 | 3.6402
95 | -0.00099084 | -0.00024833 | 0.00099085 | 0.00024819 | 9.9088e-09 | -1.4145e-07 | 0.0015027 | 0.0015027 | 0.0015027 | 0.98116 | -0.36237 | 0.98117 | -0.36217 | 0.41283
96 | -0.00099085 | -0.00024819 | 0.00099086 | 0.00024806 | 8.7484e-09 | -1.249e-07 | 0.0015027 | 0.0015026 | 0.0015027 | 0.98117 | -0.36217 | 0.98118 | -0.36198 | 0.41282
97 | 0.0051113 | 0.0012807 | -0.0051108 | -0.0012807 | 4.9036e-07 | 4.1715e-08 | 0.0077708 | 0.0077709 | 0.0077709 | 0.97874 | -0.40962 | 0.97864 | -0.41163 | 2.1349
98 | 0.0033166 | 0.00083099 | -0.0033164 | -0.00083108 | 1.2977e-07 | -8.7923e-08 | 0.0050427 | 0.0050428 | 0.0050428 | 0.97864 | -0.41163 | 0.9786 | -0.41245 | 1.3854
99 | -0.052859 | -0.013267 | 0.052936 | 0.013316 | 7.6808e-05 | 4.8755e-05 | 0.080202 | 0.080201 | 0.080202 | 0.98081 | -0.36913 | 0.98236 | -0.33871 | 22.0334
100 | -0.18389 | -0.04651 | 0.18391 | 0.046528 | 2.7971e-05 | 1.7705e-05 | 0.27816 | 0.27816 | 0.27816 | 0.98424 | -0.30137 | 0.9844 | -0.2982 | 19.1043
101 | 0.01951 | 0.0048955 | -0.019503 | -0.0048914 | 6.862e-06 | 4.1245e-06 | 0.029498 | 0.029498 | 0.029498 | 0.98424 | -0.30137 | 0.98386 | -0.30875 | 8.104
102 | -0.18784 | -0.047511 | 0.18799 | 0.047606 | 0.00014993 | 9.4945e-05 | 0.28409 | 0.28409 | 0.28409 | 0.9844 | -0.2982 | 0.98526 | -0.28157 | 19.5115
103 | 0.014886 | 0.0037341 | -0.014875 | -0.0037281 | 1.0469e-05 | 6.0012e-06 | 0.022515 | 0.022515 | 0.022515 | 0.98386 | -0.30875 | 0.98311 | -0.32351 | 6.1855
104 | 0.0016548 | 0.00041464 | -0.0016548 | -0.00041473 | 1.9872e-08 | -9.2436e-08 | 0.0025162 | 0.0025162 | 0.0025162 | 0.9786 | -0.41245 | 0.97858 | -0.41271 | 0.69128
105 | -0.015425 | -0.0038747 | 0.015427 | 0.0038756 | 1.5114e-06 | 8.7367e-07 | 0.023358 | 0.023358 | 0.023358 | 0.98279 | -0.33046 | 0.98289 | -0.32841 | 6.4171
106 | 0.02046 | 0.0051382 | -0.020456 | -0.0051361 | 3.4996e-06 | 2.1164e-06 | 0.030973 | 0.030973 | 0.030973 | 0.98308 | -0.32482 | 0.98289 | -0.32841 | 8.5089
107 | -0.02046 | -0.0051382 | 0.020466 | 0.0051418 | 5.9204e-06 | 3.5803e-06 | 0.030973 | 0.030972 | 0.030973 | 0.98308 | -0.32482 | 0.98339 | -0.31876 | 8.5089
108 | -0.032091 | -0.0080554 | 0.032104 | 0.0080636 | 1.3073e-05 | 8.1791e-06 | 0.048564 | 0.048564 | 0.048564 | 0.98339 | -0.31876 | 0.98382 | -0.31022 | 13.3417
109 | -0.095117 | -0.023938 | 0.095284 | 0.024045 | 0.00016728 | 0.00010678 | 0.1439 | 0.1439 | 0.1439 | 0.98382 | -0.31022 | 0.98571 | -0.2735 | 39.5325
110 | 0.063013 | 0.015874 | -0.062927 | -0.01582 | 8.5726e-05 | 5.4546e-05 | 0.095335 | 0.095335 | 0.095335 | 0.98382 | -0.31022 | 0.98236 | -0.33871 | 26.1909
111 | 0.16151 | 0.04105 | -0.16144 | -0.041005 | 7.1253e-05 | 4.4928e-05 | 0.24191 | 0.24191 | 0.24191 | 0.99429 | -0.10832 | 0.99381 | -0.11749 | 16.6149
112 | 0.31328 | 0.079568 | -0.31307 | -0.079434 | 0.00021 | 0.00013388 | 0.47148 | 0.47148 | 0.47148 | 0.9895 | -0.19985 | 0.98878 | -0.21378 | 32.382
113 | 0.087725 | 0.022166 | -0.087683 | -0.022141 | 4.1526e-05 | 2.5284e-05 | 0.13231 | 0.13231 | 0.13231 | 0.98705 | -0.24726 | 0.98654 | -0.25714 | 9.0875
114 | 0.0020162 | 0.00050395 | -0.0020161 | -0.0005044 | 1.4572e-07 | -4.4562e-07 | 0.0030374 | 0.0030375 | 0.0030375 | 0.98759 | -0.23673 | 0.98751 | -0.23825 | 0.83449
115 | -0.10853 | -0.027426 | 0.10855 | 0.027442 | 2.6286e-05 | 1.6285e-05 | 0.16345 | 0.16345 | 0.16345 | 0.98852 | -0.21883 | 0.98878 | -0.21378 | 11.2258
116 | -0.12488 | -0.031559 | 0.12489 | 0.031567 | 1.2494e-05 | 7.9842e-06 | 0.18816 | 0.18816 | 0.18816 | 0.98807 | -0.22779 | 0.98818 | -0.2257 | 51.6911
117 | -0.1913 | -0.048435 | 0.19162 | 0.048641 | 0.00032408 | 0.0002053 | 0.28909 | 0.28909 | 0.28909 | 0.98526 | -0.28157 | 0.98709 | -0.24636 | 19.8549
118 | 0.0071594 | 0.0017947 | -0.0071584 | -0.0017943 | 9.9134e-07 | 3.5668e-07 | 0.01091 | 0.01091 | 0.01091 | 0.97648 | -0.45287 | 0.97633 | -0.45577 | 2.9973
119 | -0.0071563 | -0.0017935 | 0.0071584 | 0.0017943 | 2.1814e-06 | 7.8516e-07 | 0.01091 | 0.01091 | 0.01091 | 0.97601 | -0.46217 | 0.97633 | -0.45577 | 2.9974
120 | -0.19858 | -0.050385 | 0.19868 | 0.050449 | 0.00010057 | 6.3751e-05 | 0.29958 | 0.29958 | 0.29958 | 0.98709 | -0.24636 | 0.98763 | -0.23583 | 20.5754
121 | -0.20232 | -0.051381 | 0.20247 | 0.051475 | 0.00014922 | 9.4625e-05 | 0.30498 | 0.30498 | 0.30498 | 0.98791 | -0.23039 | 0.98871 | -0.21508 | 20.9466
122 | 0.19873 | 0.050482 | -0.19868 | -0.050449 | 5.2008e-05 | 3.2968e-05 | 0.29958 | 0.29958 | 0.29958 | 0.98791 | -0.23039 | 0.98763 | -0.23583 | 20.5754
123 | -0.2045 | -0.051984 | 0.20451 | 0.051992 | 1.2771e-05 | 8.0996e-06 | 0.30803 | 0.30803 | 0.30803 | 0.98871 | -0.21508 | 0.98878 | -0.21378 | 21.1562
124 | -0.0048445 | -0.0012142 | 0.0048446 | 0.0012142 | 3.0183e-08 | -9.6605e-10 | 0.007212 | 0.007212 | 0.007212 | 0.99955 | -0.0087333 | 0.99955 | -0.0086026 | 1.9813
125 | -0.006679 | -0.0016739 | 0.0066791 | 0.0016739 | 8.1505e-08 | 2.3346e-08 | 0.009943 | 0.009943 | 0.009943 | 0.99955 | -0.0086026 | 0.99957 | -0.0083464 | 2.7316
126 | -0.0086404 | -0.0021655 | 0.0086426 | 0.0021664 | 2.2039e-06 | 9.4474e-07 | 0.012863 | 0.012862 | 0.012863 | 0.99957 | -0.0083464 | 0.99984 | -0.0029932 | 3.5337
127 | -0.13482 | -0.034056 | 0.13529 | 0.034356 | 0.00046924 | 0.00029993 | 0.20311 | 0.20311 | 0.20311 | 0.98818 | -0.2257 | 0.99194 | -0.15336 | 55.7998
128 | -0.13795 | -0.035023 | 0.13803 | 0.035073 | 7.7909e-05 | 4.9799e-05 | 0.20711 | 0.20711 | 0.20711 | 0.99194 | -0.15336 | 0.99255 | -0.14163 | 56.897
129 | 0.0025349 | 0.00063515 | -0.0025348 | -0.00063529 | 7.7073e-08 | -1.4007e-07 | 0.0037725 | 0.0037726 | 0.0037726 | 0.99984 | -0.0029932 | 0.99981 | -0.0036315 | 1.0364
130 | 0.017396 | 0.0043612 | -0.017395 | -0.0043607 | 9.342e-07 | 5.5031e-07 | 0.026048 | 0.026048 | 0.026048 | 0.99381 | -0.11749 | 0.99375 | -0.11862 | 7.156
131 | 0.14404 | 0.036644 | -0.14387 | -0.036537 | 0.00016734 | 0.0001066 | 0.21587 | 0.21587 | 0.21587 | 0.99381 | -0.11749 | 0.99255 | -0.14163 | 29.6519
132 | 0.015248 | 0.0038226 | -0.015247 | -0.0038215 | 1.933e-06 | 1.109e-06 | 0.022833 | 0.022833 | 0.022833 | 0.99375 | -0.11862 | 0.99361 | -0.12128 | 6.2728
133 | 0.012468 | 0.0031252 | -0.012467 | -0.0031246 | 1.107e-06 | 5.988e-07 | 0.018672 | 0.018672 | 0.018672 | 0.99361 | -0.12128 | 0.99352 | -0.12314 | 5.1298
134 | 0.0096089 | 0.0024083 | -0.0096082 | -0.0024079 | 7.343e-07 | 3.4753e-07 | 0.014392 | 0.014392 | 0.014392 | 0.99352 | -0.12314 | 0.99344 | -0.12474 | 3.9537
135 | 0.087683 | 0.022141 | -0.087679 | -0.022138 | 4.6137e-06 | 2.8092e-06 | 0.13231 | 0.13231 | 0.13231 | 0.98654 | -0.25714 | 0.98648 | -0.25824 | 9.0875
136 | 0.0020161 | 0.0005044 | -0.0020159 | -0.00050477 | 1.223e-07 | -3.739e-07 | 0.0030375 | 0.0030377 | 0.0030377 | 0.98751 | -0.23825 | 0.98745 | -0.23952 | 0.83453
137 | 0.0073311 | 0.0018372 | -0.0073306 | -0.001837 | 5.4616e-07 | 1.9317e-07 | 0.010981 | 0.010981 | 0.010981 | 0.99344 | -0.12474 | 0.99335 | -0.12631 | 3.0167
138 | 0.0050566 | 0.0012671 | -0.0050564 | -0.0012671 | 2.6046e-07 | 9.9899e-09 | 0.0075746 | 0.0075747 | 0.0075747 | 0.99335 | -0.12631 | 0.9933 | -0.12739 | 2.0809
139 | 0.0025315 | 0.00063432 | -0.0025315 | -0.00063444 | 7.0159e-08 | -1.2348e-07 | 0.0037923 | 0.0037924 | 0.0037924 | 0.9933 | -0.12739 | 0.99327 | -0.12797 | 1.0419
140 | 0.0020159 | 0.00050477 | -0.0020158 | -0.0005052 | 1.4159e-07 | -4.3273e-07 | 0.0030377 | 0.0030379 | 0.0030379 | 0.98745 | -0.23952 | 0.98737 | -0.241 | 0.83458

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52138 | 0.13345

## res_load
| p_mw | q_mvar
0 | 0.0021882 | 0.00054842
1 | 0.00403 | 0.00101
2 | 0.00087791 | 0.00022003
3 | 0.0029661 | 0.00074339
4 | 0.00066776 | 0.00016736
5 | 0.0016642 | 0.00041708
6 | 0.0015763 | 0.00039507
7 | 0.00024748 | 6.2024e-05
8 | 0.004988 | 0.0012501
9 | 8.1707e-05 | 2.0478e-05
10 | 0.00054838 | 0.00013744
11 | 0.00028955 | 7.2567e-05
12 | 0.00024557 | 6.1545e-05
13 | 0.00043795 | 0.00010976
14 | 0.00072509 | 0.00018173
15 | 0.0015235 | 0.00038182
16 | 0.0002887 | 7.2354e-05
17 | 0.00025972 | 6.5091e-05
18 | 0.00010151 | 2.5441e-05
19 | 0.00017777 | 4.4552e-05
20 | 0.00090924 | 0.00022788
21 | 0.00068907 | 0.0001727
22 | 0.0091643 | 0.0022968
23 | 0.0017439 | 0.00043707
24 | 0.0092843 | 0.0023269
25 | 0.009344 | 0.0023418
26 | 0.0044181 | 0.0011073
27 | 0.010177 | 0.0025507
28 | 0.002169 | 0.00054361
29 | 0.0013615 | 0.00034123
30 | 0.001002 | 0.00025112
31 | 0.0018461 | 0.00046267
32 | 0.0085688 | 0.0021475
33 | 0.00069649 | 0.00017456
34 | 0.0026297 | 0.00065907
35 | 0.0018106 | 0.00045379
36 | 0.0099751 | 0.0025
37 | 0.0071883 | 0.0018015
38 | 0.0010369 | 0.00025986
39 | 0.0028791 | 0.00072158
40 | 0.00174 | 0.00043607
41 | 0.001825 | 0.0004574
42 | 0.0022256 | 0.00055778
43 | 0.0020466 | 0.00051294
44 | 0.0043179 | 0.0010822
45 | 0.0018299 | 0.0004586
46 | 0.0016388 | 0.00041073
47 | 0.053263 | 0.013349
48 | 0.0034614 | 0.00086752
49 | 0.0020823 | 0.00052188
50 | 0.013379 | 0.0033531
51 | 0.057602 | 0.014436
52 | 0.0095866 | 0.0024026
53 | 0.0012846 | 0.00032196
54 | 0.0018532 | 0.00046446
55 | 0.010165 | 0.0025477
56 | 0.0087287 | 0.0021876
57 | 0.010203 | 0.0025572
58 | 0.0069606 | 0.0017445
59 | 0.00099084 | 0.00024833
60 | 0.00056839 | 0.00014245
61 | 0.0017717 | 0.00044403
62 | 0.0021037 | 0.00052725
63 | 0.0017942 | 0.00044968
64 | 0.0042967 | 0.0010768
65 | 0.010586 | 0.0026531
66 | 0.0039226 | 0.0009831
67 | 0.0046173 | 0.0011572
68 | 0.0016616 | 0.00041644
69 | 0.0012716 | 0.00031869
70 | 0.0016548 | 0.00041473
71 | 0.0050295 | 0.0012605
72 | 0.011626 | 0.0029136
73 | 0.0091838 | 0.0023017
74 | 0.0099909 | 0.0025039
75 | 0.0032441 | 0.00081306
76 | 0.0085144 | 0.0021339
77 | 0.0061315 | 0.0015367
78 | 0.005259 | 0.001318
79 | 0.0018145 | 0.00045475
80 | 0.0043946 | 0.0011014
81 | 0.009992 | 0.0025042
82 | 0.0033107 | 0.00082975
83 | 0.014875 | 0.0037281
84 | 0.0071563 | 0.0017935
85 | 0.0069592 | 0.0017441
86 | 0.0035884 | 0.00089933
87 | 0.0020282 | 0.00050831
88 | 0.0048445 | 0.0012142
89 | 0.0018345 | 0.00045976
90 | 0.0019612 | 0.00049153
91 | 0.009932 | 0.0024892
92 | 0.0026625 | 0.00066729
93 | 0.0025348 | 0.00063529
94 | 0.002147 | 0.00053809
95 | 0.0058436 | 0.0014645
96 | 0.0027783 | 0.00069631
97 | 0.0028582 | 0.00071633
98 | 0.0022771 | 0.00057069
99 | 0.002274 | 0.00056991
100 | 0.0025248 | 0.00063278
101 | 0.0025315 | 0.00063444
102 | 0.0020158 | 0.0005052
103 | 0.009029 | 0.0022629

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1