## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1707-16_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1707-16_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1707-16_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1707-16_0_3_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1707-16_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1707-16_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1707-16_0_3_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_1707-16_0_3_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1707-16_0_3_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1707-16_0_3_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_1707-16_0_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1707-16_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1707-16_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1707-16_0_3_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_1707-16_0_3_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_1707-16_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1707-16_0_3_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_1707-16_0_3_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1707-16_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1707-16_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1707-16_0_3_node_48 | 0.4 | n |  | TRUE
21 | bus_LV_1707-16_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1707-16_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1707-16_0_3_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_1707-16_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1707-16_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1707-16_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1707-16_0_3_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_1707-16_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1707-16_0_3_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1707-16_0_3_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1707-16_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1707-16_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_1707-16_0_3_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1707-16_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1707-16_0_3_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1707-16_0_3_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_1707-16_0_3_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_1707-16_0_3_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_1707-16_0_3_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1707-16_0_3_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_1707-16_0_3_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_1707-16_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1707-16_0_3_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_1707-16_0_3_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_1707-16_0_3_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1707-16_0_3_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_1707-16_0_3_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_1707-16_0_3_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_1707-16_0_3_node_44 | 0.4 | n |  | TRUE
50 | bus_MV_0_0_node_54 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1707-16_0_3_load_0 | 0 | 0.01146 | 0.0028723 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1707-16_0_3_load_1 | 1 | 0.012799 | 0.0032077 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1707-16_0_3_load_3 | 5 | 0.012991 | 0.0032558 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1707-16_0_3_load_29 | 6 | 0.012718 | 0.0031873 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1707-16_0_3_load_28 | 7 | 0.012654 | 0.0031714 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1707-16_0_3_load_4 | 8 | 0.016897 | 0.0042347 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1707-16_0_3_load_51 | 9 | 0.006822 | 0.0017098 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1707-16_0_3_load_27 | 10 | 0.012565 | 0.003149 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1707-16_0_3_load_6 | 11 | 0.016454 | 0.0041237 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1707-16_0_3_load_8 | 12 | 0.0051089 | 0.0012804 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1707-16_0_3_load_26 | 13 | 0.01706 | 0.0042756 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1707-16_0_3_load_22 | 14 | 0.017791 | 0.0044588 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1707-16_0_3_load_46 | 16 | 0.016439 | 0.0041199 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1707-16_0_3_load_48 | 20 | 0.0096535 | 0.0024194 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1707-16_0_3_load_11 | 22 | 0.0082889 | 0.0020774 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1707-16_0_3_load_47 | 23 | 0.016186 | 0.0040566 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1707-16_0_3_load_15 | 25 | 0.0084127 | 0.0021084 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1707-16_0_3_load_16 | 26 | 0.0083358 | 0.0020891 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1707-16_0_3_load_49 | 27 | 0.002745 | 0.00068795 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1707-16_0_3_load_30 | 31 | 0.0073815 | 0.00185 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1707-16_0_3_load_18 | 32 | 0.0076978 | 0.0019292 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1707-16_0_3_load_21 | 34 | 0.014915 | 0.003738 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1707-16_0_3_load_33 | 36 | 0.0075541 | 0.0018932 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1707-16_0_3_load_41 | 37 | 0.0052247 | 0.0013094 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1707-16_0_3_load_39 | 38 | 0.004602 | 0.0011534 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1707-16_0_3_load_24 | 39 | 0.010306 | 0.0025829 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1707-16_0_3_load_43 | 42 | 0.0029747 | 0.00074552 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1707-16_0_3_load_42 | 43 | 0.0053549 | 0.0013421 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1707-16_0_3_load_35 | 44 | 0.0043331 | 0.001086 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1707-16_0_3_load_38 | 46 | 0.0043332 | 0.001086 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1707-16_0_3_load_44 | 49 | 0.00066932 | 0.00016775 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1707-16_0_3_line_0 |  | 0 | 1 | 0.0072159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1707-16_0_3_line_1 |  | 1 | 2 | 0.042375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1707-16_0_3_line_2 |  | 1 | 3 | 0.041525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1707-16_0_3_line_3 |  | 2 | 5 | 0.021129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1707-16_0_3_line_4 |  | 3 | 4 | 0.058555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1707-16_0_3_line_5 |  | 4 | 13 | 0.037489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1707-16_0_3_line_6 |  | 4 | 14 | 0.026496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1707-16_0_3_line_7 |  | 5 | 6 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1707-16_0_3_line_8 |  | 6 | 7 | 0.017812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1707-16_0_3_line_9 |  | 7 | 10 | 0.017216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1707-16_0_3_line_10 |  | 8 | 9 | 0.03355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1707-16_0_3_line_11 |  | 8 | 10 | 0.057443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1707-16_0_3_line_12 |  | 11 | 12 | 0.067226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1707-16_0_3_line_13 |  | 12 | 15 | 0.023604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1707-16_0_3_line_14 |  | 13 | 16 | 0.025921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1707-16_0_3_line_15 |  | 14 | 17 | 0.014063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1707-16_0_3_line_16 |  | 15 | 18 | 0.038611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1707-16_0_3_line_17 |  | 17 | 34 | 0.013973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1707-16_0_3_line_18 |  | 18 | 19 | 0.036327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1707-16_0_3_line_19 |  | 18 | 20 | 0.02503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1707-16_0_3_line_20 |  | 19 | 21 | 0.03684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1707-16_0_3_line_21 |  | 19 | 22 | 0.020042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1707-16_0_3_line_22 |  | 20 | 23 | 0.025753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1707-16_0_3_line_23 |  | 21 | 27 | 0.011021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1707-16_0_3_line_24 |  | 21 | 28 | 0.011178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1707-16_0_3_line_25 |  | 24 | 25 | 0.013721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1707-16_0_3_line_26 |  | 24 | 26 | 0.018135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1707-16_0_3_line_27 |  | 25 | 29 | 0.035845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1707-16_0_3_line_28 |  | 28 | 30 | 0.029334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1707-16_0_3_line_29 |  | 28 | 31 | 0.023639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1707-16_0_3_line_30 |  | 29 | 32 | 0.006114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1707-16_0_3_line_31 |  | 29 | 33 | 0.009775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1707-16_0_3_line_32 |  | 30 | 44 | 0.016925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1707-16_0_3_line_33 |  | 31 | 32 | 0.029584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1707-16_0_3_line_34 |  | 33 | 35 | 0.028537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1707-16_0_3_line_35 |  | 33 | 36 | 0.014269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1707-16_0_3_line_36 |  | 34 | 40 | 0.034367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1707-16_0_3_line_37 |  | 35 | 37 | 0.017122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1707-16_0_3_line_38 |  | 35 | 38 | 0.0054549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1707-16_0_3_line_39 |  | 36 | 39 | 0.029415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1707-16_0_3_line_40 |  | 37 | 43 | 0.023001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1707-16_0_3_line_41 |  | 38 | 48 | 0.011803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1707-16_0_3_line_42 |  | 39 | 40 | 0.0056853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1707-16_0_3_line_43 |  | 41 | 42 | 0.010095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1707-16_0_3_line_44 |  | 41 | 43 | 0.020092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1707-16_0_3_line_45 |  | 45 | 46 | 0.019529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1707-16_0_3_line_46 |  | 45 | 47 | 0.11488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1707-16_0_3_line_47 |  | 46 | 48 | 0.011591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1707-16_0_3_line_48 |  | 47 | 49 | 0.0097576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1707-16_0_3_trafo_46 | 0.63 MVA 20/0.4 kV | 50 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2675029.8436 | 1221995.4953 | 2675029.7953 | 1222002.7111
1 | 2675071.7256 | 1222004.207 | 2675066.3448 | 1222001.9933 | 2675029.7953 | 1222002.7111 | 2675029.7953 | 1222002.7111
2 | 2674992.0062 | 1222019.9242 | 2675029.7953 | 1222002.7111
3 | 2675071.7256 | 1222004.207 | 2675068.4025 | 1222019.2861 | 2675067.5692 | 1222024.9125
4 | 2674964.7784 | 1222004.4825 | 2674968.8052 | 1221995.5384 | 2674968.9627 | 1221988.4579 | 2674969.9617 | 1221986.8361 | 2674992.0062 | 1222019.9242
5 | 2674964.7784 | 1222004.4825 | 2674963.1746 | 1222007.7422 | 2674963.0788 | 1222009.9313 | 2674964.2142 | 1222012.5362 | 2674970.3551 | 1222020.0406 | 2674970.9114 | 1222022.2491 | 2674970.6945 | 1222024.4144 | 2674961.702 | 1222036.009
6 | 2674964.7784 | 1222004.4825 | 2674952.3234 | 1221996.5872 | 2674947.7425 | 1221997.1188 | 2674942.7444 | 1222002.2139
7 | 2675065.0844 | 1222042.4613 | 2675065.2847 | 1222040.3384 | 2675067.5692 | 1222024.9125
8 | 2675063.411 | 1222060.1945 | 2675065.0844 | 1222042.4613
9 | 2675062.7844 | 1222077.3992 | 2675062.7917 | 1222076.8198 | 2675063.411 | 1222060.1945 | 2675063.411 | 1222060.1945
10 | 2675011.7502 | 1222103.7664 | 2674994.4037 | 1222132.4838
11 | 2675011.7502 | 1222103.7664 | 2675062.7844 | 1222077.3992
12 | 2674933.638 | 1222132.7086 | 2674945.2362 | 1222116.6434 | 2674951.2891 | 1222108.8478 | 2674962.2105 | 1222092.1298 | 2674973.6617 | 1222078.801
13 | 2674919.8214 | 1222151.8467 | 2674933.638 | 1222132.7086
14 | 2674945.8162 | 1222056.4915 | 2674961.702 | 1222036.009
15 | 2674932.8963 | 1222012.253 | 2674942.7444 | 1222002.2139
16 | 2674889.5931 | 1222127.7174 | 2674913.7175 | 1222146.8222 | 2674919.8214 | 1222151.8467
17 | 2674932.8963 | 1222012.253 | 2674921.9765 | 1222003.5345
18 | 2674860.7975 | 1222105.4631 | 2674889.5931 | 1222127.7174
19 | 2674889.5931 | 1222127.7174 | 2674905.4294 | 1222108.334
20 | 2674860.7975 | 1222105.4631 | 2674831.6577 | 1222082.8154
21 | 2674860.7975 | 1222105.4631 | 2674873.1672 | 1222089.6941
22 | 2674905.4294 | 1222108.334 | 2674916.6659 | 1222094.5806 | 2674921.5676 | 1222088.2675
23 | 2674831.6577 | 1222082.8154 | 2674838.6001 | 1222074.2414
24 | 2674822.8158 | 1222075.9442 | 2674831.6577 | 1222082.8154
25 | 2674897.4936 | 1222058.6826 | 2674886.638 | 1222050.2915
26 | 2674897.4936 | 1222058.6826 | 2674906.7819 | 1222048.1592 | 2674909.1928 | 1222044.8444
27 | 2674858.2777 | 1222028.3698 | 2674886.638 | 1222050.2915
28 | 2674822.8158 | 1222075.9442 | 2674799.8415 | 1222057.6215
29 | 2674822.8158 | 1222075.9442 | 2674836.9434 | 1222056.991
30 | 2674858.2777 | 1222028.3698 | 2674854.6237 | 1222033.2718
31 | 2674858.2777 | 1222028.3698 | 2674864.2465 | 1222020.6175
32 | 2674799.8415 | 1222057.6215 | 2674810.1566 | 1222044.2025
33 | 2674836.9434 | 1222056.991 | 2674854.6237 | 1222033.2718
34 | 2674840.9931 | 1222003.981 | 2674864.2465 | 1222020.6175
35 | 2674864.2465 | 1222020.6175 | 2674873.1698 | 1222009.4823
36 | 2674895.1196 | 1221982.0915 | 2674921.9765 | 1222003.5345
37 | 2674840.9931 | 1222003.981 | 2674851.3114 | 1221990.3172
38 | 2674840.9931 | 1222003.981 | 2674837.6848 | 1222008.3183
39 | 2674873.1698 | 1222009.4823 | 2674891.5644 | 1221986.528
40 | 2674851.3114 | 1221990.3172 | 2674865.1726 | 1221971.9619
41 | 2674830.5267 | 1222017.703 | 2674837.6848 | 1222008.3183
42 | 2674895.1196 | 1221982.0915 | 2674891.5644 | 1221986.528
43 | 2674877.2808 | 1221955.9278 | 2674869.3653 | 1221949.6631
44 | 2674877.2808 | 1221955.9278 | 2674865.1726 | 1221971.9619
45 | 2674805.8382 | 1221998.7582 | 2674821.3312 | 1222010.6468
46 | 2674805.8382 | 1221998.7582 | 2674695.0821 | 1221968.2705
47 | 2674830.5267 | 1222017.703 | 2674821.3312 | 1222010.6468
48 | 2674695.0821 | 1221968.2705 | 2674685.3685 | 1221967.345

## bus_geodata
| x | y | coords
0 | 2675029.8436 | 1221995.4953
1 | 2675029.7953 | 1222002.7111
2 | 2675071.7256 | 1222004.207
3 | 2674992.0062 | 1222019.9242
4 | 2674964.7784 | 1222004.4825
5 | 2675067.5692 | 1222024.9125
6 | 2675065.0844 | 1222042.4613
7 | 2675063.411 | 1222060.1945
8 | 2675011.7502 | 1222103.7664
9 | 2674994.4037 | 1222132.4838
10 | 2675062.7844 | 1222077.3992
11 | 2674973.6617 | 1222078.801
12 | 2674933.638 | 1222132.7086
13 | 2674961.702 | 1222036.009
14 | 2674942.7444 | 1222002.2139
15 | 2674919.8214 | 1222151.8467
16 | 2674945.8162 | 1222056.4915
17 | 2674932.8963 | 1222012.253
18 | 2674889.5931 | 1222127.7174
19 | 2674860.7975 | 1222105.4631
20 | 2674905.4294 | 1222108.334
21 | 2674831.6577 | 1222082.8154
22 | 2674873.1672 | 1222089.6941
23 | 2674921.5676 | 1222088.2675
24 | 2674897.4936 | 1222058.6826
25 | 2674886.638 | 1222050.2915
26 | 2674909.1928 | 1222044.8444
27 | 2674838.6001 | 1222074.2414
28 | 2674822.8158 | 1222075.9442
29 | 2674858.2777 | 1222028.3698
30 | 2674799.8415 | 1222057.6215
31 | 2674836.9434 | 1222056.991
32 | 2674854.6237 | 1222033.2718
33 | 2674864.2465 | 1222020.6175
34 | 2674921.9765 | 1222003.5345
35 | 2674840.9931 | 1222003.981
36 | 2674873.1698 | 1222009.4823
37 | 2674851.3114 | 1221990.3172
38 | 2674837.6848 | 1222008.3183
39 | 2674891.5644 | 1221986.528
40 | 2674895.1196 | 1221982.0915
41 | 2674877.2808 | 1221955.9278
42 | 2674869.3653 | 1221949.6631
43 | 2674865.1726 | 1221971.9619
44 | 2674810.1566 | 1222044.2025
45 | 2674805.8382 | 1221998.7582
46 | 2674821.3312 | 1222010.6468
47 | 2674695.0821 | 1221968.2705
48 | 2674830.5267 | 1222017.703
49 | 2674685.3685 | 1221967.345
50 | 2674964.7784 | 1222004.4825

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9854 | -0.27908 | 0.01146 | 0.0028723
1 | 0.98548 | -0.2776 | 0.012799 | 0.0032077
2 | 0.98255 | -0.33454 | 0 | 0
3 | 0.98928 | -0.20417 | 0 | 0
4 | 0.99464 | -0.10158 | 0 | 0
5 | 0.98109 | -0.36306 | 0.012991 | 0.0032558
6 | 0.98008 | -0.38287 | 0.012718 | 0.0031873
7 | 0.97927 | -0.3987 | 0.012654 | 0.0031714
8 | 0.97742 | -0.43489 | 0.016897 | 0.0042347
9 | 0.97721 | -0.43907 | 0.006822 | 0.0017098
10 | 0.97869 | -0.41006 | 0.012565 | 0.003149
11 | 0.97311 | -0.51933 | 0.016454 | 0.0041237
12 | 0.97414 | -0.49899 | 0.0051089 | 0.0012804
13 | 0.99773 | -0.042917 | 0.01706 | 0.0042756
14 | 0.99327 | -0.12781 | 0.017791 | 0.0044588
15 | 0.97461 | -0.48964 | 0 | 0
16 | 1 | 0 | -0.29055 | -0.074183
17 | 0.99261 | -0.14029 | 0 | 0
18 | 0.97539 | -0.47438 | 0 | 0
19 | 0.97699 | -0.44288 | 0 | 0
20 | 0.97478 | -0.48623 | 0.0096535 | 0.0024194
21 | 0.9789 | -0.40548 | 0 | 0
22 | 0.97684 | -0.44591 | 0.0082889 | 0.0020774
23 | 0.9744 | -0.49388 | 0.016186 | 0.0040566
24 | 0.9826 | -0.33347 | 0 | 0
25 | 0.98271 | -0.3314 | 0.0084127 | 0.0021084
26 | 0.98246 | -0.33619 | 0.0083358 | 0.0020891
27 | 0.97887 | -0.40603 | 0.002745 | 0.00068795
28 | 0.97951 | -0.39361 | 0 | 0
29 | 0.98326 | -0.32057 | 0 | 0
30 | 0.97939 | -0.39592 | 0 | 0
31 | 0.98089 | -0.36668 | 0.0073815 | 0.00185
32 | 0.98282 | -0.32916 | 0.0076978 | 0.0019292
33 | 0.98412 | -0.30391 | 0 | 0
34 | 0.99197 | -0.1527 | 0.014915 | 0.003738
35 | 0.98351 | -0.31582 | 0 | 0
36 | 0.98568 | -0.27371 | 0.0075541 | 0.0018932
37 | 0.98329 | -0.32 | 0.0052247 | 0.0013094
38 | 0.98346 | -0.31676 | 0.004602 | 0.0011534
39 | 0.98909 | -0.2078 | 0.010306 | 0.0025829
40 | 0.98981 | -0.19407 | 0 | 0
41 | 0.98306 | -0.32453 | 0 | 0
42 | 0.98303 | -0.32508 | 0.0029747 | 0.00074552
43 | 0.98312 | -0.32346 | 0.0053549 | 0.0013421
44 | 0.97932 | -0.39725 | 0.0043331 | 0.001086
45 | 0.98334 | -0.31911 | 0 | 0
46 | 0.98335 | -0.31887 | 0.0043332 | 0.001086
47 | 0.98327 | -0.3205 | 0 | 0
48 | 0.98341 | -0.31783 | 0 | 0
49 | 0.98326 | -0.32062 | 0.00066932 | 0.00016775
50 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01146 | -0.0028723 | 0.011461 | 0.0028727 | 8.1042e-07 | 4.2674e-07 | 0.017306 | 0.017306 | 0.017306 | 0.9854 | -0.27908 | 0.98548 | -0.2776 | 4.7544
1 | 0.075097 | 0.018994 | -0.074892 | -0.018864 | 0.00020454 | 0.00013037 | 0.11345 | 0.11345 | 0.11345 | 0.98548 | -0.2776 | 0.98255 | -0.33454 | 31.1685
2 | -0.099357 | -0.025074 | 0.099708 | 0.025298 | 0.00035076 | 0.00022396 | 0.15008 | 0.15008 | 0.15008 | 0.98548 | -0.2776 | 0.98928 | -0.20417 | 41.2321
3 | 0.074892 | 0.018864 | -0.07479 | -0.018799 | 0.00010199 | 6.5004e-05 | 0.11345 | 0.11345 | 0.11345 | 0.98255 | -0.33454 | 0.98109 | -0.36306 | 31.1686
4 | -0.099708 | -0.025298 | 0.1002 | 0.025614 | 0.00049461 | 0.0003158 | 0.15008 | 0.15008 | 0.15008 | 0.98928 | -0.20417 | 0.99464 | -0.10158 | 41.2321
5 | -0.27047 | -0.069033 | 0.27124 | 0.069524 | 0.00076894 | 0.00049066 | 0.40508 | 0.40508 | 0.40508 | 0.99464 | -0.10158 | 0.99773 | -0.042917 | 37.095
6 | 0.17027 | 0.043419 | -0.17005 | -0.043282 | 0.00021535 | 0.00013679 | 0.25499 | 0.25499 | 0.25499 | 0.99464 | -0.10158 | 0.99327 | -0.12781 | 23.3511
7 | 0.061799 | 0.015543 | -0.061741 | -0.015506 | 5.8425e-05 | 3.7169e-05 | 0.093751 | 0.093751 | 0.093751 | 0.98109 | -0.36306 | 0.98008 | -0.38287 | 25.7557
8 | 0.049023 | 0.012318 | -0.048986 | -0.012295 | 3.7015e-05 | 2.3466e-05 | 0.074442 | 0.074442 | 0.074442 | 0.98008 | -0.38287 | 0.97927 | -0.3987 | 20.4511
9 | 0.036332 | 0.0091235 | -0.036313 | -0.0091111 | 1.9682e-05 | 1.238e-05 | 0.055214 | 0.055214 | 0.055214 | 0.97927 | -0.3987 | 0.97869 | -0.41006 | 15.1687
10 | 0.0068234 | 0.0017102 | -0.006822 | -0.0017098 | 1.3576e-06 | 4.4847e-07 | 0.010388 | 0.010388 | 0.010388 | 0.97742 | -0.43489 | 0.97721 | -0.43907 | 2.8538
11 | -0.02372 | -0.0059449 | 0.023748 | 0.0059621 | 2.8089e-05 | 1.7256e-05 | 0.036111 | 0.036111 | 0.036111 | 0.97742 | -0.43489 | 0.97869 | -0.41006 | 9.9206
12 | -0.016454 | -0.0041237 | 0.01647 | 0.004133 | 1.5958e-05 | 9.3771e-06 | 0.02516 | 0.02516 | 0.02516 | 0.97311 | -0.51933 | 0.97414 | -0.49899 | 6.9121
13 | -0.021578 | -0.0054135 | 0.021588 | 0.0054193 | 9.6181e-06 | 5.8616e-06 | 0.032964 | 0.032963 | 0.032964 | 0.97414 | -0.49899 | 0.97461 | -0.48964 | 9.0559
14 | -0.2883 | -0.073799 | 0.2889 | 0.074183 | 0.00060055 | 0.00038333 | 0.43052 | 0.43052 | 0.43052 | 0.99773 | -0.042917 | 1 | 0 | 39.4249
15 | 0.15226 | 0.038823 | -0.15217 | -0.038765 | 9.1656e-05 | 5.8114e-05 | 0.22834 | 0.22834 | 0.22834 | 0.99327 | -0.12781 | 0.99261 | -0.14029 | 20.9104
16 | -0.021588 | -0.0054193 | 0.021604 | 0.0054289 | 1.5733e-05 | 9.5875e-06 | 0.032963 | 0.032963 | 0.032963 | 0.97461 | -0.48964 | 0.97539 | -0.47438 | 9.0559
17 | 0.15217 | 0.038765 | -0.15208 | -0.038707 | 9.1071e-05 | 5.7744e-05 | 0.22834 | 0.22834 | 0.22834 | 0.99261 | -0.14029 | 0.99197 | -0.1527 | 20.9104
18 | -0.047464 | -0.011917 | 0.047535 | 0.011963 | 7.144e-05 | 4.5267e-05 | 0.072417 | 0.072417 | 0.072417 | 0.97539 | -0.47438 | 0.97699 | -0.44288 | 19.8948
19 | 0.02586 | 0.0064885 | -0.025845 | -0.0064794 | 1.4611e-05 | 9.0386e-06 | 0.039454 | 0.039454 | 0.039454 | 0.97539 | -0.47438 | 0.97478 | -0.48623 | 10.839
20 | -0.055825 | -0.014041 | 0.055925 | 0.014104 | 9.9915e-05 | 6.3483e-05 | 0.085043 | 0.085043 | 0.085043 | 0.97699 | -0.44288 | 0.9789 | -0.40548 | 23.3635
21 | 0.0082901 | 0.0020779 | -0.0082889 | -0.0020774 | 1.1982e-06 | 5.1591e-07 | 0.012626 | 0.012626 | 0.012626 | 0.97699 | -0.44288 | 0.97684 | -0.44591 | 3.4688
22 | 0.016192 | 0.00406 | -0.016186 | -0.0040566 | 5.9002e-06 | 3.4553e-06 | 0.024718 | 0.024718 | 0.024718 | 0.97478 | -0.48623 | 0.9744 | -0.49388 | 6.7906
23 | 0.002745 | 0.00068786 | -0.002745 | -0.00068795 | 7.1959e-08 | -9.2493e-08 | 0.0041727 | 0.0041727 | 0.0041727 | 0.9789 | -0.40548 | 0.97887 | -0.40603 | 1.1463
24 | -0.05867 | -0.014792 | 0.058704 | 0.014813 | 3.3364e-05 | 2.1212e-05 | 0.089216 | 0.089216 | 0.089216 | 0.9789 | -0.40548 | 0.97951 | -0.39361 | 24.5098
25 | -0.0083369 | -0.0020896 | 0.0083377 | 0.00209 | 8.2011e-07 | 3.5106e-07 | 0.012625 | 0.012625 | 0.012625 | 0.9826 | -0.33347 | 0.98271 | -0.3314 | 3.4684
26 | 0.0083369 | 0.0020896 | -0.0083358 | -0.0020891 | 1.084e-06 | 4.6407e-07 | 0.012625 | 0.012625 | 0.012625 | 0.9826 | -0.33347 | 0.98246 | -0.33619 | 3.4685
27 | -0.01675 | -0.0041984 | 0.016759 | 0.0042035 | 8.6473e-06 | 5.0799e-06 | 0.025364 | 0.025363 | 0.025364 | 0.98271 | -0.3314 | 0.98326 | -0.32057 | 6.968
28 | 0.0043338 | 0.0010859 | -0.0043334 | -0.0010859 | 4.7681e-07 | -6.4028e-08 | 0.0065836 | 0.0065838 | 0.0065838 | 0.97951 | -0.39361 | 0.97939 | -0.39592 | 1.8087
29 | -0.063037 | -0.015899 | 0.063119 | 0.015951 | 8.1356e-05 | 5.177e-05 | 0.095799 | 0.095799 | 0.095799 | 0.97951 | -0.39361 | 0.98089 | -0.36668 | 26.3185
30 | 0.078357 | 0.019831 | -0.078325 | -0.019811 | 3.2278e-05 | 2.058e-05 | 0.11865 | 0.11865 | 0.11865 | 0.98326 | -0.32057 | 0.98282 | -0.32916 | 32.5966
31 | -0.095116 | -0.024035 | 0.095192 | 0.024083 | 7.6026e-05 | 4.8533e-05 | 0.14401 | 0.14401 | 0.14401 | 0.98326 | -0.32057 | 0.98412 | -0.30391 | 39.5645
32 | 0.0043334 | 0.0010859 | -0.0043331 | -0.001086 | 2.7512e-07 | -3.6897e-08 | 0.0065838 | 0.0065839 | 0.0065839 | 0.97939 | -0.39592 | 0.97932 | -0.39725 | 1.8088
33 | -0.0705 | -0.017801 | 0.070627 | 0.017882 | 0.00012701 | 8.091e-05 | 0.107 | 0.107 | 0.107 | 0.98089 | -0.36668 | 0.98282 | -0.32916 | 29.3948
34 | 0.023177 | 0.0058125 | -0.023164 | -0.0058044 | 1.3144e-05 | 8.0496e-06 | 0.035046 | 0.035046 | 0.035046 | 0.98412 | -0.30391 | 0.98351 | -0.31582 | 9.6281
35 | -0.11837 | -0.029896 | 0.11854 | 0.030006 | 0.00017157 | 0.00010962 | 0.17906 | 0.17906 | 0.17906 | 0.98412 | -0.30391 | 0.98568 | -0.27371 | 49.1925
36 | 0.13717 | 0.034969 | -0.13689 | -0.034795 | 0.00027337 | 0.00017407 | 0.20597 | 0.20597 | 0.20597 | 0.99197 | -0.1527 | 0.98981 | -0.19407 | 28.2925
37 | 0.013559 | 0.0033989 | -0.013556 | -0.0033974 | 2.702e-06 | 1.5121e-06 | 0.020514 | 0.020514 | 0.020514 | 0.98351 | -0.31582 | 0.98329 | -0.32 | 5.6357
38 | 0.0096056 | 0.0024056 | -0.0096051 | -0.0024054 | 4.32e-07 | 2.0726e-07 | 0.014532 | 0.014532 | 0.014532 | 0.98351 | -0.31582 | 0.98346 | -0.31676 | 3.9924
39 | -0.1261 | -0.031899 | 0.1265 | 0.032155 | 0.00040016 | 0.00025573 | 0.19046 | 0.19046 | 0.19046 | 0.98568 | -0.27371 | 0.98909 | -0.2078 | 52.3255
40 | 0.0083312 | 0.0020879 | -0.0083298 | -0.0020873 | 1.371e-06 | 5.8574e-07 | 0.012607 | 0.012608 | 0.012608 | 0.98329 | -0.32 | 0.98312 | -0.32346 | 3.4636
41 | 0.0050031 | 0.001252 | -0.0050029 | -0.001252 | 2.5359e-07 | 1.2539e-08 | 0.0075693 | 0.0075693 | 0.0075693 | 0.98346 | -0.31676 | 0.98341 | -0.31783 | 2.0795
42 | -0.1368 | -0.034737 | 0.13689 | 0.034795 | 9.0446e-05 | 5.7812e-05 | 0.20597 | 0.20597 | 0.20597 | 0.98909 | -0.2078 | 0.98981 | -0.19407 | 56.5849
43 | 0.0029747 | 0.00074544 | -0.0029747 | -0.00074552 | 7.6748e-08 | -7.8864e-08 | 0.0045027 | 0.0045027 | 0.0045027 | 0.98306 | -0.32453 | 0.98303 | -0.32508 | 1.237
44 | -0.0029747 | -0.00074544 | 0.0029749 | 0.00074528 | 1.5275e-07 | -1.5699e-07 | 0.0045027 | 0.0045026 | 0.0045027 | 0.98306 | -0.32453 | 0.98312 | -0.32346 | 1.237
45 | -0.00066937 | -0.0001662 | 0.00066938 | 0.00016596 | 7.5047e-09 | -2.4294e-07 | 0.0010124 | 0.0010123 | 0.0010124 | 0.98334 | -0.31911 | 0.98335 | -0.31887 | 0.27812
46 | 0.00066937 | 0.0001662 | -0.00066933 | -0.00016763 | 4.4172e-08 | -1.4289e-06 | 0.0010124 | 0.0010129 | 0.0010129 | 0.98334 | -0.31911 | 0.98327 | -0.3205 | 0.27826
47 | -0.0050026 | -0.001252 | 0.0050029 | 0.001252 | 2.4904e-07 | 1.2332e-08 | 0.0075694 | 0.0075693 | 0.0075694 | 0.98335 | -0.31887 | 0.98341 | -0.31783 | 2.0795
48 | 0.00066933 | 0.00016763 | -0.00066932 | -0.00016775 | 3.7541e-09 | -1.2136e-07 | 0.0010129 | 0.0010129 | 0.0010129 | 0.98327 | -0.3205 | 0.98326 | -0.32062 | 0.27827

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30699 | 0.078303

## res_load
| p_mw | q_mvar
0 | 0.01146 | 0.0028723
1 | 0.012799 | 0.0032077
2 | 0.012991 | 0.0032558
3 | 0.012718 | 0.0031873
4 | 0.012654 | 0.0031714
5 | 0.016897 | 0.0042347
6 | 0.006822 | 0.0017098
7 | 0.012565 | 0.003149
8 | 0.016454 | 0.0041237
9 | 0.0051089 | 0.0012804
10 | 0.01706 | 0.0042756
11 | 0.017791 | 0.0044588
12 | 0.016439 | 0.0041199
13 | 0.0096535 | 0.0024194
14 | 0.0082889 | 0.0020774
15 | 0.016186 | 0.0040566
16 | 0.0084127 | 0.0021084
17 | 0.0083358 | 0.0020891
18 | 0.002745 | 0.00068795
19 | 0.0073815 | 0.00185
20 | 0.0076978 | 0.0019292
21 | 0.014915 | 0.003738
22 | 0.0075541 | 0.0018932
23 | 0.0052247 | 0.0013094
24 | 0.004602 | 0.0011534
25 | 0.010306 | 0.0025829
26 | 0.0029747 | 0.00074552
27 | 0.0053549 | 0.0013421
28 | 0.0043331 | 0.001086
29 | 0.0043332 | 0.001086
30 | 0.00066932 | 0.00016775

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1