## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1707-19_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1707-19_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1707-19_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1707-19_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1707-19_0_4_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_1707-19_0_4_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_1707-19_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1707-19_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1707-19_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1707-19_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1707-19_0_4_node_86 | 0.4 | n |  | TRUE
11 | bus_LV_1707-19_0_4_node_88 | 0.4 | n |  | TRUE
12 | bus_LV_1707-19_0_4_node_84 | 0.4 | n |  | TRUE
13 | bus_LV_1707-19_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1707-19_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1707-19_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1707-19_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1707-19_0_4_node_123 | 0.4 | n |  | TRUE
18 | bus_LV_1707-19_0_4_node_108 | 0.4 | n |  | TRUE
19 | bus_LV_1707-19_0_4_node_124 | 0.4 | n |  | TRUE
20 | bus_LV_1707-19_0_4_node_115 | 0.4 | n |  | TRUE
21 | bus_LV_1707-19_0_4_node_107 | 0.4 | n |  | TRUE
22 | bus_LV_1707-19_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1707-19_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1707-19_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1707-19_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1707-19_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1707-19_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1707-19_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1707-19_0_4_node_46 | 0.4 | n |  | TRUE
30 | bus_LV_1707-19_0_4_node_120 | 0.4 | n |  | TRUE
31 | bus_LV_1707-19_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_1707-19_0_4_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_1707-19_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_1707-19_0_4_node_45 | 0.4 | n |  | TRUE
35 | bus_LV_1707-19_0_4_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_1707-19_0_4_node_118 | 0.4 | n |  | TRUE
37 | bus_LV_1707-19_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1707-19_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1707-19_0_4_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1707-19_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_1707-19_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1707-19_0_4_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_1707-19_0_4_node_58 | 0.4 | n |  | TRUE
44 | bus_LV_1707-19_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1707-19_0_4_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_1707-19_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1707-19_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_1707-19_0_4_node_62 | 0.4 | n |  | TRUE
49 | bus_LV_1707-19_0_4_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_1707-19_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_1707-19_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_1707-19_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_1707-19_0_4_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_1707-19_0_4_node_54 | 0.4 | n |  | TRUE
55 | bus_LV_1707-19_0_4_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_1707-19_0_4_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_1707-19_0_4_node_59 | 0.4 | n |  | TRUE
58 | bus_LV_1707-19_0_4_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_1707-19_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_1707-19_0_4_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_1707-19_0_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_1707-19_0_4_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_1707-19_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_1707-19_0_4_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_1707-19_0_4_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_1707-19_0_4_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_1707-19_0_4_node_135 | 0.4 | n |  | TRUE
68 | bus_LV_1707-19_0_4_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_1707-19_0_4_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_1707-19_0_4_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_1707-19_0_4_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_1707-19_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_1707-19_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_1707-19_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_1707-19_0_4_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_1707-19_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_1707-19_0_4_node_102 | 0.4 | n |  | TRUE
78 | bus_LV_1707-19_0_4_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_1707-19_0_4_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_1707-19_0_4_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_1707-19_0_4_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_1707-19_0_4_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_1707-19_0_4_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_1707-19_0_4_node_97 | 0.4 | n |  | TRUE
85 | bus_LV_1707-19_0_4_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_1707-19_0_4_node_95 | 0.4 | n |  | TRUE
87 | bus_LV_1707-19_0_4_node_93 | 0.4 | n |  | TRUE
88 | bus_LV_1707-19_0_4_node_105 | 0.4 | n |  | TRUE
89 | bus_LV_1707-19_0_4_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_1707-19_0_4_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_1707-19_0_4_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_1707-19_0_4_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_1707-19_0_4_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_1707-19_0_4_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_1707-19_0_4_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_1707-19_0_4_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_1707-19_0_4_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_1707-19_0_4_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_1707-19_0_4_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_1707-19_0_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_1707-19_0_4_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_1707-19_0_4_node_89 | 0.4 | n |  | TRUE
103 | bus_LV_1707-19_0_4_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_1707-19_0_4_node_96 | 0.4 | n |  | TRUE
105 | bus_LV_1707-19_0_4_node_92 | 0.4 | n |  | TRUE
106 | bus_LV_1707-19_0_4_node_127 | 0.4 | n |  | TRUE
107 | bus_LV_1707-19_0_4_node_128 | 0.4 | n |  | TRUE
108 | bus_LV_1707-19_0_4_node_129 | 0.4 | n |  | TRUE
109 | bus_LV_1707-19_0_4_node_98 | 0.4 | n |  | TRUE
110 | bus_LV_1707-19_0_4_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_1707-19_0_4_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_1707-19_0_4_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_1707-19_0_4_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_1707-19_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_1707-19_0_4_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_1707-19_0_4_node_113 | 0.4 | n |  | TRUE
117 | bus_LV_1707-19_0_4_node_130 | 0.4 | n |  | TRUE
118 | bus_LV_1707-19_0_4_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_1707-19_0_4_node_131 | 0.4 | n |  | TRUE
120 | bus_LV_1707-19_0_4_node_109 | 0.4 | n |  | TRUE
121 | bus_LV_1707-19_0_4_node_110 | 0.4 | n |  | TRUE
122 | bus_LV_1707-19_0_4_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_1707-19_0_4_node_119 | 0.4 | n |  | TRUE
124 | bus_LV_1707-19_0_4_node_112 | 0.4 | n |  | TRUE
125 | bus_LV_1707-19_0_4_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_1707-19_0_4_node_116 | 0.4 | n |  | TRUE
127 | bus_LV_1707-19_0_4_node_117 | 0.4 | n |  | TRUE
128 | bus_LV_1707-19_0_4_node_122 | 0.4 | n |  | TRUE
129 | bus_LV_1707-19_0_4_node_125 | 0.4 | n |  | TRUE
130 | bus_LV_1707-19_0_4_node_126 | 0.4 | n |  | TRUE
131 | bus_LV_1707-19_0_4_node_134 | 0.4 | n |  | TRUE
132 | bus_LV_1707-19_0_4_node_133 | 0.4 | n |  | TRUE
133 | bus_LV_1707-19_0_4_node_132 | 0.4 | n |  | TRUE
134 | bus_MV_0_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1707-19_0_4_load_0 | 0 | 0.0024869 | 0.00062327 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1707-19_0_4_load_2 | 2 | 0.00085818 | 0.00021508 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1707-19_0_4_load_3 | 3 | 0.00035465 | 8.8885e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1707-19_0_4_load_20 | 4 | 0.0017129 | 0.00042929 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1707-19_0_4_load_21 | 5 | 0.0018364 | 0.00046023 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1707-19_0_4_load_22 | 6 | 0.0017587 | 0.00044076 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1707-19_0_4_load_6 | 7 | 0.011808 | 0.0029594 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1707-19_0_4_load_88 | 11 | 0.0016346 | 0.00040968 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1707-19_0_4_load_84 | 12 | 0.0014586 | 0.00036556 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1707-19_0_4_load_7 | 13 | 0.02491 | 0.006243 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1707-19_0_4_load_8 | 14 | 0.0076938 | 0.0019282 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1707-19_0_4_load_108 | 18 | 0.0036565 | 0.00091639 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1707-19_0_4_load_124 | 19 | 0.0034342 | 0.00086068 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1707-19_0_4_load_115 | 20 | 0.0019248 | 0.00048239 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1707-19_0_4_load_107 | 21 | 0.0073936 | 0.001853 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1707-19_0_4_load_11 | 22 | 0.00093557 | 0.00023448 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1707-19_0_4_load_12 | 23 | 0.0011394 | 0.00028556 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1707-19_0_4_load_13 | 24 | 0.00077806 | 0.000195 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1707-19_0_4_load_15 | 26 | 0.00072092 | 0.00018068 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1707-19_0_4_load_19 | 27 | 0.001332 | 0.00033383 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1707-19_0_4_load_16 | 28 | 0.0014743 | 0.0003695 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1707-19_0_4_load_46 | 29 | 0.0020983 | 0.00052588 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1707-19_0_4_load_120 | 30 | 0.00091566 | 0.00022949 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1707-19_0_4_load_17 | 31 | 0.002213 | 0.00055462 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1707-19_0_4_load_47 | 32 | 0.0038513 | 0.00096522 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1707-19_0_4_load_18 | 33 | 0.002672 | 0.00066966 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1707-19_0_4_load_45 | 34 | 0.003567 | 0.00089398 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1707-19_0_4_load_44 | 35 | 0.0031143 | 0.00078053 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1707-19_0_4_load_118 | 36 | 0.00090691 | 0.00022729 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1707-19_0_4_load_23 | 37 | 0.0023423 | 0.00058703 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1707-19_0_4_load_24 | 38 | 0.0053873 | 0.0013502 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1707-19_0_4_load_40 | 42 | 0.0043433 | 0.0010885 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1707-19_0_4_load_58 | 43 | 0.0020715 | 0.00051917 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1707-19_0_4_load_30 | 44 | 0.0059399 | 0.0014887 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1707-19_0_4_load_26 | 45 | 0.0021971 | 0.00055066 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1707-19_0_4_load_28 | 46 | 0.0021732 | 0.00054465 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1707-19_0_4_load_29 | 47 | 0.0078462 | 0.0019664 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1707-19_0_4_load_62 | 48 | 0.0064752 | 0.0016228 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1707-19_0_4_load_43 | 49 | 0.0096221 | 0.0024115 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1707-19_0_4_load_31 | 50 | 0.0017435 | 0.00043696 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1707-19_0_4_load_32 | 51 | 0.002856 | 0.00071578 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1707-19_0_4_load_33 | 52 | 0.0034308 | 0.00085983 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1707-19_0_4_load_34 | 53 | 0.0026677 | 0.00066858 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1707-19_0_4_load_54 | 54 | 0.0017562 | 0.00044016 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1707-19_0_4_load_53 | 55 | 0.0070329 | 0.0017626 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1707-19_0_4_load_39 | 56 | 0.0087234 | 0.0021863 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1707-19_0_4_load_59 | 57 | 0.0018764 | 0.00047026 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1707-19_0_4_load_36 | 58 | 0.0088803 | 0.0022256 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1707-19_0_4_load_37 | 59 | 0.0034752 | 0.00087097 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1707-19_0_4_load_38 | 60 | 0.003465 | 0.00086842 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1707-19_0_4_load_42 | 61 | 0.0032872 | 0.00082385 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1707-19_0_4_load_41 | 62 | 0.005682 | 0.001424 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1707-19_0_4_load_48 | 64 | 0.0019351 | 0.00048498 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1707-19_0_4_load_51 | 66 | 0.00094718 | 0.00023739 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1707-19_0_4_load_135 | 67 | 0.00087278 | 0.00021874 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1707-19_0_4_load_52 | 68 | 0.0014487 | 0.00036307 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1707-19_0_4_load_55 | 69 | 0.0054277 | 0.0013603 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1707-19_0_4_load_56 | 70 | 0.0057751 | 0.0014474 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1707-19_0_4_load_57 | 71 | 0.0030875 | 0.00077379 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1707-19_0_4_load_63 | 72 | 0.0041617 | 0.001043 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1707-19_0_4_load_64 | 73 | 0.0023463 | 0.00058805 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1707-19_0_4_load_60 | 74 | 0.0030203 | 0.00075695 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1707-19_0_4_load_61 | 75 | 0.0031005 | 0.00077706 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1707-19_0_4_load_102 | 77 | 0.0014745 | 0.00036954 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1707-19_0_4_load_65 | 79 | 0.0038614 | 0.00096775 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1707-19_0_4_load_66 | 80 | 0.001359 | 0.0003406 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1707-19_0_4_load_74 | 82 | 0.0022357 | 0.00056032 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1707-19_0_4_load_79 | 83 | 0.002529 | 0.00063383 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1707-19_0_4_load_97 | 84 | 0.0028553 | 0.0007156 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1707-19_0_4_load_95 | 86 | 0.0023106 | 0.00057909 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1707-19_0_4_load_93 | 87 | 0.0021604 | 0.00054145 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1707-19_0_4_load_70 | 89 | 0.0017115 | 0.00042894 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1707-19_0_4_load_75 | 92 | 0.0018262 | 0.00045768 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1707-19_0_4_load_76 | 93 | 0.0016074 | 0.00040285 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1707-19_0_4_load_78 | 94 | 0.0022458 | 0.00056285 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1707-19_0_4_load_77 | 95 | 0.0016443 | 0.00041211 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1707-19_0_4_load_80 | 96 | 0.0018288 | 0.00045833 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1707-19_0_4_load_81 | 97 | 0.0024918 | 0.00062451 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1707-19_0_4_load_83 | 98 | 0.0026411 | 0.00066191 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1707-19_0_4_load_82 | 99 | 0.0030248 | 0.00075808 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1707-19_0_4_load_85 | 100 | 0.0027497 | 0.00068913 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1707-19_0_4_load_87 | 101 | 0.0032301 | 0.00080955 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1707-19_0_4_load_89 | 102 | 0.0038385 | 0.00096201 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1707-19_0_4_load_96 | 104 | 0.0027052 | 0.00067798 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1707-19_0_4_load_92 | 105 | 0.0025148 | 0.00063026 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1707-19_0_4_load_127 | 106 | 0.0047245 | 0.0011841 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1707-19_0_4_load_128 | 107 | 0.0016845 | 0.00042217 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1707-19_0_4_load_129 | 108 | 0.0033418 | 0.00083752 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1707-19_0_4_load_98 | 109 | 0.0037213 | 0.00093265 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1707-19_0_4_load_99 | 110 | 0.0044173 | 0.0011071 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1707-19_0_4_load_100 | 111 | 0.0032665 | 0.00081866 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1707-19_0_4_load_101 | 112 | 0.0032013 | 0.00080231 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1707-19_0_4_load_103 | 113 | 0.0035279 | 0.00088416 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1707-19_0_4_load_104 | 114 | 0.0028413 | 0.00071209 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1707-19_0_4_load_130 | 117 | 0.0020591 | 0.00051607 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1707-19_0_4_load_111 | 118 | 0.0033412 | 0.00083737 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1707-19_0_4_load_131 | 119 | 0.0025938 | 0.00065006 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1707-19_0_4_load_109 | 120 | 0.0012026 | 0.00030141 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1707-19_0_4_load_110 | 121 | 0.0013071 | 0.0003276 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1707-19_0_4_load_121 | 122 | 0.0023487 | 0.00058865 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1707-19_0_4_load_119 | 123 | 0.0011326 | 0.00028386 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1707-19_0_4_load_112 | 124 | 0.0030913 | 0.00077476 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1707-19_0_4_load_114 | 125 | 0.003632 | 0.00091026 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1707-19_0_4_load_116 | 126 | 0.0022577 | 0.00056583 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1707-19_0_4_load_117 | 127 | 0.0022064 | 0.00055296 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1707-19_0_4_load_122 | 128 | 0.0073846 | 0.0018508 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1707-19_0_4_load_125 | 129 | 0.0032012 | 0.0008023 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1707-19_0_4_load_126 | 130 | 0.0024917 | 0.00062447 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1707-19_0_4_load_134 | 131 | 0.0029414 | 0.00073718 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1707-19_0_4_load_133 | 132 | 0.0060707 | 0.0015215 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1707-19_0_4_load_132 | 133 | 0.0026038 | 0.00065258 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 109 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1707-19_0_4_line_0 |  | 0 | 1 | 0.019171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1707-19_0_4_line_1 |  | 1 | 2 | 0.022293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1707-19_0_4_line_2 |  | 1 | 3 | 0.029728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1707-19_0_4_line_3 |  | 2 | 7 | 0.19137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1707-19_0_4_line_4 |  | 4 | 5 | 0.006346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1707-19_0_4_line_5 |  | 4 | 6 | 0.0026236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1707-19_0_4_line_6 |  | 5 | 37 | 0.026532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1707-19_0_4_line_7 |  | 6 | 38 | 0.014251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1707-19_0_4_line_8 |  | 7 | 9 | 0.018764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1707-19_0_4_line_9 |  | 8 | 9 | 0.005186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1707-19_0_4_line_10 |  | 8 | 10 | 0.22247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1707-19_0_4_line_11 |  | 10 | 11 | 0.014668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1707-19_0_4_line_12 |  | 10 | 12 | 0.050409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1707-19_0_4_line_13 |  | 11 | 93 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1707-19_0_4_line_14 |  | 12 | 100 | 0.012673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1707-19_0_4_line_15 |  | 13 | 14 | 0.019966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1707-19_0_4_line_16 |  | 13 | 15 | 0.022045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1707-19_0_4_line_17 |  | 15 | 16 | 0.035275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1707-19_0_4_line_18 |  | 16 | 17 | 0.048011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1707-19_0_4_line_19 |  | 16 | 18 | 0.021682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1707-19_0_4_line_20 |  | 17 | 19 | 0.028015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1707-19_0_4_line_21 |  | 17 | 20 | 0.034954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1707-19_0_4_line_22 |  | 18 | 21 | 0.012265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1707-19_0_4_line_23 |  | 19 | 129 | 0.024987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1707-19_0_4_line_24 |  | 20 | 116 | 0.0043869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1707-19_0_4_line_25 |  | 21 | 120 | 0.012508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1707-19_0_4_line_26 |  | 22 | 23 | 0.0092158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1707-19_0_4_line_27 |  | 22 | 24 | 0.062796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1707-19_0_4_line_28 |  | 23 | 25 | 0.02664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1707-19_0_4_line_29 |  | 24 | 26 | 0.0005753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1707-19_0_4_line_30 |  | 25 | 27 | 0.035346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1707-19_0_4_line_31 |  | 25 | 28 | 0.036396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1707-19_0_4_line_32 |  | 26 | 29 | 0.017127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1707-19_0_4_line_33 |  | 27 | 30 | 0.001848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1707-19_0_4_line_34 |  | 28 | 31 | 0.042397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1707-19_0_4_line_35 |  | 29 | 32 | 0.0099159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1707-19_0_4_line_36 |  | 30 | 36 | 0.023589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1707-19_0_4_line_37 |  | 31 | 33 | 0.021961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1707-19_0_4_line_38 |  | 32 | 63 | 0.044458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1707-19_0_4_line_39 |  | 33 | 34 | 0.026295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_1707-19_0_4_line_40 |  | 34 | 35 | 0.03043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1707-19_0_4_line_41 |  | 35 | 49 | 0.050681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1707-19_0_4_line_42 |  | 36 | 123 | 0.015448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1707-19_0_4_line_43 |  | 37 | 39 | 0.039019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1707-19_0_4_line_44 |  | 39 | 40 | 0.02479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1707-19_0_4_line_45 |  | 40 | 44 | 0.030855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1707-19_0_4_line_46 |  | 40 | 45 | 0.012929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1707-19_0_4_line_47 |  | 41 | 42 | 0.025085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1707-19_0_4_line_48 |  | 41 | 43 | 0.016687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1707-19_0_4_line_49 |  | 42 | 56 | 0.010283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1707-19_0_4_line_50 |  | 43 | 57 | 0.020356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1707-19_0_4_line_51 |  | 44 | 49 | 0.0028126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1707-19_0_4_line_52 |  | 45 | 46 | 0.074641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1707-19_0_4_line_53 |  | 46 | 47 | 0.0079456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1707-19_0_4_line_54 |  | 47 | 48 | 0.017426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1707-19_0_4_line_55 |  | 50 | 51 | 0.0046984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1707-19_0_4_line_56 |  | 50 | 52 | 0.018974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1707-19_0_4_line_57 |  | 51 | 53 | 0.027705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1707-19_0_4_line_58 |  | 53 | 54 | 0.0052652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1707-19_0_4_line_59 |  | 54 | 55 | 0.017259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1707-19_0_4_line_60 |  | 55 | 69 | 0.0064607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1707-19_0_4_line_61 |  | 56 | 62 | 0.022991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1707-19_0_4_line_62 |  | 57 | 74 | 0.0051929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1707-19_0_4_line_63 |  | 58 | 59 | 0.0060527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1707-19_0_4_line_64 |  | 59 | 60 | 0.024178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1707-19_0_4_line_65 |  | 60 | 61 | 0.0066419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1707-19_0_4_line_66 |  | 61 | 62 | 0.015762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1707-19_0_4_line_67 |  | 63 | 64 | 0.016438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1707-19_0_4_line_68 |  | 64 | 65 | 0.11816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1707-19_0_4_line_69 |  | 65 | 66 | 0.0091536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1707-19_0_4_line_70 |  | 65 | 67 | 0.29597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1707-19_0_4_line_71 |  | 66 | 68 | 0.066588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1707-19_0_4_line_72 |  | 69 | 70 | 0.02023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1707-19_0_4_line_73 |  | 70 | 71 | 0.014862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1707-19_0_4_line_74 |  | 71 | 72 | 0.019032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1707-19_0_4_line_75 |  | 72 | 73 | 0.0094659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1707-19_0_4_line_76 |  | 73 | 79 | 0.0028814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1707-19_0_4_line_77 |  | 74 | 75 | 0.031811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1707-19_0_4_line_78 |  | 75 | 76 | 0.04372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1707-19_0_4_line_79 |  | 76 | 77 | 0.045102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_1707-19_0_4_line_80 |  | 76 | 78 | 0.031341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1707-19_0_4_line_81 |  | 77 | 88 | 0.018281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_1707-19_0_4_line_82 |  | 78 | 81 | 0.010668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1707-19_0_4_line_83 |  | 78 | 80 | 0.019412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1707-19_0_4_line_84 |  | 79 | 80 | 0.0069089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1707-19_0_4_line_85 |  | 81 | 82 | 0.019859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1707-19_0_4_line_86 |  | 82 | 85 | 0.018343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1707-19_0_4_line_87 |  | 83 | 84 | 0.012166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1707-19_0_4_line_88 |  | 84 | 98 | 0.0010491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1707-19_0_4_line_89 |  | 85 | 90 | 0.021874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1707-19_0_4_line_90 |  | 85 | 89 | 0.013002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1707-19_0_4_line_91 |  | 86 | 87 | 0.021926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1707-19_0_4_line_92 |  | 87 | 105 | 0.00078304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1707-19_0_4_line_93 |  | 88 | 115 | 0.023064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_1707-19_0_4_line_94 |  | 88 | 114 | 0.019722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_1707-19_0_4_line_95 |  | 90 | 94 | 0.0079358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1707-19_0_4_line_96 |  | 90 | 95 | 0.016911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1707-19_0_4_line_97 |  | 91 | 92 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1707-19_0_4_line_98 |  | 91 | 93 | 0.014358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1707-19_0_4_line_99 |  | 92 | 95 | 0.0050146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1707-19_0_4_line_100 |  | 94 | 96 | 0.014904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1707-19_0_4_line_101 |  | 96 | 97 | 0.011763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1707-19_0_4_line_102 |  | 97 | 99 | 0.0069905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1707-19_0_4_line_103 |  | 98 | 99 | 0.013424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1707-19_0_4_line_104 |  | 100 | 101 | 0.028355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1707-19_0_4_line_105 |  | 101 | 102 | 0.020868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1707-19_0_4_line_106 |  | 103 | 104 | 0.025023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1707-19_0_4_line_107 |  | 103 | 105 | 0.021898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1707-19_0_4_line_108 |  | 104 | 107 | 0.026398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1707-19_0_4_line_109 |  | 106 | 107 | 0.016952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1707-19_0_4_line_110 |  | 107 | 108 | 0.012211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1707-19_0_4_line_111 |  | 108 | 131 | 0.0092827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1707-19_0_4_line_112 |  | 109 | 110 | 0.0031644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_1707-19_0_4_line_113 |  | 109 | 111 | 0.030303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1707-19_0_4_line_114 |  | 110 | 112 | 0.02831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_1707-19_0_4_line_115 |  | 112 | 113 | 0.0052134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_1707-19_0_4_line_116 |  | 113 | 114 | 0.016114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_1707-19_0_4_line_117 |  | 115 | 116 | 0.05644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_1707-19_0_4_line_118 |  | 115 | 117 | 0.022887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1707-19_0_4_line_119 |  | 116 | 118 | 0.021625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1707-19_0_4_line_120 |  | 117 | 119 | 0.00049553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1707-19_0_4_line_121 |  | 118 | 124 | 0.0097376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1707-19_0_4_line_122 |  | 119 | 133 | 0.011973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1707-19_0_4_line_123 |  | 120 | 121 | 0.015828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_1707-19_0_4_line_124 |  | 121 | 122 | 0.017502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_1707-19_0_4_line_125 |  | 122 | 123 | 0.00095785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_1707-19_0_4_line_126 |  | 124 | 125 | 0.016698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1707-19_0_4_line_127 |  | 125 | 126 | 0.016808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1707-19_0_4_line_128 |  | 126 | 127 | 0.0090886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1707-19_0_4_line_129 |  | 127 | 128 | 0.016251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1707-19_0_4_line_130 |  | 129 | 130 | 0.0065319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1707-19_0_4_line_131 |  | 131 | 132 | 0.01334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1707-19_0_4_line_132 |  | 132 | 133 | 0.011432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1707-19_0_4_trafo_98 | 0.63 MVA 20/0.4 kV | 134 | 109 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2676466.4317 | 1221777.2108 | 2676464.2507 | 1221796.2576
1 | 2676466.4317 | 1221777.2108 | 2676484.7011 | 1221764.4356
2 | 2676466.4317 | 1221777.2108 | 2676437.1898 | 1221782.5649
3 | 2676484.7011 | 1221764.4356 | 2676604.5964 | 1221615.2771
4 | 2676839.6959 | 1221864.2828 | 2676839.6959 | 1221864.2828 | 2676845.6918 | 1221866.3613
5 | 2676839.7505 | 1221866.9058 | 2676839.6959 | 1221864.2828
6 | 2676870.7605 | 1221875.0511 | 2676845.6918 | 1221866.3613
7 | 2676840.047 | 1221881.154 | 2676839.7505 | 1221866.9058
8 | 2676623.3186 | 1221614.0195 | 2676604.5964 | 1221615.2771
9 | 2676624.1099 | 1221619.1441 | 2676623.3186 | 1221614.0195
10 | 2676845.4758 | 1221596.959 | 2676624.1099 | 1221619.1441
11 | 2676845.4758 | 1221596.959 | 2676845.9212 | 1221603.0021 | 2676846.5186 | 1221611.5894
12 | 2676845.4758 | 1221596.959 | 2676865.3981 | 1221594.5589 | 2676885.0804 | 1221591.9446 | 2676895.5167 | 1221590.9056
13 | 2676846.5186 | 1221611.5894 | 2676847.3308 | 1221623.266
14 | 2676895.5167 | 1221590.9056 | 2676908.1269 | 1221589.6503
15 | 2677216.8429 | 1221762.7113 | 2677220.3715 | 1221763.4394 | 2677224.9616 | 1221764.5663 | 2677236.5442 | 1221765.69
16 | 2677195.6528 | 1221756.6589 | 2677203.2256 | 1221758.8585 | 2677214.6214 | 1221762.253 | 2677216.8429 | 1221762.7113
17 | 2677162.9238 | 1221750.4085 | 2677165.212 | 1221747.703 | 2677182.656 | 1221752.699 | 2677195.6528 | 1221756.6589
18 | 2677162.9238 | 1221750.4085 | 2677115.6517 | 1221741.2681
19 | 2677162.9238 | 1221750.4085 | 2677157.3039 | 1221758.4966 | 2677152.5776 | 1221766.1182 | 2677151.7182 | 1221768.8518
20 | 2677115.6517 | 1221741.2681 | 2677120.2475 | 1221726.7402 | 2677125.2023 | 1221714.9624
21 | 2677115.6517 | 1221741.2681 | 2677081.4725 | 1221733.9499
22 | 2677149.099 | 1221780.7053 | 2677149.0408 | 1221777.3687 | 2677151.7182 | 1221768.8518
23 | 2677125.2023 | 1221714.9624 | 2677134.8916 | 1221691.9302
24 | 2677077.1828 | 1221733.0314 | 2677081.4725 | 1221733.9499
25 | 2677149.3172 | 1221793.2115 | 2677149.099 | 1221780.7053
26 | 2677130.2102 | 1221936.591 | 2677129.2995 | 1221929.758 | 2677129.1506 | 1221927.4404
27 | 2677138.4081 | 1221998.8488 | 2677137.2359 | 1221989.3445 | 2677132.5282 | 1221953.9825 | 2677130.2102 | 1221936.591
28 | 2677127.3906 | 1221900.8587 | 2677128.1127 | 1221911.286 | 2677129.1506 | 1221927.4404
29 | 2677138.4785 | 1221999.4198 | 2677138.4081 | 1221998.8488
30 | 2677127.3906 | 1221900.8587 | 2677128.7251 | 1221893.2932 | 2677136.7005 | 1221866.8042
31 | 2677127.3906 | 1221900.8587 | 2677115.2208 | 1221905.1039 | 2677103.8606 | 1221908.9371 | 2677098.8418 | 1221910.4509 | 2677094.0083 | 1221911.1333 | 2677092.6149 | 1221911.1812
32 | 2677138.4785 | 1221999.4198 | 2677140.5749 | 1222016.418
33 | 2677136.7005 | 1221866.8042 | 2677137.2333 | 1221865.0347
34 | 2677092.6149 | 1221911.1812 | 2677077.5699 | 1221911.6987 | 2677057.8152 | 1221913.5332 | 2677050.6943 | 1221913.9413 | 2677050.3307 | 1221914.0135
35 | 2677140.5749 | 1222016.418 | 2677141.7886 | 1222026.2593
36 | 2677144.034 | 1221842.4474 | 2677137.2333 | 1221865.0347
37 | 2677029.15 | 1221919.6646 | 2677032.3922 | 1221918.4186 | 2677041.8035 | 1221915.7052 | 2677050.3307 | 1221914.0135
38 | 2677147.2305 | 1222070.383 | 2677141.7886 | 1222026.2593
39 | 2677029.15 | 1221919.6646 | 2677004.6054 | 1221929.0966
40 | 2676975.7367 | 1221938.586 | 2676978.4221 | 1221938.0783 | 2676989.6779 | 1221934.6882 | 2676995.5006 | 1221932.5954 | 2677004.6054 | 1221929.0966
41 | 2676930.0181 | 1221923.2167 | 2676937.5515 | 1221926.1757 | 2676947.8167 | 1221934.2803 | 2676952.8426 | 1221938.07 | 2676959.8222 | 1221939.7835 | 2676969.3956 | 1221939.785 | 2676975.7367 | 1221938.586
42 | 2677144.034 | 1221842.4474 | 2677145.8082 | 1221836.5548 | 2677147.1205 | 1221827.3536
43 | 2676907.6275 | 1221887.8306 | 2676870.7605 | 1221875.0511
44 | 2676898.6814 | 1221910.9081 | 2676903.2449 | 1221901.1717 | 2676907.6275 | 1221887.8306
45 | 2676898.6814 | 1221910.9081 | 2676927.4003 | 1221922.1885
46 | 2676898.6814 | 1221910.9081 | 2676895.316 | 1221917.7358 | 2676892.4606 | 1221922.2211
47 | 2676918.9549 | 1221821.9557 | 2676943.5478 | 1221826.8998
48 | 2676918.9549 | 1221821.9557 | 2676921.379 | 1221805.446
49 | 2676953.6291 | 1221828.9266 | 2676943.5478 | 1221826.8998
50 | 2676921.379 | 1221805.446 | 2676924.3362 | 1221785.3057
51 | 2676930.0181 | 1221923.2167 | 2676927.4003 | 1221922.1885
52 | 2676892.4606 | 1221922.2211 | 2676835.5566 | 1221970.5248
53 | 2676828.1321 | 1221973.3547 | 2676835.5566 | 1221970.5248
54 | 2676828.1321 | 1221973.3547 | 2676816.8021 | 1221977.6734 | 2676811.7154 | 1221979.1651
55 | 2676874.2443 | 1221838.1686 | 2676875.6012 | 1221833.6704 | 2676875.6012 | 1221833.6704
56 | 2676874.2443 | 1221838.1686 | 2676868.7644 | 1221856.3344
57 | 2676870.9199 | 1221806.3982 | 2676870.8469 | 1221807.6586 | 2676875.6012 | 1221833.6704
58 | 2676871.2245 | 1221801.1418 | 2676870.9199 | 1221806.3982
59 | 2676873.2249 | 1221784.0495 | 2676871.8524 | 1221790.3045 | 2676871.2245 | 1221801.1418
60 | 2676873.2249 | 1221784.0495 | 2676874.6095 | 1221777.7389
61 | 2676953.6291 | 1221828.9266 | 2676976.1695 | 1221833.4581
62 | 2676924.3362 | 1221785.3057 | 2676925.0906 | 1221780.1679
63 | 2676972.651 | 1221881.3244 | 2676973.7214 | 1221875.3671
64 | 2676973.7214 | 1221875.3671 | 2676977.9974 | 1221851.5704
65 | 2676979.172 | 1221845.0333 | 2676977.9974 | 1221851.5704
66 | 2676976.1695 | 1221833.4581 | 2676981.0748 | 1221834.4442 | 2676979.172 | 1221845.0333
67 | 2677147.2305 | 1222070.383 | 2677163.2928 | 1222073.8767
68 | 2677163.2928 | 1222073.8767 | 2677281.4009 | 1222070.2557
69 | 2677281.4009 | 1222070.2557 | 2677283.5176 | 1222063.8011 | 2677282.9335 | 1222061.5137
70 | 2677281.4009 | 1222070.2557 | 2677239.7227 | 1222363.2753
71 | 2677280.7336 | 1221996.6206 | 2677274.422 | 1222028.1818 | 2677282.9335 | 1222061.5137
72 | 2676874.6095 | 1221777.7389 | 2676875.8907 | 1221771.9001 | 2676883.0234 | 1221759.5614
73 | 2676883.0234 | 1221759.5614 | 2676885.9004 | 1221754.5845 | 2676889.658 | 1221747.3505 | 2676889.7971 | 1221746.3988
74 | 2676892.5506 | 1221727.5675 | 2676889.7971 | 1221746.3988
75 | 2676892.5506 | 1221727.5675 | 2676893.9201 | 1221718.2011
76 | 2676894.337 | 1221715.3501 | 2676893.9201 | 1221718.2011
77 | 2676925.0906 | 1221780.1679 | 2676929.7117 | 1221748.6947
78 | 2676937.178 | 1221705.6366 | 2676933.3621 | 1221723.8327 | 2676929.7117 | 1221748.6947
79 | 2676937.178 | 1221705.6366 | 2676950.6034 | 1221711.6696 | 2676972.4761 | 1221714.4651 | 2676980.6569 | 1221716.0469
80 | 2676937.178 | 1221705.6366 | 2676926.6677 | 1221700.6198 | 2676908.109 | 1221693.7979
81 | 2676998.6058 | 1221719.5173 | 2676980.6569 | 1221716.0469
82 | 2676908.109 | 1221693.7979 | 2676910.4359 | 1221683.3877
83 | 2676908.109 | 1221693.7979 | 2676896.5693 | 1221706.8019 | 2676895.6704 | 1221708.618
84 | 2676894.337 | 1221715.3501 | 2676895.175 | 1221709.6191 | 2676895.6704 | 1221708.618
85 | 2676910.4359 | 1221683.3877 | 2676891.0275 | 1221679.1822
86 | 2676878.5345 | 1221672.3353 | 2676877.0968 | 1221676.1637 | 2676891.0275 | 1221679.1822
87 | 2676928.798 | 1221656.1763 | 2676932.1226 | 1221648.3447 | 2676930.4669 | 1221645.0832
88 | 2676929.992 | 1221644.1477 | 2676929.992 | 1221644.1477 | 2676930.4669 | 1221645.0832
89 | 2676886.1958 | 1221651.8429 | 2676878.5345 | 1221672.3353
90 | 2676878.5345 | 1221672.3353 | 2676866.322 | 1221667.8746
91 | 2676979.6484 | 1221636.8698 | 2676965.221 | 1221653.3803
92 | 2676979.6484 | 1221636.8698 | 2676980.1637 | 1221636.2802
93 | 2677021.4296 | 1221723.2704 | 2676998.6058 | 1221719.5173
94 | 2676998.6058 | 1221719.5173 | 2677000.0724 | 1221739.1851
95 | 2676886.1958 | 1221651.8429 | 2676889.7256 | 1221644.7354
96 | 2676886.1958 | 1221651.8429 | 2676870.3687 | 1221645.8871
97 | 2676848.3272 | 1221637.5892 | 2676851.0978 | 1221638.6368 | 2676851.8832 | 1221638.9138 | 2676852.4266 | 1221639.132 | 2676861.939 | 1221642.7127 | 2676862.4222 | 1221642.8968 | 2676865.6754 | 1221644.121
98 | 2676848.3272 | 1221637.5892 | 2676847.3308 | 1221623.266
99 | 2676865.6754 | 1221644.121 | 2676870.3687 | 1221645.8871
100 | 2676889.7256 | 1221644.7354 | 2676893.7509 | 1221636.6304 | 2676899.5616 | 1221635.9126
101 | 2676899.5616 | 1221635.9126 | 2676906.463 | 1221635.0601 | 2676910.9489 | 1221636.7927
102 | 2676910.9489 | 1221636.7927 | 2676917.47 | 1221639.3113
103 | 2676929.992 | 1221644.1477 | 2676917.47 | 1221639.3113
104 | 2676936.3403 | 1221586.8241 | 2676934.607 | 1221587.0141 | 2676908.1269 | 1221589.6503
105 | 2676936.3403 | 1221586.8241 | 2676952.84 | 1221585.015 | 2676956.9481 | 1221583.8514
106 | 2676995.4324 | 1221620.5889 | 2677017.6934 | 1221632.0174
107 | 2676995.4324 | 1221620.5889 | 2676981.7493 | 1221634.4656 | 2676980.1637 | 1221636.2802
108 | 2677041.1772 | 1221644.0736 | 2677017.6934 | 1221632.0174
109 | 2677041.1772 | 1221644.0736 | 2677043.861 | 1221627.3352
110 | 2677041.1772 | 1221644.0736 | 2677038.2229 | 1221655.9217
111 | 2677038.2229 | 1221655.9217 | 2677035.977 | 1221664.9287
112 | 2677008.7457 | 1221789.0148 | 2677009.0205 | 1221785.8623 | 2677009.0205 | 1221785.8623
113 | 2676998.2192 | 1221815.6757 | 2677000.5983 | 1221804.7548 | 2677007.5674 | 1221799.0856 | 2677008.4415 | 1221792.5037 | 2677008.7457 | 1221789.0148
114 | 2677001.6584 | 1221760.4533 | 2677002.1743 | 1221767.3728 | 2677003.0252 | 1221769.0404 | 2677004.3632 | 1221769.9917 | 2677006.8753 | 1221771.0804 | 2677007.5438 | 1221772.1787 | 2677008.0741 | 1221773.4086 | 2677008.727 | 1221779.8212 | 2677009.0205 | 1221785.8623
115 | 2677001.6584 | 1221760.4533 | 2677001.2707 | 1221755.2544
116 | 2677000.0724 | 1221739.1851 | 2677001.2707 | 1221755.2544
117 | 2677077.1828 | 1221733.0314 | 2677021.4296 | 1221723.2704
118 | 2677021.4296 | 1221723.2704 | 2677026.9669 | 1221701.063
119 | 2677077.1828 | 1221733.0314 | 2677075.9917 | 1221754.6235
120 | 2677027.0868 | 1221700.5822 | 2677026.9669 | 1221701.063
121 | 2677075.9917 | 1221754.6235 | 2677075.4553 | 1221764.3463
122 | 2677029.9836 | 1221688.9648 | 2677027.0868 | 1221700.5822
123 | 2677149.3172 | 1221793.2115 | 2677149.5544 | 1221806.8059 | 2677149.2926 | 1221809.0219
124 | 2677149.2926 | 1221809.0219 | 2677147.2396 | 1221826.4032
125 | 2677147.2396 | 1221826.4032 | 2677147.16 | 1221827.0771 | 2677147.1205 | 1221827.3536
126 | 2677072.7275 | 1221780.789 | 2677075.2399 | 1221768.2517 | 2677075.4553 | 1221764.3463
127 | 2677072.7275 | 1221780.789 | 2677069.425 | 1221797.2691
128 | 2677067.4964 | 1221806.143 | 2677067.884 | 1221804.9585 | 2677069.425 | 1221797.2691
129 | 2677062.442 | 1221821.5879 | 2677067.4964 | 1221806.143
130 | 2677134.8916 | 1221691.9302 | 2677137.4245 | 1221685.9094
131 | 2677032.7496 | 1221677.8721 | 2677035.977 | 1221664.9287
132 | 2677032.7496 | 1221677.8721 | 2677029.9836 | 1221688.9648

## bus_geodata
| x | y | coords
0 | 2676464.2507 | 1221796.2576
1 | 2676466.4317 | 1221777.2108
2 | 2676484.7011 | 1221764.4356
3 | 2676437.1898 | 1221782.5649
4 | 2676839.6959 | 1221864.2828
5 | 2676845.6918 | 1221866.3613
6 | 2676839.7505 | 1221866.9058
7 | 2676604.5964 | 1221615.2771
8 | 2676624.1099 | 1221619.1441
9 | 2676623.3186 | 1221614.0195
10 | 2676845.4758 | 1221596.959
11 | 2676846.5186 | 1221611.5894
12 | 2676895.5167 | 1221590.9056
13 | 2677216.8429 | 1221762.7113
14 | 2677236.5442 | 1221765.69
15 | 2677195.6528 | 1221756.6589
16 | 2677162.9238 | 1221750.4085
17 | 2677115.6517 | 1221741.2681
18 | 2677151.7182 | 1221768.8518
19 | 2677125.2023 | 1221714.9624
20 | 2677081.4725 | 1221733.9499
21 | 2677149.099 | 1221780.7053
22 | 2677130.2102 | 1221936.591
23 | 2677129.1506 | 1221927.4404
24 | 2677138.4081 | 1221998.8488
25 | 2677127.3906 | 1221900.8587
26 | 2677138.4785 | 1221999.4198
27 | 2677136.7005 | 1221866.8042
28 | 2677092.6149 | 1221911.1812
29 | 2677140.5749 | 1222016.418
30 | 2677137.2333 | 1221865.0347
31 | 2677050.3307 | 1221914.0135
32 | 2677141.7886 | 1222026.2593
33 | 2677029.15 | 1221919.6646
34 | 2677004.6054 | 1221929.0966
35 | 2676975.7367 | 1221938.586
36 | 2677144.034 | 1221842.4474
37 | 2676870.7605 | 1221875.0511
38 | 2676840.047 | 1221881.154
39 | 2676907.6275 | 1221887.8306
40 | 2676898.6814 | 1221910.9081
41 | 2676918.9549 | 1221821.9557
42 | 2676943.5478 | 1221826.8998
43 | 2676921.379 | 1221805.446
44 | 2676927.4003 | 1221922.1885
45 | 2676892.4606 | 1221922.2211
46 | 2676835.5566 | 1221970.5248
47 | 2676828.1321 | 1221973.3547
48 | 2676811.7154 | 1221979.1651
49 | 2676930.0181 | 1221923.2167
50 | 2676874.2443 | 1221838.1686
51 | 2676875.6012 | 1221833.6704
52 | 2676868.7644 | 1221856.3344
53 | 2676870.9199 | 1221806.3982
54 | 2676871.2245 | 1221801.1418
55 | 2676873.2249 | 1221784.0495
56 | 2676953.6291 | 1221828.9266
57 | 2676924.3362 | 1221785.3057
58 | 2676972.651 | 1221881.3244
59 | 2676973.7214 | 1221875.3671
60 | 2676977.9974 | 1221851.5704
61 | 2676979.172 | 1221845.0333
62 | 2676976.1695 | 1221833.4581
63 | 2677147.2305 | 1222070.383
64 | 2677163.2928 | 1222073.8767
65 | 2677281.4009 | 1222070.2557
66 | 2677282.9335 | 1222061.5137
67 | 2677239.7227 | 1222363.2753
68 | 2677280.7336 | 1221996.6206
69 | 2676874.6095 | 1221777.7389
70 | 2676883.0234 | 1221759.5614
71 | 2676889.7971 | 1221746.3988
72 | 2676892.5506 | 1221727.5675
73 | 2676893.9201 | 1221718.2011
74 | 2676925.0906 | 1221780.1679
75 | 2676929.7117 | 1221748.6947
76 | 2676937.178 | 1221705.6366
77 | 2676980.6569 | 1221716.0469
78 | 2676908.109 | 1221693.7979
79 | 2676894.337 | 1221715.3501
80 | 2676895.6704 | 1221708.618
81 | 2676910.4359 | 1221683.3877
82 | 2676891.0275 | 1221679.1822
83 | 2676928.798 | 1221656.1763
84 | 2676930.4669 | 1221645.0832
85 | 2676878.5345 | 1221672.3353
86 | 2676965.221 | 1221653.3803
87 | 2676979.6484 | 1221636.8698
88 | 2676998.6058 | 1221719.5173
89 | 2676866.322 | 1221667.8746
90 | 2676886.1958 | 1221651.8429
91 | 2676848.3272 | 1221637.5892
92 | 2676865.6754 | 1221644.121
93 | 2676847.3308 | 1221623.266
94 | 2676889.7256 | 1221644.7354
95 | 2676870.3687 | 1221645.8871
96 | 2676899.5616 | 1221635.9126
97 | 2676910.9489 | 1221636.7927
98 | 2676929.992 | 1221644.1477
99 | 2676917.47 | 1221639.3113
100 | 2676908.1269 | 1221589.6503
101 | 2676936.3403 | 1221586.8241
102 | 2676956.9481 | 1221583.8514
103 | 2676995.4324 | 1221620.5889
104 | 2677017.6934 | 1221632.0174
105 | 2676980.1637 | 1221636.2802
106 | 2677043.861 | 1221627.3352
107 | 2677041.1772 | 1221644.0736
108 | 2677038.2229 | 1221655.9217
109 | 2677008.7457 | 1221789.0148
110 | 2677009.0205 | 1221785.8623
111 | 2676998.2192 | 1221815.6757
112 | 2677001.6584 | 1221760.4533
113 | 2677001.2707 | 1221755.2544
114 | 2677000.0724 | 1221739.1851
115 | 2677021.4296 | 1221723.2704
116 | 2677077.1828 | 1221733.0314
117 | 2677026.9669 | 1221701.063
118 | 2677075.9917 | 1221754.6235
119 | 2677027.0868 | 1221700.5822
120 | 2677149.3172 | 1221793.2115
121 | 2677149.2926 | 1221809.0219
122 | 2677147.2396 | 1221826.4032
123 | 2677147.1205 | 1221827.3536
124 | 2677075.4553 | 1221764.3463
125 | 2677072.7275 | 1221780.789
126 | 2677069.425 | 1221797.2691
127 | 2677067.4964 | 1221806.143
128 | 2677062.442 | 1221821.5879
129 | 2677134.8916 | 1221691.9302
130 | 2677137.4245 | 1221685.9094
131 | 2677035.977 | 1221664.9287
132 | 2677032.7496 | 1221677.8721
133 | 2677029.9836 | 1221688.9648
134 | 2676998.2192 | 1221815.6757

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97521 | -0.47868 | 0.0024869 | 0.00062327
1 | 0.97525 | -0.4778 | 0 | 0
2 | 0.97531 | -0.47664 | 0.00085818 | 0.00021508
3 | 0.97524 | -0.478 | 0.00035465 | 8.8885e-05
4 | 0.9719 | -0.543 | 0.0017129 | 0.00042929
5 | 0.97195 | -0.54196 | 0.0018364 | 0.00046023
6 | 0.97188 | -0.54335 | 0.0017587 | 0.00044076
7 | 0.97597 | -0.46366 | 0.011808 | 0.0029594
8 | 0.97632 | -0.45686 | 0 | 0
9 | 0.97624 | -0.45833 | 0 | 0
10 | 0.97952 | -0.39393 | 0 | 0
11 | 0.97989 | -0.38679 | 0.0016346 | 0.00040968
12 | 0.97899 | -0.40426 | 0.0014586 | 0.00036556
13 | 0.98264 | -0.33286 | 0.02491 | 0.006243
14 | 0.9825 | -0.33563 | 0.0076938 | 0.0019282
15 | 0.9833 | -0.3199 | 0 | 0
16 | 0.98436 | -0.29918 | 0 | 0
17 | 0.98626 | -0.26243 | 0 | 0
18 | 0.98373 | -0.31158 | 0.0036565 | 0.00091639
19 | 0.98603 | -0.26701 | 0.0034342 | 0.00086068
20 | 0.98774 | -0.23386 | 0.0019248 | 0.00048239
21 | 0.98338 | -0.31834 | 0.0073936 | 0.001853
22 | 0.97989 | -0.38622 | 0.00093557 | 0.00023448
23 | 0.98001 | -0.38395 | 0.0011394 | 0.00028556
24 | 0.97915 | -0.40068 | 0.00077806 | 0.000195
25 | 0.98037 | -0.37682 | 0 | 0
26 | 0.97915 | -0.4008 | 0.00072092 | 0.00018068
27 | 0.98119 | -0.36079 | 0.001332 | 0.00033383
28 | 0.97969 | -0.39011 | 0.0014743 | 0.0003695
29 | 0.97897 | -0.40428 | 0.0020983 | 0.00052588
30 | 0.98124 | -0.35993 | 0.00091566 | 0.00022949
31 | 0.97891 | -0.40523 | 0.002213 | 0.00055462
32 | 0.97889 | -0.40592 | 0.0038513 | 0.00096522
33 | 0.97833 | -0.41655 | 0.002672 | 0.00066966
34 | 0.97767 | -0.42948 | 0.003567 | 0.00089398
35 | 0.97624 | -0.4575 | 0.0031143 | 0.00078053
36 | 0.9818 | -0.34893 | 0.00090691 | 0.00022729
37 | 0.97222 | -0.53673 | 0.0023423 | 0.00058703
38 | 0.97181 | -0.54477 | 0.0053873 | 0.0013502
39 | 0.97269 | -0.52735 | 0 | 0
40 | 0.97299 | -0.5214 | 0 | 0
41 | 0.9834 | -0.31829 | 0 | 0
42 | 0.98253 | -0.33542 | 0.0043433 | 0.0010885
43 | 0.98399 | -0.30691 | 0.0020715 | 0.00051917
44 | 0.97391 | -0.50339 | 0.0059399 | 0.0014887
45 | 0.97277 | -0.52585 | 0.0021971 | 0.00055066
46 | 0.97162 | -0.54856 | 0.0021732 | 0.00054465
47 | 0.97151 | -0.55066 | 0.0078462 | 0.0019664
48 | 0.97141 | -0.55274 | 0.0064752 | 0.0016228
49 | 0.97401 | -0.50144 | 0.0096221 | 0.0024115
50 | 0.98166 | -0.35224 | 0.0017435 | 0.00043696
51 | 0.98169 | -0.3518 | 0.002856 | 0.00071578
52 | 0.9816 | -0.35342 | 0.0034308 | 0.00085983
53 | 0.98189 | -0.34778 | 0.0026677 | 0.00066858
54 | 0.98194 | -0.34676 | 0.0017562 | 0.00044016
55 | 0.98214 | -0.34287 | 0.0070329 | 0.0017626
56 | 0.98221 | -0.34164 | 0.0087234 | 0.0021863
57 | 0.98474 | -0.29229 | 0.0018764 | 0.00047026
58 | 0.98098 | -0.36568 | 0.0088803 | 0.0022256
59 | 0.98103 | -0.36471 | 0.0034752 | 0.00087097
60 | 0.98131 | -0.3593 | 0.003465 | 0.00086842
61 | 0.9814 | -0.3574 | 0.0032872 | 0.00082385
62 | 0.98168 | -0.35195 | 0.005682 | 0.001424
63 | 0.97867 | -0.41014 | 0 | 0
64 | 0.97859 | -0.4117 | 0.0019351 | 0.00048498
65 | 0.97824 | -0.41877 | 0 | 0
66 | 0.97822 | -0.41917 | 0.00094718 | 0.00023739
67 | 0.978 | -0.4235 | 0.00087278 | 0.00021874
68 | 0.97813 | -0.42092 | 0.0014487 | 0.00036307
69 | 0.98226 | -0.3406 | 0.0054277 | 0.0013603
70 | 0.98272 | -0.3315 | 0.0057751 | 0.0014474
71 | 0.98315 | -0.32327 | 0.0030875 | 0.00077379
72 | 0.98374 | -0.31168 | 0.0041617 | 0.001043
73 | 0.98407 | -0.30521 | 0.0023463 | 0.00058805
74 | 0.98494 | -0.28838 | 0.0030203 | 0.00075695
75 | 0.98625 | -0.2628 | 0.0031005 | 0.00077706
76 | 0.98819 | -0.22532 | 0 | 0
77 | 0.99129 | -0.16572 | 0.0014745 | 0.00036954
78 | 0.98527 | -0.28176 | 0 | 0
79 | 0.98418 | -0.30312 | 0.0038614 | 0.00096775
80 | 0.98446 | -0.29764 | 0.001359 | 0.0003406
81 | 0.98473 | -0.29232 | 0 | 0
82 | 0.98372 | -0.312 | 0.0022357 | 0.00056032
83 | 0.98109 | -0.36325 | 0.002529 | 0.00063383
84 | 0.98112 | -0.36269 | 0.0028553 | 0.0007156
85 | 0.98282 | -0.32948 | 0 | 0
86 | 0.98812 | -0.22698 | 0.0023106 | 0.00057909
87 | 0.98817 | -0.22608 | 0.0021604 | 0.00054145
88 | 0.99213 | -0.14952 | 0 | 0
89 | 0.9828 | -0.32988 | 0.0017115 | 0.00042894
90 | 0.98178 | -0.34969 | 0 | 0
91 | 0.98059 | -0.37293 | 0 | 0
92 | 0.98111 | -0.36283 | 0.0018262 | 0.00045768
93 | 0.98019 | -0.38075 | 0.0016074 | 0.00040285
94 | 0.98166 | -0.35221 | 0.0022458 | 0.00056285
95 | 0.98126 | -0.35994 | 0.0016443 | 0.00041211
96 | 0.98144 | -0.35636 | 0.0018288 | 0.00045833
97 | 0.9813 | -0.35924 | 0.0024918 | 0.00062451
98 | 0.98113 | -0.36259 | 0.0026411 | 0.00066191
99 | 0.98122 | -0.36064 | 0.0030248 | 0.00075808
100 | 0.97888 | -0.40653 | 0.0027497 | 0.00068913
101 | 0.97869 | -0.41017 | 0.0032301 | 0.00080955
102 | 0.97862 | -0.41163 | 0.0038385 | 0.00096201
103 | 0.98832 | -0.22328 | 0 | 0
104 | 0.98848 | -0.22016 | 0.0027052 | 0.00067798
105 | 0.98817 | -0.22601 | 0.0025148 | 0.00063026
106 | 0.98864 | -0.21703 | 0.0047245 | 0.0011841
107 | 0.98871 | -0.2156 | 0.0016845 | 0.00042217
108 | 0.98889 | -0.21209 | 0.0033418 | 0.00083752
109 | 1 | 0 | -0.37145 | -0.094978
110 | 0.99965 | -0.0066323 | 0.0044173 | 0.0011071
111 | 0.99991 | -0.0017256 | 0.0032665 | 0.00081866
112 | 0.99654 | -0.065443 | 0.0032013 | 0.00080231
113 | 0.99597 | -0.076216 | 0.0035279 | 0.00088416
114 | 0.99424 | -0.10926 | 0.0028413 | 0.00071209
115 | 0.99073 | -0.17633 | 0 | 0
116 | 0.98793 | -0.23023 | 0 | 0
117 | 0.98998 | -0.19085 | 0.0020591 | 0.00051607
118 | 0.9875 | -0.2387 | 0.0033412 | 0.00083737
119 | 0.98997 | -0.19115 | 0.0025938 | 0.00065006
120 | 0.98305 | -0.32467 | 0.0012026 | 0.00030141
121 | 0.98264 | -0.33258 | 0.0013071 | 0.0003276
122 | 0.9822 | -0.34119 | 0.0023487 | 0.00058865
123 | 0.98218 | -0.34165 | 0.0011326 | 0.00028386
124 | 0.98733 | -0.24193 | 0.0030913 | 0.00077476
125 | 0.98709 | -0.24655 | 0.003632 | 0.00091026
126 | 0.98691 | -0.25012 | 0.0022577 | 0.00056583
127 | 0.98683 | -0.25168 | 0.0022064 | 0.00055296
128 | 0.98672 | -0.25383 | 0.0073846 | 0.0018508
129 | 0.9859 | -0.26957 | 0.0032012 | 0.0008023
130 | 0.98588 | -0.26986 | 0.0024917 | 0.00062447
131 | 0.98906 | -0.20888 | 0.0029414 | 0.00073718
132 | 0.98933 | -0.20356 | 0.0060707 | 0.0015215
133 | 0.98963 | -0.19777 | 0.0026038 | 0.00065258
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0024869 | -0.00062327 | 0.002487 | 0.0006231 | 1.0352e-07 | -1.7296e-07 | 0.0037946 | 0.0037945 | 0.0037946 | 0.97521 | -0.47868 | 0.97525 | -0.4778 | 1.0425
1 | -0.0028416 | -0.00071162 | 0.0028418 | 0.00071144 | 1.5713e-07 | -1.7762e-07 | 0.0043355 | 0.0043354 | 0.0043355 | 0.97525 | -0.4778 | 0.97531 | -0.47664 | 1.1911
2 | 0.00035466 | 8.8516e-05 | -0.00035465 | -8.8885e-05 | 3.2635e-09 | -3.6885e-07 | 0.00054099 | 0.00054113 | 0.00054113 | 0.97525 | -0.4778 | 0.97524 | -0.478 | 0.14866
3 | -0.0037 | -0.00092652 | 0.0037023 | 0.00092559 | 2.2863e-06 | -9.2663e-07 | 0.0056447 | 0.0056439 | 0.0056447 | 0.97531 | -0.47664 | 0.97597 | -0.46366 | 1.5507
4 | -0.0088594 | -0.0022203 | 0.0088598 | 0.0022205 | 4.3783e-07 | 2.0157e-07 | 0.013564 | 0.013564 | 0.013564 | 0.9719 | -0.543 | 0.97195 | -0.54196 | 3.7264
5 | 0.0071465 | 0.0017911 | -0.0071464 | -0.001791 | 1.1778e-07 | 4.2869e-08 | 0.010942 | 0.010942 | 0.010942 | 0.9719 | -0.543 | 0.97188 | -0.54335 | 3.0059
6 | -0.010696 | -0.0026808 | 0.010699 | 0.0026822 | 2.668e-06 | 1.3786e-06 | 0.016375 | 0.016375 | 0.016375 | 0.97195 | -0.54196 | 0.97222 | -0.53673 | 4.4987
7 | 0.0053877 | 0.0013503 | -0.0053873 | -0.0013502 | 3.6365e-07 | 5.6148e-08 | 0.0082489 | 0.008249 | 0.008249 | 0.97188 | -0.54335 | 0.97181 | -0.54477 | 2.2662
8 | -0.01551 | -0.0038849 | 0.015514 | 0.0038872 | 3.9347e-06 | 2.2837e-06 | 0.023647 | 0.023647 | 0.023647 | 0.97597 | -0.46366 | 0.97624 | -0.45833 | 6.4964
9 | 0.015515 | 0.0038879 | -0.015514 | -0.0038872 | 1.0874e-06 | 6.3112e-07 | 0.023647 | 0.023647 | 0.023647 | 0.97632 | -0.45686 | 0.97624 | -0.45833 | 6.4964
10 | -0.015515 | -0.0038879 | 0.015562 | 0.0039149 | 4.6649e-05 | 2.7064e-05 | 0.023647 | 0.023646 | 0.023647 | 0.97632 | -0.45686 | 0.97952 | -0.39393 | 6.4964
11 | -0.026847 | -0.0067449 | 0.026856 | 0.0067506 | 9.1514e-06 | 5.6722e-06 | 0.04079 | 0.04079 | 0.04079 | 0.97952 | -0.39393 | 0.97989 | -0.38679 | 11.206
12 | 0.011285 | 0.00283 | -0.011279 | -0.0028271 | 5.5561e-06 | 2.9217e-06 | 0.017144 | 0.017144 | 0.017144 | 0.97952 | -0.39393 | 0.97899 | -0.40426 | 4.7099
13 | -0.028491 | -0.0071603 | 0.028499 | 0.0071654 | 8.2188e-06 | 5.1125e-06 | 0.043272 | 0.043272 | 0.043272 | 0.97989 | -0.38679 | 0.98019 | -0.38075 | 11.8879
14 | 0.0098208 | 0.0024615 | -0.0098198 | -0.002461 | 1.0589e-06 | 5.1836e-07 | 0.014927 | 0.014927 | 0.014927 | 0.97899 | -0.40426 | 0.97888 | -0.40653 | 4.1009
15 | 0.0076948 | 0.0019286 | -0.0076938 | -0.0019282 | 1.0166e-06 | 3.9774e-07 | 0.011652 | 0.011652 | 0.011652 | 0.98264 | -0.33286 | 0.9825 | -0.33563 | 3.2012
16 | -0.032605 | -0.0081716 | 0.032625 | 0.0081842 | 2.0152e-05 | 1.2618e-05 | 0.049373 | 0.049373 | 0.049373 | 0.98264 | -0.33286 | 0.9833 | -0.3199 | 13.5641
17 | -0.032625 | -0.0081842 | 0.032657 | 0.0082044 | 3.2247e-05 | 2.019e-05 | 0.049373 | 0.049373 | 0.049373 | 0.9833 | -0.3199 | 0.98436 | -0.29918 | 13.5641
18 | -0.12862 | -0.03251 | 0.12885 | 0.032654 | 0.00022711 | 0.00014352 | 0.19453 | 0.19453 | 0.19453 | 0.98436 | -0.29918 | 0.98626 | -0.26243 | 17.8143
19 | 0.095967 | 0.024306 | -0.09591 | -0.02427 | 5.711e-05 | 3.5724e-05 | 0.14516 | 0.14516 | 0.14516 | 0.98436 | -0.29918 | 0.98373 | -0.31158 | 13.293
20 | 0.0091298 | 0.0022884 | -0.0091278 | -0.0022875 | 1.9934e-06 | 9.1832e-07 | 0.013775 | 0.013775 | 0.013775 | 0.98626 | -0.26243 | 0.98603 | -0.26701 | 3.7843
21 | -0.13798 | -0.034942 | 0.13817 | 0.035062 | 0.00018959 | 0.00012 | 0.20831 | 0.20831 | 0.20831 | 0.98626 | -0.26243 | 0.98774 | -0.23386 | 19.0757
22 | 0.092253 | 0.023354 | -0.092223 | -0.023335 | 2.989e-05 | 1.8663e-05 | 0.13963 | 0.13963 | 0.13963 | 0.98373 | -0.31158 | 0.98338 | -0.31834 | 12.7866
23 | 0.0056936 | 0.0014268 | -0.0056929 | -0.0014267 | 6.9177e-07 | 1.2406e-07 | 0.0085922 | 0.0085923 | 0.0085923 | 0.98603 | -0.26701 | 0.9859 | -0.26957 | 2.3605
24 | -0.1401 | -0.035545 | 0.14012 | 0.03556 | 2.4461e-05 | 1.5487e-05 | 0.21121 | 0.21121 | 0.21121 | 0.98774 | -0.23386 | 0.98793 | -0.23023 | 19.3412
25 | 0.08483 | 0.021482 | -0.084804 | -0.021466 | 2.5793e-05 | 1.6032e-05 | 0.12844 | 0.12844 | 0.12844 | 0.98338 | -0.31834 | 0.98305 | -0.32467 | 11.762
26 | -0.013602 | -0.0034065 | 0.013604 | 0.0034073 | 1.4743e-06 | 8.2747e-07 | 0.020655 | 0.020655 | 0.020655 | 0.97989 | -0.38622 | 0.98001 | -0.38395 | 5.6743
27 | 0.012667 | 0.003172 | -0.012658 | -0.0031672 | 8.7117e-06 | 4.785e-06 | 0.019234 | 0.019234 | 0.019234 | 0.97989 | -0.38622 | 0.97915 | -0.40068 | 5.2841
28 | -0.014743 | -0.0036929 | 0.014748 | 0.0036957 | 5.0057e-06 | 2.8678e-06 | 0.022385 | 0.022384 | 0.022385 | 0.98001 | -0.38395 | 0.98037 | -0.37682 | 6.1496
29 | 0.01188 | 0.0029722 | -0.01188 | -0.0029722 | 7.0301e-08 | 3.7757e-08 | 0.018052 | 0.018052 | 0.018052 | 0.97915 | -0.40068 | 0.97915 | -0.4008 | 4.9593
30 | -0.075461 | -0.019052 | 0.075519 | 0.019088 | 5.8011e-05 | 3.5789e-05 | 0.11459 | 0.11459 | 0.11459 | 0.98037 | -0.37682 | 0.98119 | -0.36079 | 10.4932
31 | 0.060713 | 0.015356 | -0.060675 | -0.015333 | 3.8676e-05 | 2.3377e-05 | 0.092202 | 0.092202 | 0.092202 | 0.98037 | -0.37682 | 0.97969 | -0.39011 | 8.4434
32 | 0.011159 | 0.0027915 | -0.011157 | -0.0027905 | 1.8466e-06 | 9.6643e-07 | 0.016956 | 0.016956 | 0.016956 | 0.97915 | -0.4008 | 0.97897 | -0.40428 | 4.6583
33 | -0.076851 | -0.019422 | 0.076854 | 0.019423 | 3.1408e-06 | 1.9401e-06 | 0.11661 | 0.11661 | 0.11661 | 0.98119 | -0.36079 | 0.98124 | -0.35993 | 10.6782
34 | 0.0592 | 0.014963 | -0.059157 | -0.014937 | 4.2892e-05 | 2.585e-05 | 0.089963 | 0.089963 | 0.089963 | 0.97969 | -0.39011 | 0.97891 | -0.40523 | 8.2384
35 | 0.0090586 | 0.0022647 | -0.0090579 | -0.0022643 | 7.0475e-07 | 3.2637e-07 | 0.013767 | 0.013767 | 0.013767 | 0.97897 | -0.40428 | 0.97889 | -0.40592 | 3.7821
36 | -0.07777 | -0.019653 | 0.077811 | 0.019678 | 4.1052e-05 | 2.5379e-05 | 0.11799 | 0.11799 | 0.11799 | 0.98124 | -0.35993 | 0.9818 | -0.34893 | 10.8053
37 | 0.056944 | 0.014383 | -0.056913 | -0.014364 | 3.0881e-05 | 1.9212e-05 | 0.086599 | 0.0866 | 0.0866 | 0.97891 | -0.40523 | 0.97833 | -0.41655 | 11.8956
38 | 0.0052066 | 0.0012991 | -0.0052056 | -0.001299 | 1.0438e-06 | 1.0927e-07 | 0.0079125 | 0.0079127 | 0.0079127 | 0.97889 | -0.40592 | 0.97867 | -0.41014 | 2.1738
39 | 0.054241 | 0.013694 | -0.054208 | -0.013673 | 3.3585e-05 | 2.0835e-05 | 0.082536 | 0.082536 | 0.082536 | 0.97833 | -0.41655 | 0.97767 | -0.42948 | 11.3374
40 | 0.050641 | 0.012779 | -0.050573 | -0.012736 | 6.7844e-05 | 4.3039e-05 | 0.077107 | 0.077107 | 0.077107 | 0.97767 | -0.42948 | 0.97624 | -0.4575 | 21.1833
41 | 0.047459 | 0.011956 | -0.047359 | -0.011893 | 9.9512e-05 | 6.3055e-05 | 0.07236 | 0.07236 | 0.07236 | 0.97624 | -0.4575 | 0.97401 | -0.50144 | 19.8792
42 | -0.078718 | -0.019906 | 0.078745 | 0.019923 | 2.7515e-05 | 1.7023e-05 | 0.11937 | 0.11937 | 0.11937 | 0.9818 | -0.34893 | 0.98218 | -0.34165 | 10.9312
43 | -0.013041 | -0.0032692 | 0.013047 | 0.0032724 | 5.8295e-06 | 3.2468e-06 | 0.01996 | 0.01996 | 0.01996 | 0.97222 | -0.53673 | 0.97269 | -0.52735 | 5.4836
44 | -0.013047 | -0.0032724 | 0.013051 | 0.0032745 | 3.7036e-06 | 2.0625e-06 | 0.01996 | 0.01996 | 0.01996 | 0.97269 | -0.52735 | 0.97299 | -0.5214 | 5.4835
45 | -0.031766 | -0.007973 | 0.031794 | 0.0079901 | 2.7312e-05 | 1.7096e-05 | 0.048585 | 0.048585 | 0.048585 | 0.97299 | -0.5214 | 0.97391 | -0.50339 | 13.3475
46 | 0.018716 | 0.0046985 | -0.018712 | -0.0046961 | 3.9728e-06 | 2.382e-06 | 0.028625 | 0.028625 | 0.028625 | 0.97299 | -0.5214 | 0.97277 | -0.52585 | 7.864
47 | 0.03792 | 0.0095267 | -0.037889 | -0.0095072 | 3.0978e-05 | 1.9508e-05 | 0.057385 | 0.057386 | 0.057386 | 0.9834 | -0.31829 | 0.98253 | -0.33542 | 15.7652
48 | -0.03792 | -0.0095267 | 0.03794 | 0.0095397 | 2.0607e-05 | 1.2976e-05 | 0.057385 | 0.057385 | 0.057385 | 0.9834 | -0.31829 | 0.98399 | -0.30691 | 15.7652
49 | 0.033545 | 0.0084187 | -0.033535 | -0.0084124 | 9.9543e-06 | 6.2405e-06 | 0.050808 | 0.050808 | 0.050808 | 0.98253 | -0.33542 | 0.98221 | -0.34164 | 13.9582
50 | -0.040012 | -0.010059 | 0.04004 | 0.010076 | 2.7957e-05 | 1.7634e-05 | 0.060518 | 0.060518 | 0.060518 | 0.98399 | -0.30691 | 0.98474 | -0.29229 | 16.6258
51 | -0.037734 | -0.0094788 | 0.037737 | 0.009481 | 3.5066e-06 | 2.2092e-06 | 0.05766 | 0.05766 | 0.05766 | 0.97391 | -0.50339 | 0.97401 | -0.50144 | 15.8408
52 | 0.016515 | 0.0041455 | -0.016497 | -0.004135 | 1.7866e-05 | 1.0509e-05 | 0.025264 | 0.025265 | 0.025265 | 0.97277 | -0.52585 | 0.97162 | -0.54856 | 6.9408
53 | 0.014324 | 0.0035903 | -0.014322 | -0.0035895 | 1.4338e-06 | 8.1923e-07 | 0.021936 | 0.021936 | 0.021936 | 0.97162 | -0.54856 | 0.97151 | -0.55066 | 6.0265
54 | 0.0064759 | 0.001623 | -0.0064752 | -0.0016228 | 6.4291e-07 | 1.9571e-07 | 0.0099188 | 0.0099189 | 0.0099189 | 0.97151 | -0.55066 | 0.97141 | -0.55274 | 2.725
55 | -0.0051744 | -0.0012967 | 0.0051746 | 0.0012967 | 1.0839e-07 | 9.9684e-09 | 0.0078434 | 0.0078434 | 0.0078434 | 0.98166 | -0.35224 | 0.98169 | -0.3518 | 2.1548
56 | 0.003431 | 0.00085971 | -0.0034308 | -0.00085983 | 1.9245e-07 | -1.167e-07 | 0.0052006 | 0.0052007 | 0.0052007 | 0.98166 | -0.35224 | 0.9816 | -0.35342 | 1.4288
57 | -0.0080305 | -0.0020125 | 0.0080321 | 0.0020131 | 1.5394e-06 | 6.3484e-07 | 0.012172 | 0.012172 | 0.012172 | 0.98169 | -0.3518 | 0.98189 | -0.34778 | 3.3441
58 | -0.0107 | -0.0026817 | 0.0107 | 0.0026819 | 5.1914e-07 | 2.6565e-07 | 0.016215 | 0.016215 | 0.016215 | 0.98189 | -0.34778 | 0.98194 | -0.34676 | 4.4547
59 | -0.012457 | -0.0031221 | 0.012459 | 0.0031234 | 2.3062e-06 | 1.2576e-06 | 0.018876 | 0.018876 | 0.018876 | 0.98194 | -0.34676 | 0.98214 | -0.34287 | 5.1858
60 | -0.019492 | -0.004886 | 0.019494 | 0.0048872 | 2.1129e-06 | 1.2705e-06 | 0.029532 | 0.029532 | 0.029532 | 0.98214 | -0.34287 | 0.98226 | -0.3406 | 8.1131
61 | 0.024812 | 0.0062261 | -0.0248 | -0.0062186 | 1.2184e-05 | 7.5069e-06 | 0.037592 | 0.037592 | 0.037592 | 0.98221 | -0.34164 | 0.98168 | -0.35195 | 10.3275
62 | -0.041916 | -0.010547 | 0.041924 | 0.010552 | 7.8159e-06 | 4.9361e-06 | 0.063353 | 0.063353 | 0.063353 | 0.98474 | -0.29229 | 0.98494 | -0.28838 | 17.4047
63 | -0.0088803 | -0.0022256 | 0.0088807 | 0.0022258 | 4.1184e-07 | 1.8716e-07 | 0.01347 | 0.01347 | 0.01347 | 0.98098 | -0.36568 | 0.98103 | -0.36471 | 3.7006
64 | -0.012356 | -0.0030968 | 0.012359 | 0.0030985 | 3.1845e-06 | 1.7328e-06 | 0.018741 | 0.018741 | 0.018741 | 0.98103 | -0.36471 | 0.98131 | -0.3593 | 5.1487
65 | -0.015824 | -0.0039669 | 0.015826 | 0.0039678 | 1.4341e-06 | 8.3391e-07 | 0.023996 | 0.023996 | 0.023996 | 0.98131 | -0.3593 | 0.9814 | -0.3574 | 6.5922
66 | -0.019113 | -0.0047916 | 0.019118 | 0.0047946 | 4.964e-06 | 2.9777e-06 | 0.02898 | 0.02898 | 0.02898 | 0.9814 | -0.3574 | 0.98168 | -0.35195 | 7.9614
67 | 0.0052056 | 0.001299 | -0.0052052 | -0.001299 | 3.8595e-07 | 4.0473e-08 | 0.0079127 | 0.0079128 | 0.0079128 | 0.97867 | -0.41014 | 0.97859 | -0.4117 | 2.1738
68 | 0.0032701 | 0.00081398 | -0.003269 | -0.00081476 | 1.0948e-06 | -7.8334e-07 | 0.0049704 | 0.0049709 | 0.0049709 | 0.97859 | -0.4117 | 0.97824 | -0.41877 | 1.3656
69 | 0.002396 | 0.00059961 | -0.002396 | -0.0005997 | 4.5589e-08 | -8.5739e-08 | 0.0036443 | 0.0036444 | 0.0036444 | 0.97824 | -0.41877 | 0.97822 | -0.41917 | 1.0012
70 | 0.00087297 | 0.00021515 | -0.00087278 | -0.00021874 | 1.9552e-07 | -3.5897e-06 | 0.0013266 | 0.0013279 | 0.0013279 | 0.97824 | -0.41877 | 0.978 | -0.4235 | 0.36481
71 | 0.0014488 | 0.00036231 | -0.0014487 | -0.00036307 | 1.2126e-07 | -7.5825e-07 | 0.0022036 | 0.0022039 | 0.0022039 | 0.97822 | -0.41917 | 0.97813 | -0.42092 | 0.60545
72 | -0.024922 | -0.0062475 | 0.024932 | 0.0062542 | 1.0813e-05 | 6.6641e-06 | 0.037754 | 0.037754 | 0.037754 | 0.98226 | -0.3406 | 0.98272 | -0.3315 | 10.372
73 | -0.030707 | -0.0077016 | 0.030719 | 0.0077091 | 1.205e-05 | 7.5236e-06 | 0.046498 | 0.046498 | 0.046498 | 0.98272 | -0.3315 | 0.98315 | -0.32327 | 12.7743
74 | -0.033807 | -0.0084829 | 0.033826 | 0.0084946 | 1.8688e-05 | 1.1719e-05 | 0.051171 | 0.051171 | 0.051171 | 0.98315 | -0.32327 | 0.98374 | -0.31168 | 14.058
75 | -0.037987 | -0.0095376 | 0.037999 | 0.009545 | 1.1723e-05 | 7.3822e-06 | 0.057466 | 0.057466 | 0.057466 | 0.98374 | -0.31168 | 0.98407 | -0.30521 | 15.7874
76 | -0.040345 | -0.010133 | 0.040349 | 0.010136 | 4.0224e-06 | 2.5378e-06 | 0.061014 | 0.061014 | 0.061014 | 0.98407 | -0.30521 | 0.98418 | -0.30312 | 16.7621
77 | -0.044944 | -0.011309 | 0.044999 | 0.011343 | 5.5024e-05 | 3.481e-05 | 0.067916 | 0.067916 | 0.067916 | 0.98494 | -0.28838 | 0.98625 | -0.2628 | 18.6583
78 | -0.0481 | -0.01212 | 0.048186 | 0.012175 | 8.64e-05 | 5.4737e-05 | 0.072594 | 0.072594 | 0.072594 | 0.98625 | -0.2628 | 0.98819 | -0.22532 | 19.9434
79 | -0.14945 | -0.03781 | 0.14987 | 0.038083 | 0.00042873 | 0.00027323 | 0.22516 | 0.22516 | 0.22516 | 0.98819 | -0.22532 | 0.99129 | -0.16572 | 30.9288
80 | 0.10126 | 0.025634 | -0.10099 | -0.02546 | 0.00027357 | 0.00017469 | 0.15257 | 0.15257 | 0.15257 | 0.98819 | -0.22532 | 0.98527 | -0.28176 | 41.9142
81 | -0.15135 | -0.038452 | 0.15147 | 0.038527 | 0.00011814 | 7.4903e-05 | 0.22737 | 0.22737 | 0.22737 | 0.99129 | -0.16572 | 0.99213 | -0.14952 | 20.8218
82 | 0.05537 | 0.013987 | -0.055342 | -0.013969 | 2.8001e-05 | 1.7785e-05 | 0.083662 | 0.083662 | 0.083662 | 0.98527 | -0.28176 | 0.98473 | -0.29232 | 22.984
83 | 0.045616 | 0.011473 | -0.045581 | -0.011451 | 3.4564e-05 | 2.1874e-05 | 0.068906 | 0.068906 | 0.068906 | 0.98527 | -0.28176 | 0.98446 | -0.29764 | 18.9303
84 | -0.044211 | -0.011103 | 0.044222 | 0.011111 | 1.1579e-05 | 7.3227e-06 | 0.066852 | 0.066852 | 0.066852 | 0.98418 | -0.30312 | 0.98446 | -0.29764 | 18.366
85 | 0.055342 | 0.013969 | -0.05529 | -0.013936 | 5.2124e-05 | 3.3107e-05 | 0.083662 | 0.083662 | 0.083662 | 0.98473 | -0.29232 | 0.98372 | -0.312 | 22.984
86 | 0.053054 | 0.013375 | -0.05301 | -0.013347 | 4.4333e-05 | 2.814e-05 | 0.08028 | 0.08028 | 0.08028 | 0.98372 | -0.312 | 0.98282 | -0.32948 | 22.0549
87 | -0.002529 | -0.00063383 | 0.0025291 | 0.00063372 | 6.7121e-08 | -1.1067e-07 | 0.0038357 | 0.0038357 | 0.0038357 | 0.98109 | -0.36325 | 0.98112 | -0.36269 | 1.0538
88 | -0.0053843 | -0.0013493 | 0.0053844 | 0.0013493 | 2.6236e-08 | 3.5417e-09 | 0.0081661 | 0.0081661 | 0.0081661 | 0.98112 | -0.36269 | 0.98113 | -0.36259 | 2.2434
89 | 0.051298 | 0.012918 | -0.051249 | -0.012887 | 4.9508e-05 | 3.1408e-05 | 0.077689 | 0.077689 | 0.077689 | 0.98282 | -0.32948 | 0.98178 | -0.34969 | 21.3431
90 | 0.0017115 | 0.0004288 | -0.0017115 | -0.00042894 | 3.2739e-08 | -1.4381e-07 | 0.0025913 | 0.0025913 | 0.0025913 | 0.98282 | -0.32948 | 0.9828 | -0.32988 | 0.7119
91 | -0.0023106 | -0.00057909 | 0.0023107 | 0.00057887 | 9.9544e-08 | -2.1717e-07 | 0.0034795 | 0.0034794 | 0.0034795 | 0.98812 | -0.22698 | 0.98817 | -0.22608 | 0.95591
92 | -0.0044711 | -0.0011203 | 0.0044711 | 0.0011203 | 1.331e-08 | -1.5129e-09 | 0.0067326 | 0.0067326 | 0.0067326 | 0.98817 | -0.22608 | 0.98817 | -0.22601 | 1.8496
93 | 0.1985 | 0.050478 | -0.19824 | -0.050315 | 0.00025597 | 0.00016293 | 0.29797 | 0.29797 | 0.29797 | 0.99213 | -0.14952 | 0.99073 | -0.17633 | 27.2867
94 | -0.34996 | -0.089005 | 0.35064 | 0.08944 | 0.00068039 | 0.00043468 | 0.52534 | 0.52534 | 0.52534 | 0.99213 | -0.14952 | 0.99424 | -0.10926 | 48.1084
95 | 0.017625 | 0.0044198 | -0.017623 | -0.0044185 | 2.1237e-06 | 1.2588e-06 | 0.026714 | 0.026714 | 0.026714 | 0.98178 | -0.34969 | 0.98166 | -0.35221 | 7.339
96 | 0.033623 | 0.0084672 | -0.033607 | -0.0084569 | 1.6478e-05 | 1.0332e-05 | 0.050975 | 0.050975 | 0.050975 | 0.98178 | -0.34969 | 0.98126 | -0.35994 | 14.0041
97 | -0.030118 | -0.0075753 | 0.030132 | 0.0075843 | 1.4526e-05 | 9.0625e-06 | 0.045712 | 0.045712 | 0.045712 | 0.98059 | -0.37293 | 0.98111 | -0.36283 | 12.5582
98 | 0.030118 | 0.0075753 | -0.030106 | -0.0075683 | 1.1251e-05 | 7.0194e-06 | 0.045712 | 0.045712 | 0.045712 | 0.98059 | -0.37293 | 0.98019 | -0.38075 | 12.5582
99 | -0.031958 | -0.008042 | 0.031963 | 0.0080448 | 4.42e-06 | 2.7655e-06 | 0.048482 | 0.048482 | 0.048482 | 0.98111 | -0.36283 | 0.98126 | -0.35994 | 13.3191
100 | 0.015377 | 0.0038556 | -0.015374 | -0.0038539 | 3.0368e-06 | 1.7552e-06 | 0.02331 | 0.02331 | 0.02331 | 0.98166 | -0.35221 | 0.98144 | -0.35636 | 6.4038
101 | 0.013545 | 0.0033956 | -0.013544 | -0.0033945 | 1.8604e-06 | 1.0421e-06 | 0.020537 | 0.020537 | 0.020537 | 0.98144 | -0.35636 | 0.9813 | -0.35924 | 5.6421
102 | 0.011052 | 0.00277 | -0.011051 | -0.0027696 | 7.3624e-07 | 3.8289e-07 | 0.016759 | 0.016759 | 0.016759 | 0.9813 | -0.35924 | 0.98122 | -0.36064 | 4.604
103 | -0.0080254 | -0.0020112 | 0.0080262 | 0.0020115 | 7.4576e-07 | 3.0774e-07 | 0.012172 | 0.012172 | 0.012172 | 0.98113 | -0.36259 | 0.98122 | -0.36064 | 3.3439
104 | 0.0070701 | 0.0017719 | -0.0070689 | -0.0017715 | 1.2282e-06 | 4.2967e-07 | 0.010747 | 0.010748 | 0.010748 | 0.97888 | -0.40653 | 0.97869 | -0.41017 | 2.9526
105 | 0.0038387 | 0.00096192 | -0.0038385 | -0.00096201 | 2.6657e-07 | -9.1609e-08 | 0.0058364 | 0.0058365 | 0.0058365 | 0.97869 | -0.41017 | 0.97862 | -0.41163 | 1.6034
106 | -0.0069868 | -0.0017509 | 0.0069878 | 0.0017512 | 1.0384e-06 | 3.4383e-07 | 0.010519 | 0.010519 | 0.010519 | 0.98832 | -0.22328 | 0.98848 | -0.22016 | 2.8899
107 | 0.0069868 | 0.0017509 | -0.0069859 | -0.0017506 | 9.0868e-07 | 3.0099e-07 | 0.010519 | 0.010519 | 0.010519 | 0.98832 | -0.22328 | 0.98817 | -0.22601 | 2.8899
108 | -0.009693 | -0.0024292 | 0.0096951 | 0.0024302 | 2.1076e-06 | 1.0104e-06 | 0.014591 | 0.014591 | 0.014591 | 0.98848 | -0.22016 | 0.98871 | -0.2156 | 4.0086
109 | -0.0047245 | -0.0011841 | 0.0047248 | 0.0011841 | 3.2145e-07 | -1.1666e-08 | 0.007111 | 0.0071109 | 0.007111 | 0.98864 | -0.21703 | 0.98871 | -0.2156 | 1.9536
110 | -0.016104 | -0.0040364 | 0.016107 | 0.004038 | 2.69e-06 | 1.565e-06 | 0.024237 | 0.024237 | 0.024237 | 0.98871 | -0.2156 | 0.98889 | -0.21209 | 6.6586
111 | -0.019449 | -0.0048755 | 0.019452 | 0.0048773 | 2.9814e-06 | 1.789e-06 | 0.029266 | 0.029266 | 0.029266 | 0.98889 | -0.21209 | 0.98906 | -0.20888 | 8.0401
112 | 0.36653 | 0.094159 | -0.36641 | -0.094084 | 0.00011801 | 7.5405e-05 | 0.54622 | 0.54622 | 0.54622 | 1 | 0 | 0.99965 | -0.0066323 | 50.0203
113 | 0.0032667 | 0.00081843 | -0.0032665 | -0.00081866 | 2.6851e-07 | -2.2567e-07 | 0.0048609 | 0.004861 | 0.004861 | 1 | 0 | 0.99991 | -0.0017256 | 1.3354
114 | 0.362 | 0.092977 | -0.36097 | -0.092319 | 0.0010305 | 0.00065843 | 0.53965 | 0.53965 | 0.53965 | 0.99965 | -0.0066323 | 0.99654 | -0.065443 | 49.4182
115 | 0.35776 | 0.091516 | -0.35758 | -0.091397 | 0.00018643 | 0.00011911 | 0.53487 | 0.53487 | 0.53487 | 0.99654 | -0.065443 | 0.99597 | -0.076216 | 48.9804
116 | 0.35405 | 0.090513 | -0.35349 | -0.090152 | 0.00056494 | 0.00036093 | 0.5296 | 0.5296 | 0.5296 | 0.99597 | -0.076216 | 0.99424 | -0.10926 | 48.4978
117 | 0.16247 | 0.04133 | -0.16205 | -0.041063 | 0.00042086 | 0.00026717 | 0.24424 | 0.24424 | 0.24424 | 0.99073 | -0.17633 | 0.98793 | -0.23023 | 22.3664
118 | 0.035769 | 0.008985 | -0.035744 | -0.0089694 | 2.4778e-05 | 1.5563e-05 | 0.05373 | 0.05373 | 0.05373 | 0.99073 | -0.17633 | 0.98998 | -0.19085 | 14.7611
119 | 0.021932 | 0.0055027 | -0.021923 | -0.0054973 | 8.8502e-06 | 5.3873e-06 | 0.033036 | 0.033036 | 0.033036 | 0.98793 | -0.23023 | 0.9875 | -0.2387 | 9.0758
120 | 0.033685 | 0.0084534 | -0.033685 | -0.0084531 | 4.7644e-07 | 2.9855e-07 | 0.050635 | 0.050635 | 0.050635 | 0.98998 | -0.19085 | 0.98997 | -0.19115 | 13.9108
121 | 0.018582 | 0.0046599 | -0.018579 | -0.0046582 | 2.8631e-06 | 1.7078e-06 | 0.028001 | 0.028001 | 0.028001 | 0.9875 | -0.2387 | 0.98733 | -0.24193 | 7.6926
122 | 0.031091 | 0.007803 | -0.031081 | -0.0077969 | 9.8074e-06 | 6.1229e-06 | 0.046737 | 0.046737 | 0.046737 | 0.98997 | -0.19115 | 0.98963 | -0.19777 | 12.8398
123 | 0.083601 | 0.021165 | -0.08357 | -0.021145 | 3.1721e-05 | 1.97e-05 | 0.12662 | 0.12662 | 0.12662 | 0.98305 | -0.32467 | 0.98264 | -0.33258 | 11.5954
124 | 0.082262 | 0.020817 | -0.082229 | -0.020796 | 3.3988e-05 | 2.1088e-05 | 0.12464 | 0.12464 | 0.12464 | 0.98264 | -0.33258 | 0.9822 | -0.34119 | 11.4141
125 | 0.07988 | 0.020208 | -0.079878 | -0.020207 | 1.7554e-06 | 1.0871e-06 | 0.12108 | 0.12108 | 0.12108 | 0.9822 | -0.34119 | 0.98218 | -0.34165 | 11.0883
126 | 0.015488 | 0.0038835 | -0.015484 | -0.0038815 | 3.4117e-06 | 1.97e-06 | 0.023342 | 0.023342 | 0.023342 | 0.98733 | -0.24193 | 0.98709 | -0.24655 | 6.4127
127 | 0.011852 | 0.0029713 | -0.01185 | -0.0029702 | 2.0121e-06 | 1.0729e-06 | 0.017867 | 0.017867 | 0.017867 | 0.98709 | -0.24655 | 0.98691 | -0.25012 | 4.9086
128 | 0.0095925 | 0.0024043 | -0.0095917 | -0.002404 | 7.1294e-07 | 3.4016e-07 | 0.014463 | 0.014463 | 0.014463 | 0.98691 | -0.25012 | 0.98683 | -0.25168 | 3.9734
129 | 0.0073854 | 0.001851 | -0.0073846 | -0.0018508 | 7.5578e-07 | 2.761e-07 | 0.011136 | 0.011136 | 0.011136 | 0.98683 | -0.25168 | 0.98672 | -0.25383 | 3.0594
130 | 0.0024917 | 0.00062441 | -0.0024917 | -0.00062447 | 3.4643e-08 | -6.1121e-08 | 0.0037607 | 0.0037607 | 0.0037607 | 0.9859 | -0.26957 | 0.98588 | -0.26986 | 1.0332
131 | -0.022393 | -0.0056145 | 0.022399 | 0.005618 | 5.6781e-06 | 3.4628e-06 | 0.033691 | 0.033691 | 0.033691 | 0.98906 | -0.20888 | 0.98933 | -0.20356 | 9.2558
132 | -0.02847 | -0.0071394 | 0.028477 | 0.0071443 | 7.8612e-06 | 4.8843e-06 | 0.042822 | 0.042822 | 0.042822 | 0.98933 | -0.20356 | 0.98963 | -0.19777 | 11.7642

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37517 | 0.095911

## res_load
| p_mw | q_mvar
0 | 0.0024869 | 0.00062327
1 | 0.00085818 | 0.00021508
2 | 0.00035465 | 8.8885e-05
3 | 0.0017129 | 0.00042929
4 | 0.0018364 | 0.00046023
5 | 0.0017587 | 0.00044076
6 | 0.011808 | 0.0029594
7 | 0.0016346 | 0.00040968
8 | 0.0014586 | 0.00036556
9 | 0.02491 | 0.006243
10 | 0.0076938 | 0.0019282
11 | 0.0036565 | 0.00091639
12 | 0.0034342 | 0.00086068
13 | 0.0019248 | 0.00048239
14 | 0.0073936 | 0.001853
15 | 0.00093557 | 0.00023448
16 | 0.0011394 | 0.00028556
17 | 0.00077806 | 0.000195
18 | 0.00072092 | 0.00018068
19 | 0.001332 | 0.00033383
20 | 0.0014743 | 0.0003695
21 | 0.0020983 | 0.00052588
22 | 0.00091566 | 0.00022949
23 | 0.002213 | 0.00055462
24 | 0.0038513 | 0.00096522
25 | 0.002672 | 0.00066966
26 | 0.003567 | 0.00089398
27 | 0.0031143 | 0.00078053
28 | 0.00090691 | 0.00022729
29 | 0.0023423 | 0.00058703
30 | 0.0053873 | 0.0013502
31 | 0.0043433 | 0.0010885
32 | 0.0020715 | 0.00051917
33 | 0.0059399 | 0.0014887
34 | 0.0021971 | 0.00055066
35 | 0.0021732 | 0.00054465
36 | 0.0078462 | 0.0019664
37 | 0.0064752 | 0.0016228
38 | 0.0096221 | 0.0024115
39 | 0.0017435 | 0.00043696
40 | 0.002856 | 0.00071578
41 | 0.0034308 | 0.00085983
42 | 0.0026677 | 0.00066858
43 | 0.0017562 | 0.00044016
44 | 0.0070329 | 0.0017626
45 | 0.0087234 | 0.0021863
46 | 0.0018764 | 0.00047026
47 | 0.0088803 | 0.0022256
48 | 0.0034752 | 0.00087097
49 | 0.003465 | 0.00086842
50 | 0.0032872 | 0.00082385
51 | 0.005682 | 0.001424
52 | 0.0019351 | 0.00048498
53 | 0.00094718 | 0.00023739
54 | 0.00087278 | 0.00021874
55 | 0.0014487 | 0.00036307
56 | 0.0054277 | 0.0013603
57 | 0.0057751 | 0.0014474
58 | 0.0030875 | 0.00077379
59 | 0.0041617 | 0.001043
60 | 0.0023463 | 0.00058805
61 | 0.0030203 | 0.00075695
62 | 0.0031005 | 0.00077706
63 | 0.0014745 | 0.00036954
64 | 0.0038614 | 0.00096775
65 | 0.001359 | 0.0003406
66 | 0.0022357 | 0.00056032
67 | 0.002529 | 0.00063383
68 | 0.0028553 | 0.0007156
69 | 0.0023106 | 0.00057909
70 | 0.0021604 | 0.00054145
71 | 0.0017115 | 0.00042894
72 | 0.0018262 | 0.00045768
73 | 0.0016074 | 0.00040285
74 | 0.0022458 | 0.00056285
75 | 0.0016443 | 0.00041211
76 | 0.0018288 | 0.00045833
77 | 0.0024918 | 0.00062451
78 | 0.0026411 | 0.00066191
79 | 0.0030248 | 0.00075808
80 | 0.0027497 | 0.00068913
81 | 0.0032301 | 0.00080955
82 | 0.0038385 | 0.00096201
83 | 0.0027052 | 0.00067798
84 | 0.0025148 | 0.00063026
85 | 0.0047245 | 0.0011841
86 | 0.0016845 | 0.00042217
87 | 0.0033418 | 0.00083752
88 | 0.0037213 | 0.00093265
89 | 0.0044173 | 0.0011071
90 | 0.0032665 | 0.00081866
91 | 0.0032013 | 0.00080231
92 | 0.0035279 | 0.00088416
93 | 0.0028413 | 0.00071209
94 | 0.0020591 | 0.00051607
95 | 0.0033412 | 0.00083737
96 | 0.0025938 | 0.00065006
97 | 0.0012026 | 0.00030141
98 | 0.0013071 | 0.0003276
99 | 0.0023487 | 0.00058865
100 | 0.0011326 | 0.00028386
101 | 0.0030913 | 0.00077476
102 | 0.003632 | 0.00091026
103 | 0.0022577 | 0.00056583
104 | 0.0022064 | 0.00055296
105 | 0.0073846 | 0.0018508
106 | 0.0032012 | 0.0008023
107 | 0.0024917 | 0.00062447
108 | 0.0029414 | 0.00073718
109 | 0.0060707 | 0.0015215
110 | 0.0026038 | 0.00065258

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1