## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1707-26_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1707-26_0_5_node_143 | 0.4 | n |  | TRUE
2 | bus_LV_1707-26_0_5_node_141 | 0.4 | n |  | TRUE
3 | bus_LV_1707-26_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1707-26_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1707-26_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1707-26_0_5_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_1707-26_0_5_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1707-26_0_5_node_82 | 0.4 | n |  | TRUE
9 | bus_LV_1707-26_0_5_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1707-26_0_5_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1707-26_0_5_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1707-26_0_5_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1707-26_0_5_node_88 | 0.4 | n |  | TRUE
14 | bus_LV_1707-26_0_5_node_87 | 0.4 | n |  | TRUE
15 | bus_LV_1707-26_0_5_node_90 | 0.4 | n |  | TRUE
16 | bus_LV_1707-26_0_5_node_5 | 0.4 | n |  | TRUE
17 | bus_LV_1707-26_0_5_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_1707-26_0_5_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1707-26_0_5_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1707-26_0_5_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1707-26_0_5_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1707-26_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1707-26_0_5_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1707-26_0_5_node_53 | 0.4 | n |  | TRUE
25 | bus_LV_1707-26_0_5_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_1707-26_0_5_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1707-26_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1707-26_0_5_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_1707-26_0_5_node_59 | 0.4 | n |  | TRUE
30 | bus_LV_1707-26_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1707-26_0_5_node_49 | 0.4 | n |  | TRUE
32 | bus_LV_1707-26_0_5_node_58 | 0.4 | n |  | TRUE
33 | bus_LV_1707-26_0_5_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1707-26_0_5_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_1707-26_0_5_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1707-26_0_5_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_1707-26_0_5_node_60 | 0.4 | n |  | TRUE
38 | bus_LV_1707-26_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1707-26_0_5_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1707-26_0_5_node_57 | 0.4 | n |  | TRUE
41 | bus_LV_1707-26_0_5_node_89 | 0.4 | n |  | TRUE
42 | bus_LV_1707-26_0_5_node_102 | 0.4 | n |  | TRUE
43 | bus_LV_1707-26_0_5_node_101 | 0.4 | n |  | TRUE
44 | bus_LV_1707-26_0_5_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_1707-26_0_5_node_97 | 0.4 | n |  | TRUE
46 | bus_LV_1707-26_0_5_node_110 | 0.4 | n |  | TRUE
47 | bus_LV_1707-26_0_5_node_54 | 0.4 | n |  | TRUE
48 | bus_LV_1707-26_0_5_node_55 | 0.4 | n |  | TRUE
49 | bus_LV_1707-26_0_5_node_113 | 0.4 | n |  | TRUE
50 | bus_LV_1707-26_0_5_node_127 | 0.4 | n |  | TRUE
51 | bus_LV_1707-26_0_5_node_124 | 0.4 | n |  | TRUE
52 | bus_LV_1707-26_0_5_node_73 | 0.4 | n |  | TRUE
53 | bus_LV_1707-26_0_5_node_153 | 0.4 | n |  | TRUE
54 | bus_LV_1707-26_0_5_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_1707-26_0_5_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_1707-26_0_5_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_1707-26_0_5_node_27 | 0.4 | n |  | TRUE
58 | bus_LV_1707-26_0_5_node_91 | 0.4 | n |  | TRUE
59 | bus_LV_1707-26_0_5_node_77 | 0.4 | n |  | TRUE
60 | bus_LV_1707-26_0_5_node_144 | 0.4 | n |  | TRUE
61 | bus_LV_1707-26_0_5_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_1707-26_0_5_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_1707-26_0_5_node_29 | 0.4 | n |  | TRUE
64 | bus_LV_1707-26_0_5_node_30 | 0.4 | n |  | TRUE
65 | bus_LV_1707-26_0_5_node_31 | 0.4 | n |  | TRUE
66 | bus_LV_1707-26_0_5_node_32 | 0.4 | n |  | TRUE
67 | bus_LV_1707-26_0_5_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_1707-26_0_5_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_1707-26_0_5_node_148 | 0.4 | n |  | TRUE
70 | bus_LV_1707-26_0_5_node_149 | 0.4 | n |  | TRUE
71 | bus_LV_1707-26_0_5_node_45 | 0.4 | n |  | TRUE
72 | bus_LV_1707-26_0_5_node_42 | 0.4 | n |  | TRUE
73 | bus_LV_1707-26_0_5_node_38 | 0.4 | n |  | TRUE
74 | bus_LV_1707-26_0_5_node_142 | 0.4 | n |  | TRUE
75 | bus_LV_1707-26_0_5_node_35 | 0.4 | n |  | TRUE
76 | bus_LV_1707-26_0_5_node_36 | 0.4 | n |  | TRUE
77 | bus_LV_1707-26_0_5_node_40 | 0.4 | n |  | TRUE
78 | bus_LV_1707-26_0_5_node_51 | 0.4 | n |  | TRUE
79 | bus_LV_1707-26_0_5_node_39 | 0.4 | n |  | TRUE
80 | bus_LV_1707-26_0_5_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_1707-26_0_5_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_1707-26_0_5_node_145 | 0.4 | n |  | TRUE
83 | bus_LV_1707-26_0_5_node_44 | 0.4 | n |  | TRUE
84 | bus_LV_1707-26_0_5_node_46 | 0.4 | n |  | TRUE
85 | bus_LV_1707-26_0_5_node_47 | 0.4 | n |  | TRUE
86 | bus_LV_1707-26_0_5_node_150 | 0.4 | n |  | TRUE
87 | bus_LV_1707-26_0_5_node_64 | 0.4 | n |  | TRUE
88 | bus_LV_1707-26_0_5_node_112 | 0.4 | n |  | TRUE
89 | bus_LV_1707-26_0_5_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_1707-26_0_5_node_114 | 0.4 | n |  | TRUE
91 | bus_LV_1707-26_0_5_node_109 | 0.4 | n |  | TRUE
92 | bus_LV_1707-26_0_5_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_1707-26_0_5_node_62 | 0.4 | n |  | TRUE
94 | bus_LV_1707-26_0_5_node_63 | 0.4 | n |  | TRUE
95 | bus_LV_1707-26_0_5_node_65 | 0.4 | n |  | TRUE
96 | bus_LV_1707-26_0_5_node_68 | 0.4 | n |  | TRUE
97 | bus_LV_1707-26_0_5_node_69 | 0.4 | n |  | TRUE
98 | bus_LV_1707-26_0_5_node_75 | 0.4 | n |  | TRUE
99 | bus_LV_1707-26_0_5_node_151 | 0.4 | n |  | TRUE
100 | bus_LV_1707-26_0_5_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_1707-26_0_5_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_1707-26_0_5_node_129 | 0.4 | n |  | TRUE
103 | bus_LV_1707-26_0_5_node_134 | 0.4 | n |  | TRUE
104 | bus_LV_1707-26_0_5_node_131 | 0.4 | n |  | TRUE
105 | bus_LV_1707-26_0_5_node_147 | 0.4 | n |  | TRUE
106 | bus_LV_1707-26_0_5_node_152 | 0.4 | n |  | TRUE
107 | bus_LV_1707-26_0_5_node_78 | 0.4 | n |  | TRUE
108 | bus_LV_1707-26_0_5_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_1707-26_0_5_node_81 | 0.4 | n |  | TRUE
110 | bus_LV_1707-26_0_5_node_84 | 0.4 | n |  | TRUE
111 | bus_LV_1707-26_0_5_node_83 | 0.4 | n |  | TRUE
112 | bus_LV_1707-26_0_5_node_85 | 0.4 | n |  | TRUE
113 | bus_LV_1707-26_0_5_node_86 | 0.4 | n |  | TRUE
114 | bus_LV_1707-26_0_5_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_1707-26_0_5_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_1707-26_0_5_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_1707-26_0_5_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_1707-26_0_5_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_1707-26_0_5_node_94 | 0.4 | n |  | TRUE
120 | bus_LV_1707-26_0_5_node_98 | 0.4 | n |  | TRUE
121 | bus_LV_1707-26_0_5_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_1707-26_0_5_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_1707-26_0_5_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_1707-26_0_5_node_138 | 0.4 | n |  | TRUE
125 | bus_LV_1707-26_0_5_node_104 | 0.4 | n |  | TRUE
126 | bus_LV_1707-26_0_5_node_136 | 0.4 | n |  | TRUE
127 | bus_LV_1707-26_0_5_node_105 | 0.4 | n |  | TRUE
128 | bus_LV_1707-26_0_5_node_107 | 0.4 | n |  | TRUE
129 | bus_LV_1707-26_0_5_node_108 | 0.4 | n |  | TRUE
130 | bus_LV_1707-26_0_5_node_115 | 0.4 | n |  | TRUE
131 | bus_LV_1707-26_0_5_node_125 | 0.4 | n |  | TRUE
132 | bus_LV_1707-26_0_5_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_1707-26_0_5_node_126 | 0.4 | n |  | TRUE
134 | bus_LV_1707-26_0_5_node_122 | 0.4 | n |  | TRUE
135 | bus_LV_1707-26_0_5_node_119 | 0.4 | n |  | TRUE
136 | bus_LV_1707-26_0_5_node_116 | 0.4 | n |  | TRUE
137 | bus_LV_1707-26_0_5_node_117 | 0.4 | n |  | TRUE
138 | bus_LV_1707-26_0_5_node_118 | 0.4 | n |  | TRUE
139 | bus_LV_1707-26_0_5_node_120 | 0.4 | n |  | TRUE
140 | bus_LV_1707-26_0_5_node_121 | 0.4 | n |  | TRUE
141 | bus_LV_1707-26_0_5_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_1707-26_0_5_node_146 | 0.4 | n |  | TRUE
143 | bus_LV_1707-26_0_5_node_130 | 0.4 | n |  | TRUE
144 | bus_LV_1707-26_0_5_node_132 | 0.4 | n |  | TRUE
145 | bus_LV_1707-26_0_5_node_133 | 0.4 | n |  | TRUE
146 | bus_LV_1707-26_0_5_node_135 | 0.4 | n |  | TRUE
147 | bus_LV_1707-26_0_5_node_137 | 0.4 | n |  | TRUE
148 | bus_LV_1707-26_0_5_node_139 | 0.4 | n |  | TRUE
149 | bus_MV_232_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1707-26_0_5_load_0 | 0 | 0.017806 | 0.0044626 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1707-26_0_5_load_141 | 2 | 0.0015813 | 0.0003963 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1707-26_0_5_load_2 | 3 | 0.0045314 | 0.0011357 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1707-26_0_5_load_3 | 4 | 0.0029895 | 0.00074923 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1707-26_0_5_load_82 | 8 | 0.0019591 | 0.00049099 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1707-26_0_5_load_28 | 12 | 0.0039541 | 0.00099098 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1707-26_0_5_load_88 | 13 | 0.0026435 | 0.00066251 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1707-26_0_5_load_87 | 14 | 0.0025252 | 0.00063288 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1707-26_0_5_load_5 | 16 | 0.0066918 | 0.0016771 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1707-26_0_5_load_25 | 19 | 0.016025 | 0.0040162 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1707-26_0_5_load_11 | 22 | 0.063889 | 0.016012 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1707-26_0_5_load_52 | 25 | 0.006903 | 0.0017301 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1707-26_0_5_load_26 | 26 | 0.013878 | 0.0034782 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1707-26_0_5_load_61 | 28 | 0.0037306 | 0.00093498 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1707-26_0_5_load_59 | 29 | 0.0024951 | 0.00062534 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1707-26_0_5_load_58 | 32 | 0.016732 | 0.0041935 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1707-26_0_5_load_60 | 37 | 0.0067044 | 0.0016803 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1707-26_0_5_load_34 | 39 | 0.0024695 | 0.00061892 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1707-26_0_5_load_57 | 40 | 0.002216 | 0.00055539 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1707-26_0_5_load_102 | 42 | 0.012094 | 0.003031 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1707-26_0_5_load_101 | 43 | 0.011271 | 0.0028248 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1707-26_0_5_load_80 | 44 | 0.0028931 | 0.00072508 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1707-26_0_5_load_97 | 45 | 0.001681 | 0.00042129 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1707-26_0_5_load_110 | 46 | 0.0012442 | 0.00031182 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1707-26_0_5_load_127 | 50 | 0.0043156 | 0.0010816 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1707-26_0_5_load_124 | 51 | 0.00091149 | 0.00022844 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1707-26_0_5_load_153 | 53 | 0.0021743 | 0.00054494 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1707-26_0_5_load_33 | 55 | 0.0027222 | 0.00068224 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1707-26_0_5_load_56 | 56 | 0.0027641 | 0.00069274 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1707-26_0_5_load_91 | 58 | 0.0038304 | 0.00096 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1707-26_0_5_load_144 | 60 | 0.027762 | 0.0069579 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1707-26_0_5_load_71 | 62 | 0.020876 | 0.005232 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1707-26_0_5_load_29 | 63 | 0.010089 | 0.0025284 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1707-26_0_5_load_50 | 68 | 0.0050844 | 0.0012743 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1707-26_0_5_load_148 | 69 | 0.0092125 | 0.0023089 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1707-26_0_5_load_149 | 70 | 0.0096924 | 0.0024291 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1707-26_0_5_load_45 | 71 | 0.006515 | 0.0016328 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1707-26_0_5_load_42 | 72 | 0.0071644 | 0.0017956 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1707-26_0_5_load_35 | 75 | 0.0057446 | 0.0014397 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1707-26_0_5_load_40 | 77 | 0.006898 | 0.0017288 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1707-26_0_5_load_66 | 81 | 0.0038265 | 0.00095901 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1707-26_0_5_load_145 | 82 | 0.026933 | 0.0067501 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1707-26_0_5_load_46 | 84 | 0.00981 | 0.0024586 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1707-26_0_5_load_47 | 85 | 0.0086513 | 0.0021682 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1707-26_0_5_load_150 | 86 | 0.012082 | 0.003028 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1707-26_0_5_load_112 | 88 | 0.003706 | 0.00092881 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1707-26_0_5_load_109 | 91 | 0.005958 | 0.0014932 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1707-26_0_5_load_62 | 93 | 0.002183 | 0.00054711 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1707-26_0_5_load_63 | 94 | 0.0014025 | 0.00035151 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1707-26_0_5_load_65 | 95 | 0.0024847 | 0.00062273 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1707-26_0_5_load_68 | 96 | 0.0041359 | 0.0010366 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1707-26_0_5_load_69 | 97 | 0.0030354 | 0.00076074 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1707-26_0_5_load_151 | 99 | 0.014465 | 0.0036254 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1707-26_0_5_load_134 | 103 | 0.00021808 | 5.4655e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1707-26_0_5_load_131 | 104 | 0.00028766 | 7.2095e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1707-26_0_5_load_147 | 105 | 0.01476 | 0.0036992 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1707-26_0_5_load_152 | 106 | 0.013839 | 0.0034684 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1707-26_0_5_load_78 | 107 | 0.0025959 | 0.0006506 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1707-26_0_5_load_79 | 108 | 0.0016724 | 0.00041914 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1707-26_0_5_load_81 | 109 | 0.0077202 | 0.0019349 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1707-26_0_5_load_84 | 110 | 0.001676 | 0.00042003 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1707-26_0_5_load_83 | 111 | 0.001676 | 0.00042003 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1707-26_0_5_load_85 | 112 | 0.001676 | 0.00042003 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1707-26_0_5_load_86 | 113 | 0.0058592 | 0.0014685 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1707-26_0_5_load_95 | 115 | 0.0055341 | 0.001387 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1707-26_0_5_load_96 | 116 | 0.0042767 | 0.0010718 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1707-26_0_5_load_92 | 117 | 0.0026422 | 0.00066221 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1707-26_0_5_load_93 | 118 | 0.01032 | 0.0025864 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1707-26_0_5_load_94 | 119 | 0.0026422 | 0.00066221 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1707-26_0_5_load_103 | 122 | 0.0034782 | 0.00087172 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1707-26_0_5_load_106 | 123 | 0.0073514 | 0.0018424 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1707-26_0_5_load_138 | 124 | 0.0021914 | 0.00054922 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1707-26_0_5_load_104 | 125 | 0.013019 | 0.0032629 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1707-26_0_5_load_136 | 126 | 0.00088813 | 0.00022259 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1707-26_0_5_load_105 | 127 | 0.015763 | 0.0039506 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1707-26_0_5_load_107 | 128 | 0.011812 | 0.0029604 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1707-26_0_5_load_108 | 129 | 0.0026113 | 0.00065446 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1707-26_0_5_load_125 | 131 | 0.002926 | 0.00073332 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1707-26_0_5_load_123 | 132 | 0.0021947 | 0.00055003 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1707-26_0_5_load_122 | 134 | 0.00091746 | 0.00022994 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1707-26_0_5_load_119 | 135 | 0.0011693 | 0.00029304 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1707-26_0_5_load_116 | 136 | 0.0010008 | 0.00025082 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1707-26_0_5_load_117 | 137 | 0.0021008 | 0.00052651 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1707-26_0_5_load_120 | 139 | 0.0017412 | 0.0004364 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1707-26_0_5_load_128 | 141 | 0.0013511 | 0.00033861 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1707-26_0_5_load_146 | 142 | 0.0045254 | 0.0011342 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1707-26_0_5_load_130 | 143 | 0.0011049 | 0.00027691 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1707-26_0_5_load_132 | 144 | 0.00068042 | 0.00017053 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1707-26_0_5_load_133 | 145 | 0.0022222 | 0.00055694 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1707-26_0_5_load_135 | 146 | 0.00065597 | 0.0001644 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1707-26_0_5_load_137 | 147 | 0.0033979 | 0.0008516 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1707-26_0_5_load_139 | 148 | 0.00045454 | 0.00011392 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1707-26_0_5_line_0 |  | 0 | 1 | 0.23606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1707-26_0_5_line_1 |  | 1 | 2 | 0.034062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1707-26_0_5_line_2 |  | 2 | 74 | 0.022355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1707-26_0_5_line_3 |  | 3 | 4 | 0.10314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1707-26_0_5_line_4 |  | 4 | 5 | 0.070665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1707-26_0_5_line_5 |  | 5 | 6 | 0.040361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1707-26_0_5_line_6 |  | 6 | 13 | 0.042657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1707-26_0_5_line_7 |  | 6 | 14 | 0.0067364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1707-26_0_5_line_8 |  | 7 | 8 | 0.012659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1707-26_0_5_line_9 |  | 7 | 9 | 0.008787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1707-26_0_5_line_10 |  | 8 | 44 | 0.017638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1707-26_0_5_line_11 |  | 9 | 19 | 0.013797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1707-26_0_5_line_12 |  | 9 | 17 | 0.032513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1707-26_0_5_line_13 |  | 10 | 11 | 0.026076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1707-26_0_5_line_14 |  | 10 | 12 | 0.012587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_1707-26_0_5_line_15 |  | 11 | 15 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1707-26_0_5_line_16 |  | 11 | 14 | 0.02556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1707-26_0_5_line_17 |  | 12 | 18 | 0.018803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1707-26_0_5_line_18 |  | 15 | 45 | 0.032878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1707-26_0_5_line_19 |  | 15 | 46 | 0.013141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1707-26_0_5_line_20 |  | 16 | 17 | 0.015102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1707-26_0_5_line_21 |  | 17 | 18 | 0.015107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_1707-26_0_5_line_22 |  | 19 | 26 | 0.0099784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_1707-26_0_5_line_23 |  | 20 | 21 | 0.030007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1707-26_0_5_line_24 |  | 20 | 22 | 0.023149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1707-26_0_5_line_25 |  | 21 | 25 | 0.011935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1707-26_0_5_line_26 |  | 23 | 24 | 0.00664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1707-26_0_5_line_27 |  | 23 | 25 | 0.006057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1707-26_0_5_line_28 |  | 24 | 47 | 0.04181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1707-26_0_5_line_29 |  | 26 | 57 | 0.016793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1707-26_0_5_line_30 |  | 27 | 28 | 0.0096271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1707-26_0_5_line_31 |  | 27 | 29 | 0.0088627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1707-26_0_5_line_32 |  | 28 | 52 | 0.016821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1707-26_0_5_line_33 |  | 29 | 34 | 0.018029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1707-26_0_5_line_34 |  | 30 | 31 | 0.025337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1707-26_0_5_line_35 |  | 30 | 32 | 0.02135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1707-26_0_5_line_36 |  | 31 | 37 | 0.018948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1707-26_0_5_line_37 |  | 32 | 33 | 0.015397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1707-26_0_5_line_38 |  | 33 | 34 | 0.018062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1707-26_0_5_line_39 |  | 34 | 38 | 0.025782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1707-26_0_5_line_40 |  | 34 | 39 | 0.0089293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1707-26_0_5_line_41 |  | 35 | 36 | 0.007196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1707-26_0_5_line_42 |  | 35 | 37 | 0.016445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1707-26_0_5_line_43 |  | 36 | 53 | 0.01148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1707-26_0_5_line_44 |  | 36 | 54 | 0.023546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1707-26_0_5_line_45 |  | 38 | 40 | 0.0090954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1707-26_0_5_line_46 |  | 39 | 55 | 0.00011399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1707-26_0_5_line_47 |  | 40 | 56 | 0.00013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1707-26_0_5_line_48 |  | 41 | 42 | 0.027457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1707-26_0_5_line_49 |  | 41 | 43 | 0.020253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1707-26_0_5_line_50 |  | 42 | 114 | 0.017207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1707-26_0_5_line_51 |  | 43 | 115 | 0.024916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1707-26_0_5_line_52 |  | 44 | 107 | 0.00053559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1707-26_0_5_line_53 |  | 45 | 116 | 0.024158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_1707-26_0_5_line_54 |  | 46 | 89 | 0.018726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1707-26_0_5_line_55 |  | 47 | 48 | 0.032434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1707-26_0_5_line_56 |  | 47 | 49 | 0.022312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_1707-26_0_5_line_57 |  | 47 | 50 | 0.027483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1707-26_0_5_line_58 |  | 48 | 51 | 0.069105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1707-26_0_5_line_59 |  | 49 | 90 | 0.059162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1707-26_0_5_line_60 |  | 49 | 91 | 0.013884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1707-26_0_5_line_61 |  | 52 | 92 | 0.018952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1707-26_0_5_line_62 |  | 54 | 77 | 0.019754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1707-26_0_5_line_63 |  | 54 | 75 | 0.020191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1707-26_0_5_line_64 |  | 57 | 58 | 0.03469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1707-26_0_5_line_65 |  | 57 | 59 | 0.012451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_1707-26_0_5_line_66 |  | 58 | 60 | 0.0050822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_1707-26_0_5_line_67 |  | 59 | 61 | 0.035229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_1707-26_0_5_line_68 |  | 59 | 62 | 0.028009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1707-26_0_5_line_69 |  | 61 | 82 | 0.014059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1707-26_0_5_line_70 |  | 61 | 79 | 0.035884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_1707-26_0_5_line_71 |  | 63 | 64 | 0.014677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1707-26_0_5_line_72 |  | 64 | 65 | 0.027603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1707-26_0_5_line_73 |  | 64 | 66 | 0.011016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1707-26_0_5_line_74 |  | 65 | 67 | 0.013972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1707-26_0_5_line_75 |  | 65 | 68 | 0.027444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1707-26_0_5_line_76 |  | 66 | 69 | 0.012966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1707-26_0_5_line_77 |  | 66 | 70 | 0.011094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1707-26_0_5_line_78 |  | 67 | 71 | 0.014895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1707-26_0_5_line_79 |  | 67 | 72 | 0.017258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1707-26_0_5_line_80 |  | 68 | 73 | 0.037771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1707-26_0_5_line_81 |  | 70 | 74 | 0.23654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1707-26_0_5_line_82 |  | 72 | 83 | 0.01016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1707-26_0_5_line_83 |  | 73 | 78 | 0.03619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1707-26_0_5_line_84 |  | 73 | 76 | 0.001947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1707-26_0_5_line_85 |  | 75 | 76 | 0.012367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1707-26_0_5_line_86 |  | 77 | 79 | 0.015747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_1707-26_0_5_line_87 |  | 78 | 80 | 0.028101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1707-26_0_5_line_88 |  | 78 | 81 | 0.017747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1707-26_0_5_line_89 |  | 80 | 86 | 0.003464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1707-26_0_5_line_90 |  | 81 | 87 | 0.023227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1707-26_0_5_line_91 |  | 83 | 84 | 0.010321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1707-26_0_5_line_92 |  | 83 | 85 | 0.03413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1707-26_0_5_line_93 |  | 87 | 93 | 0.0036323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1707-26_0_5_line_94 |  | 88 | 89 | 0.024115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1707-26_0_5_line_95 |  | 90 | 130 | 0.035314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1707-26_0_5_line_96 |  | 90 | 131 | 0.018797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1707-26_0_5_line_97 |  | 91 | 129 | 0.019256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_1707-26_0_5_line_98 |  | 92 | 100 | 0.024959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1707-26_0_5_line_99 |  | 92 | 105 | 0.002499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1707-26_0_5_line_100 |  | 93 | 94 | 0.02149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1707-26_0_5_line_101 |  | 94 | 95 | 0.0009891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1707-26_0_5_line_102 |  | 95 | 96 | 0.031016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1707-26_0_5_line_103 |  | 96 | 97 | 0.024688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1707-26_0_5_line_104 |  | 97 | 101 | 0.097894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1707-26_0_5_line_105 |  | 98 | 99 | 0.008362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1707-26_0_5_line_106 |  | 98 | 100 | 0.038634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1707-26_0_5_line_107 |  | 100 | 106 | 0.005328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1707-26_0_5_line_108 |  | 101 | 102 | 0.055205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1707-26_0_5_line_109 |  | 102 | 103 | 0.015415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1707-26_0_5_line_110 |  | 102 | 104 | 0.055749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1707-26_0_5_line_111 |  | 104 | 143 | 0.015424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1707-26_0_5_line_112 |  | 107 | 108 | 0.0087372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1707-26_0_5_line_113 |  | 108 | 109 | 0.0060358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1707-26_0_5_line_114 |  | 109 | 110 | 0.00014012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1707-26_0_5_line_115 |  | 110 | 111 | 0.0061806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1707-26_0_5_line_116 |  | 111 | 112 | 0.0061818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1707-26_0_5_line_117 |  | 112 | 113 | 0.0029986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1707-26_0_5_line_118 |  | 114 | 122 | 0.051712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1707-26_0_5_line_119 |  | 114 | 120 | 0.059539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1707-26_0_5_line_120 |  | 115 | 118 | 0.0056389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1707-26_0_5_line_121 |  | 116 | 120 | 0.030346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_1707-26_0_5_line_122 |  | 117 | 118 | 0.0086952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1707-26_0_5_line_123 |  | 117 | 119 | 0.001123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1707-26_0_5_line_124 |  | 120 | 121 | 0.044505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_1707-26_0_5_line_125 |  | 121 | 123 | 0.035821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_1707-26_0_5_line_126 |  | 122 | 124 | 0.077898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1707-26_0_5_line_127 |  | 123 | 125 | 0.046033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_1707-26_0_5_line_128 |  | 124 | 126 | 0.02777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1707-26_0_5_line_129 |  | 125 | 127 | 0.013473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_1707-26_0_5_line_130 |  | 126 | 146 | 0.0022243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1707-26_0_5_line_131 |  | 127 | 128 | 0.029654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_1707-26_0_5_line_132 |  | 128 | 129 | 0.013849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_1707-26_0_5_line_133 |  | 130 | 132 | 0.02956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1707-26_0_5_line_134 |  | 131 | 133 | 0.012772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1707-26_0_5_line_135 |  | 133 | 140 | 0.010478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1707-26_0_5_line_136 |  | 134 | 135 | 0.010306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1707-26_0_5_line_137 |  | 135 | 137 | 0.012171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1707-26_0_5_line_138 |  | 136 | 137 | 0.013956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1707-26_0_5_line_139 |  | 136 | 138 | 0.012976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1707-26_0_5_line_140 |  | 138 | 139 | 0.023497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1707-26_0_5_line_141 |  | 138 | 140 | 0.024584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1707-26_0_5_line_142 |  | 139 | 141 | 0.020909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1707-26_0_5_line_143 |  | 140 | 142 | 0.008556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1707-26_0_5_line_144 |  | 143 | 144 | 0.028048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1707-26_0_5_line_145 |  | 144 | 145 | 0.050698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1707-26_0_5_line_146 |  | 146 | 147 | 0.021672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1707-26_0_5_line_147 |  | 147 | 148 | 0.028363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1707-26_0_5_trafo_144 | 0.63 MVA 20/0.4 kV | 149 | 60 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2676296.4561 | 1223031.8247 | 2676303.1387 | 1223267.7884
1 | 2676296.4561 | 1223031.8247 | 2676297.6278 | 1223029.1713 | 2676298.3209 | 1223023.6209 | 2676298.9638 | 1223021.3944 | 2676300.5309 | 1223018.0678 | 2676300.1813 | 1223013.3936 | 2676298.8075 | 1223009.3288 | 2676292.9288 | 1223000.5144
2 | 2676278.4062 | 1222983.8062 | 2676284.2284 | 1222988.7507 | 2676288.666 | 1222993.4329 | 2676292.9288 | 1223000.5144
3 | 2676046.2862 | 1223327.2864 | 2676036.6989 | 1223315.9122 | 2675997.1997 | 1223269.6885 | 2675979.7916 | 1223249.0861 | 2675979.4647 | 1223248.7177
4 | 2675932.8529 | 1223195.6077 | 2675954.887 | 1223221.0166 | 2675979.4647 | 1223248.7177
5 | 2675897.9832 | 1223198.3761 | 2675905.0791 | 1223201.5798 | 2675912.8869 | 1223206.0489 | 2675917.2222 | 1223202.7131 | 2675922.1588 | 1223200.986 | 2675927.4837 | 1223200.9205 | 2675932.8529 | 1223195.6077
6 | 2675897.9832 | 1223198.3761 | 2675896.8644 | 1223202.8426 | 2675879.8973 | 1223236.9032
7 | 2675897.9832 | 1223198.3761 | 2675898.3646 | 1223191.6505
8 | 2675943.557 | 1223124.0747 | 2675953.0468 | 1223129.2881 | 2675954.0594 | 1223130.8141
9 | 2675943.557 | 1223124.0747 | 2675947.1407 | 1223116.0485
10 | 2675955.6414 | 1223148.0862 | 2675955.7882 | 1223135.5494 | 2675954.8922 | 1223132.069 | 2675954.0594 | 1223130.8141
11 | 2675947.1407 | 1223116.0485 | 2675951.7475 | 1223103.0434
12 | 2675916.9718 | 1223112.3503 | 2675920.619 | 1223117.1777 | 2675921.8028 | 1223117.1261 | 2675926.8935 | 1223117.002 | 2675933.1542 | 1223116.715 | 2675940.5148 | 1223116.4198 | 2675947.1407 | 1223116.0485
13 | 2675898.089 | 1223166.2896 | 2675904.831 | 1223162.1617 | 2675913.9273 | 1223156.5962 | 2675909.8286 | 1223150.3065
14 | 2675909.8286 | 1223150.3065 | 2675910.6311 | 1223149.2271 | 2675909.701 | 1223138.0239
15 | 2675898.089 | 1223166.2896 | 2675894.2528 | 1223156.0673
16 | 2675898.089 | 1223166.2896 | 2675899.4802 | 1223171.9777 | 2675898.3646 | 1223191.6505
17 | 2675904.2692 | 1223120.5827 | 2675908.8561 | 1223127.8459 | 2675909.701 | 1223138.0239
18 | 2675894.2528 | 1223156.0673 | 2675889.7764 | 1223157.9782 | 2675877.0847 | 1223169.5352 | 2675869.6049 | 1223177.389
19 | 2675894.2528 | 1223156.0673 | 2675891.1296 | 1223149.4009 | 2675888.2368 | 1223144.3977
20 | 2675916.9718 | 1223112.3503 | 2675907.4018 | 1223100.667
21 | 2675916.9718 | 1223112.3503 | 2675904.2692 | 1223120.5827
22 | 2675951.7475 | 1223103.0434 | 2675954.1902 | 1223096.1475 | 2675954.8915 | 1223093.5788
23 | 2675829.3057 | 1223021.7625 | 2675834.3347 | 1223030.0542 | 2675838.7002 | 1223035.6579 | 2675841.1033 | 1223038.1346 | 2675844.3525 | 1223040.8667 | 2675846.2392 | 1223043.3924 | 2675848.2496 | 1223042.1616
24 | 2675848.2496 | 1223042.1616 | 2675860.2949 | 1223061.9296
25 | 2675829.3057 | 1223021.7625 | 2675823.286 | 1223011.4568
26 | 2675818.0444 | 1223014.4921 | 2675812.2833 | 1223017.8209
27 | 2675818.0444 | 1223014.4921 | 2675823.286 | 1223011.4568
28 | 2675788.5873 | 1222994.1593 | 2675796.1054 | 1222989.2517 | 2675800.755 | 1222997.5608 | 2675812.2833 | 1223017.8209
29 | 2675959.3141 | 1223077.3782 | 2675954.8915 | 1223093.5788
30 | 2675850.2777 | 1222977.0556 | 2675846.56 | 1222977.7532 | 2675845.6557 | 1222971.9791
31 | 2675850.2777 | 1222977.0556 | 2675856.9005 | 1222975.1498 | 2675858.7948 | 1222974.6051
32 | 2675843.0531 | 1222955.3604 | 2675845.6557 | 1222971.9791
33 | 2675876.1219 | 1222969.6244 | 2675873.0541 | 1222970.5081 | 2675870.2299 | 1222971.3171 | 2675858.7948 | 1222974.6051
34 | 2675923.3791 | 1223009.0193 | 2675899.5356 | 1223017.7767
35 | 2675899.5356 | 1223017.7767 | 2675892.0189 | 1223001.1589 | 2675890.7379 | 1222998.3232
36 | 2675923.3791 | 1223009.0193 | 2675919.5676 | 1222990.4588
37 | 2675884.3916 | 1222984.295 | 2675889.7102 | 1222996.0483 | 2675890.7379 | 1222998.3232
38 | 2675876.1219 | 1222969.6244 | 2675877.5683 | 1222969.2092 | 2675878.3649 | 1222970.9761 | 2675878.9698 | 1222972.3069 | 2675883.1671 | 1222981.5887 | 2675883.9859 | 1222983.4003 | 2675884.3916 | 1222984.295
39 | 2675876.1219 | 1222969.6244 | 2675877.5683 | 1222969.2092 | 2675881.2679 | 1222968.1445 | 2675895.0769 | 1222964.1734 | 2675900.9004 | 1222962.5021
40 | 2675876.1219 | 1222969.6244 | 2675873.6368 | 1222961.0479
41 | 2675923.3882 | 1222973.2292 | 2675919.2995 | 1222973.8775 | 2675916.2597 | 1222974.3501
42 | 2675916.2597 | 1222974.3501 | 2675919.5676 | 1222990.4588
43 | 2675919.613 | 1222962.385 | 2675923.3882 | 1222973.2292
44 | 2675923.3882 | 1222973.2292 | 2675925.8429 | 1222972.8491 | 2675946.7262 | 1222969.6355
45 | 2675900.9004 | 1222962.5021 | 2675898.3712 | 1222953.7654
46 | 2675873.6051 | 1222960.9384 | 2675873.6368 | 1222961.0479
47 | 2675898.3345 | 1222953.6385 | 2675898.3712 | 1222953.7654
48 | 2675805.4899 | 1223276.6385 | 2675787.0916 | 1223256.258
49 | 2675805.4899 | 1223276.6385 | 2675819.9849 | 1223262.4937
50 | 2675777.5341 | 1223242.1488 | 2675781.3339 | 1223249.8801 | 2675787.0916 | 1223256.258
51 | 2675837.8174 | 1223245.0918 | 2675819.9849 | 1223262.4937
52 | 2675955.6351 | 1223148.6218 | 2675955.6414 | 1223148.0862
53 | 2675851.6198 | 1223193.3098 | 2675859.4042 | 1223188.1 | 2675869.6049 | 1223177.389
54 | 2675878.8633 | 1223128.1861 | 2675888.2368 | 1223144.3977
55 | 2675785.3505 | 1222968.4122 | 2675792.8054 | 1222983.3503 | 2675796.1054 | 1222989.2517 | 2675788.5873 | 1222994.1593
56 | 2675788.5873 | 1222994.1593 | 2675769.7682 | 1223006.2277
57 | 2675788.5873 | 1222994.1593 | 2675774.0593 | 1222970.8305
58 | 2675785.3505 | 1222968.4122 | 2675750.1361 | 1222908.9527
59 | 2675725.806 | 1222974.8368 | 2675733.3092 | 1222975.2658 | 2675750.0109 | 1222977.602 | 2675769.7682 | 1223006.2277
60 | 2675769.7682 | 1223006.2277 | 2675776.308 | 1223018.4754
61 | 2675833.3883 | 1222940.6387 | 2675834.7635 | 1222947.0049 | 2675836.8532 | 1222951.4567 | 2675841.5302 | 1222955.2298 | 2675843.0531 | 1222955.3604
62 | 2675946.7262 | 1222969.6355 | 2675947.7108 | 1222989.3648
63 | 2675946.7262 | 1222969.6355 | 2675945.726 | 1222949.4695
64 | 2675959.3141 | 1223077.3782 | 2675950.2699 | 1223077.6631 | 2675935.8611 | 1223078.1352 | 2675924.6419 | 1223078.5023
65 | 2675959.3141 | 1223077.3782 | 2675960.625 | 1223064.9979
66 | 2675922.1852 | 1223074.0692 | 2675924.6163 | 1223078.5032 | 2675924.6419 | 1223078.5023
67 | 2675960.0885 | 1223029.7789 | 2675960.625 | 1223064.9979
68 | 2675960.625 | 1223064.9979 | 2675980.1628 | 1223066.159 | 2675987.8264 | 1223062.6315
69 | 2675960.0885 | 1223029.7789 | 2675945.9922 | 1223030.1216
70 | 2675958.6121 | 1222993.9253 | 2675959.3182 | 1223011.1012 | 2675960.0885 | 1223029.7789
71 | 2676024.8972 | 1222969.266 | 2676024.8596 | 1222954.5893
72 | 2676024.8972 | 1222969.266 | 2675997.2369 | 1222970.4137
73 | 2676024.8972 | 1222969.266 | 2676034.5366 | 1222974.6482
74 | 2675997.2369 | 1222970.4137 | 2675997.4756 | 1222984.3815
75 | 2675997.2369 | 1222970.4137 | 2675996.8188 | 1222945.5364 | 2675994.2558 | 1222945.5321
76 | 2676034.5366 | 1222974.6482 | 2676034.7883 | 1222982.2564 | 2676029.4297 | 1222982.566
77 | 2676042.214 | 1222970.9438 | 2676042.3464 | 1222974.2365 | 2676034.5366 | 1222974.6482
78 | 2675983.2725 | 1222982.9883 | 2675985.5004 | 1222984.918 | 2675997.4756 | 1222984.3815
79 | 2675997.4756 | 1222984.3815 | 2676002.1524 | 1222984.608 | 2676003.0326 | 1222997.153
80 | 2675956.4846 | 1222945.4996 | 2675967.9447 | 1222945.5124 | 2675989.7881 | 1222945.5245 | 2675994.2558 | 1222945.5321
81 | 2676042.214 | 1222970.9438 | 2676278.4062 | 1222983.8062
82 | 2676003.7437 | 1223007.2877 | 2676003.0326 | 1222997.153
83 | 2675956.4846 | 1222945.4996 | 2675956.0838 | 1222933.5199 | 2675955.8617 | 1222909.3233
84 | 2675956.4846 | 1222945.4996 | 2675956.5204 | 1222947.4458
85 | 2675956.5204 | 1222947.4458 | 2675945.6524 | 1222947.9853 | 2675945.726 | 1222949.4695
86 | 2675958.6121 | 1222993.9253 | 2675947.9644 | 1222994.4454 | 2675947.7108 | 1222989.3648
87 | 2675955.8617 | 1222909.3233 | 2675928.9876 | 1222917.7862
88 | 2675955.8617 | 1222909.3233 | 2675955.5691 | 1222891.5785
89 | 2675927.9452 | 1222914.4819 | 2675928.9876 | 1222917.7862
90 | 2675955.1862 | 1222868.3544 | 2675955.5691 | 1222891.5785
91 | 2676003.7437 | 1223007.2877 | 2676004.4693 | 1223017.5816
92 | 2676003.7437 | 1223007.2877 | 2676011.1894 | 1223009.84 | 2676015.7355 | 1223028.6104 | 2676018.0371 | 1223035.1637
93 | 2675955.1862 | 1222868.3544 | 2675954.9812 | 1222864.7278
94 | 2675878.8633 | 1223128.1861 | 2675868.9052 | 1223110.3252 | 2675867.0435 | 1223107.1677
95 | 2675744.8436 | 1222951.5635 | 2675741.7873 | 1222950.9465 | 2675740.1892 | 1222950.7705 | 2675738.5016 | 1222951.0714 | 2675726.1105 | 1222963.422 | 2675725.806 | 1222974.8368
96 | 2675725.806 | 1222974.8368 | 2675713.5733 | 1222974.1474 | 2675707.3225 | 1222972.2069
97 | 2675776.308 | 1223018.4754 | 2675785.378 | 1223035.4618
98 | 2675833.3883 | 1222940.6387 | 2675837.7899 | 1222939.2494 | 2675844.8491 | 1222937.0267 | 2675857.1933 | 1222933.137
99 | 2675830.9973 | 1222941.3866 | 2675833.3883 | 1222940.6387
100 | 2675954.9812 | 1222864.7278 | 2675953.7681 | 1222843.2724
101 | 2675953.7681 | 1222843.2724 | 2675953.7123 | 1222842.2849
102 | 2675953.7123 | 1222842.2849 | 2675953.0637 | 1222830.8137 | 2675952.7254 | 1222811.2899
103 | 2675952.7254 | 1222811.2899 | 2675952.6357 | 1222806.1141 | 2675955.3397 | 1222786.7914 | 2675955.3397 | 1222786.7914
104 | 2675972.5661 | 1222690.4254 | 2675971.8164 | 1222695.0856 | 2675955.3397 | 1222786.7914
105 | 2675891.5129 | 1222913.5613 | 2675894.0431 | 1222921.5321
106 | 2675857.1933 | 1222933.137 | 2675869.9792 | 1222929.1083 | 2675875.7439 | 1222927.2917 | 2675894.0431 | 1222921.5321
107 | 2675855.5819 | 1222928.0575 | 2675857.1933 | 1222933.137
108 | 2675922.4062 | 1222697.0457 | 2675926.2302 | 1222692.7916 | 2675930.7696 | 1222688.9359 | 2675939.4683 | 1222684.8663 | 2675949.3593 | 1222684.2476 | 2675972.5661 | 1222690.4254
109 | 2675922.4062 | 1222697.0457 | 2675909.3643 | 1222688.8277
110 | 2675922.4062 | 1222697.0457 | 2675915.3027 | 1222708.6628 | 2675911.0248 | 1222719.9602 | 2675909.6106 | 1222721.4209 | 2675883.8825 | 1222732.5173
111 | 2675869.7195 | 1222738.6258 | 2675883.8825 | 1222732.5173
112 | 2675955.6351 | 1223148.6218 | 2675955.5328 | 1223157.3583
113 | 2675955.5328 | 1223157.3583 | 2675955.4621 | 1223163.3937
114 | 2675955.4604 | 1223163.5339 | 2675955.4621 | 1223163.3937
115 | 2675955.388 | 1223169.714 | 2675955.4604 | 1223163.5339
116 | 2675955.388 | 1223169.714 | 2675955.3156 | 1223175.8954
117 | 2675955.2805 | 1223178.8938 | 2675955.3156 | 1223175.8954
118 | 2675777.5341 | 1223242.1488 | 2675769.4016 | 1223242.3232 | 2675757.5102 | 1223247.0417 | 2675732.1074 | 1223261.0167 | 2675730.5653 | 1223261.9277
119 | 2675825.2453 | 1223208.2893 | 2675792.0749 | 1223227.1128 | 2675781.0373 | 1223235.0554 | 2675777.5341 | 1223242.1488
120 | 2675837.8174 | 1223245.0918 | 2675841.8531 | 1223241.1535
121 | 2675825.2453 | 1223208.2893 | 2675847.8458 | 1223195.8356 | 2675851.6198 | 1223193.3098
122 | 2675848.0763 | 1223235.0807 | 2675841.8531 | 1223241.1535
123 | 2675848.88 | 1223234.2964 | 2675848.0763 | 1223235.0807
124 | 2675823.0632 | 1223166.4562 | 2675831.0549 | 1223189.2396 | 2675830.8641 | 1223194.6853 | 2675829.6625 | 1223199.7066 | 2675828.2735 | 1223203.9584 | 2675825.2453 | 1223208.2893
125 | 2675823.0632 | 1223166.4562 | 2675817.2083 | 1223149.7706 | 2675816.1615 | 1223133.7134 | 2675816.0797 | 1223131.6685
126 | 2675730.5653 | 1223261.9277 | 2675706.2407 | 1223276.2979 | 2675687.4584 | 1223287.9335 | 2675662.6649 | 1223299.9486 | 2675662.6649 | 1223299.9486
127 | 2675811.6617 | 1223085.9005 | 2675815.3101 | 1223112.4329 | 2675816.0797 | 1223131.6685
128 | 2675645.7752 | 1223321.1254 | 2675647.0838 | 1223316.9174 | 2675652.604 | 1223308.0483 | 2675662.6649 | 1223299.9486
129 | 2675811.6617 | 1223085.9005 | 2675811.4368 | 1223084.2651 | 2675805.8686 | 1223073.8367
130 | 2675645.1147 | 1223323.2494 | 2675645.7752 | 1223321.1254
131 | 2675791.901 | 1223047.6782 | 2675805.8686 | 1223073.8367
132 | 2675791.901 | 1223047.6782 | 2675785.378 | 1223035.4618
133 | 2675744.8436 | 1222951.5635 | 2675722.4732 | 1222932.1663
134 | 2675695.1248 | 1222968.4202 | 2675707.3225 | 1222972.2069
135 | 2675691.4511 | 1222959.1007 | 2675695.1385 | 1222964.3622 | 2675695.1248 | 1222968.4202
136 | 2675730.8468 | 1222914.2118 | 2675724.2358 | 1222906.305
137 | 2675724.2358 | 1222906.305 | 2675724.2358 | 1222906.305 | 2675715.7494 | 1222915.03
138 | 2675707.7999 | 1222926.4939 | 2675715.4978 | 1222915.2887 | 2675715.7494 | 1222915.03
139 | 2675700.452 | 1222937.1896 | 2675707.7999 | 1222926.4939
140 | 2675700.452 | 1222937.1896 | 2675678.7914 | 1222928.0834
141 | 2675700.452 | 1222937.1896 | 2675699.6785 | 1222946.7194 | 2675694.886 | 1222952.6068 | 2675693.7738 | 1222955.9726 | 2675691.4511 | 1222959.1007
142 | 2675659.5169 | 1222919.9803 | 2675678.7914 | 1222928.0834
143 | 2675691.4511 | 1222959.1007 | 2675683.5916 | 1222955.6653
144 | 2675869.7195 | 1222738.6258 | 2675843.9649 | 1222749.7337
145 | 2675843.9649 | 1222749.7337 | 2675825.3044 | 1222757.7819 | 2675822.0777 | 1222763.389 | 2675830.4907 | 1222785.7662
146 | 2675645.1147 | 1223323.2494 | 2675638.6795 | 1223343.9437
147 | 2675630.2573 | 1223371.0274 | 2675638.6795 | 1223343.9437

## bus_geodata
| x | y | coords
0 | 2676303.1387 | 1223267.7884
1 | 2676296.4561 | 1223031.8247
2 | 2676292.9288 | 1223000.5144
3 | 2676046.2862 | 1223327.2864
4 | 2675979.4647 | 1223248.7177
5 | 2675932.8529 | 1223195.6077
6 | 2675897.9832 | 1223198.3761
7 | 2675943.557 | 1223124.0747
8 | 2675954.0594 | 1223130.8141
9 | 2675947.1407 | 1223116.0485
10 | 2675909.8286 | 1223150.3065
11 | 2675898.089 | 1223166.2896
12 | 2675909.701 | 1223138.0239
13 | 2675879.8973 | 1223236.9032
14 | 2675898.3646 | 1223191.6505
15 | 2675894.2528 | 1223156.0673
16 | 2675907.4018 | 1223100.667
17 | 2675916.9718 | 1223112.3503
18 | 2675904.2692 | 1223120.5827
19 | 2675951.7475 | 1223103.0434
20 | 2675848.2496 | 1223042.1616
21 | 2675829.3057 | 1223021.7625
22 | 2675860.2949 | 1223061.9296
23 | 2675818.0444 | 1223014.4921
24 | 2675812.2833 | 1223017.8209
25 | 2675823.286 | 1223011.4568
26 | 2675954.8915 | 1223093.5788
27 | 2675850.2777 | 1222977.0556
28 | 2675845.6557 | 1222971.9791
29 | 2675858.7948 | 1222974.6051
30 | 2675899.5356 | 1223017.7767
31 | 2675923.3791 | 1223009.0193
32 | 2675890.7379 | 1222998.3232
33 | 2675884.3916 | 1222984.295
34 | 2675876.1219 | 1222969.6244
35 | 2675916.2597 | 1222974.3501
36 | 2675923.3882 | 1222973.2292
37 | 2675919.5676 | 1222990.4588
38 | 2675900.9004 | 1222962.5021
39 | 2675873.6368 | 1222961.0479
40 | 2675898.3712 | 1222953.7654
41 | 2675805.4899 | 1223276.6385
42 | 2675787.0916 | 1223256.258
43 | 2675819.9849 | 1223262.4937
44 | 2675955.6414 | 1223148.0862
45 | 2675869.6049 | 1223177.389
46 | 2675888.2368 | 1223144.3977
47 | 2675788.5873 | 1222994.1593
48 | 2675785.3505 | 1222968.4122
49 | 2675769.7682 | 1223006.2277
50 | 2675774.0593 | 1222970.8305
51 | 2675750.1361 | 1222908.9527
52 | 2675843.0531 | 1222955.3604
53 | 2675919.613 | 1222962.385
54 | 2675946.7262 | 1222969.6355
55 | 2675873.6051 | 1222960.9384
56 | 2675898.3345 | 1222953.6385
57 | 2675959.3141 | 1223077.3782
58 | 2675924.6419 | 1223078.5023
59 | 2675960.625 | 1223064.9979
60 | 2675922.1852 | 1223074.0692
61 | 2675960.0885 | 1223029.7789
62 | 2675987.8264 | 1223062.6315
63 | 2676024.8596 | 1222954.5893
64 | 2676024.8972 | 1222969.266
65 | 2675997.2369 | 1222970.4137
66 | 2676034.5366 | 1222974.6482
67 | 2675997.4756 | 1222984.3815
68 | 2675994.2558 | 1222945.5321
69 | 2676029.4297 | 1222982.566
70 | 2676042.214 | 1222970.9438
71 | 2675983.2725 | 1222982.9883
72 | 2676003.0326 | 1222997.153
73 | 2675956.4846 | 1222945.4996
74 | 2676278.4062 | 1222983.8062
75 | 2675945.726 | 1222949.4695
76 | 2675956.5204 | 1222947.4458
77 | 2675947.7108 | 1222989.3648
78 | 2675955.8617 | 1222909.3233
79 | 2675958.6121 | 1222993.9253
80 | 2675928.9876 | 1222917.7862
81 | 2675955.5691 | 1222891.5785
82 | 2675945.9922 | 1223030.1216
83 | 2676003.7437 | 1223007.2877
84 | 2676004.4693 | 1223017.5816
85 | 2676018.0371 | 1223035.1637
86 | 2675927.9452 | 1222914.4819
87 | 2675955.1862 | 1222868.3544
88 | 2675867.0435 | 1223107.1677
89 | 2675878.8633 | 1223128.1861
90 | 2675725.806 | 1222974.8368
91 | 2675776.308 | 1223018.4754
92 | 2675833.3883 | 1222940.6387
93 | 2675954.9812 | 1222864.7278
94 | 2675953.7681 | 1222843.2724
95 | 2675953.7123 | 1222842.2849
96 | 2675952.7254 | 1222811.2899
97 | 2675955.3397 | 1222786.7914
98 | 2675894.0431 | 1222921.5321
99 | 2675891.5129 | 1222913.5613
100 | 2675857.1933 | 1222933.137
101 | 2675972.5661 | 1222690.4254
102 | 2675922.4062 | 1222697.0457
103 | 2675909.3643 | 1222688.8277
104 | 2675883.8825 | 1222732.5173
105 | 2675830.9973 | 1222941.3866
106 | 2675855.5819 | 1222928.0575
107 | 2675955.6351 | 1223148.6218
108 | 2675955.5328 | 1223157.3583
109 | 2675955.4621 | 1223163.3937
110 | 2675955.4604 | 1223163.5339
111 | 2675955.388 | 1223169.714
112 | 2675955.3156 | 1223175.8954
113 | 2675955.2805 | 1223178.8938
114 | 2675777.5341 | 1223242.1488
115 | 2675837.8174 | 1223245.0918
116 | 2675851.6198 | 1223193.3098
117 | 2675848.0763 | 1223235.0807
118 | 2675841.8531 | 1223241.1535
119 | 2675848.88 | 1223234.2964
120 | 2675825.2453 | 1223208.2893
121 | 2675823.0632 | 1223166.4562
122 | 2675730.5653 | 1223261.9277
123 | 2675816.0797 | 1223131.6685
124 | 2675662.6649 | 1223299.9486
125 | 2675811.6617 | 1223085.9005
126 | 2675645.7752 | 1223321.1254
127 | 2675805.8686 | 1223073.8367
128 | 2675791.901 | 1223047.6782
129 | 2675785.378 | 1223035.4618
130 | 2675744.8436 | 1222951.5635
131 | 2675707.3225 | 1222972.2069
132 | 2675722.4732 | 1222932.1663
133 | 2675695.1248 | 1222968.4202
134 | 2675730.8468 | 1222914.2118
135 | 2675724.2358 | 1222906.305
136 | 2675707.7999 | 1222926.4939
137 | 2675715.7494 | 1222915.03
138 | 2675700.452 | 1222937.1896
139 | 2675678.7914 | 1222928.0834
140 | 2675691.4511 | 1222959.1007
141 | 2675659.5169 | 1222919.9803
142 | 2675683.5916 | 1222955.6653
143 | 2675869.7195 | 1222738.6258
144 | 2675843.9649 | 1222749.7337
145 | 2675830.4907 | 1222785.7662
146 | 2675645.1147 | 1223323.2494
147 | 2675638.6795 | 1223343.9437
148 | 2675630.2573 | 1223371.0274
149 | 2675959.3141 | 1223077.3782

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97022 | -0.57621 | 0.017806 | 0.0044626
1 | 0.97414 | -0.49868 | 0 | 0
2 | 0.97471 | -0.48754 | 0.0015813 | 0.0003963
3 | 0.9876 | -0.23666 | 0.0045314 | 0.0011357
4 | 0.98803 | -0.22831 | 0.0029895 | 0.00074923
5 | 0.98852 | -0.21882 | 0 | 0
6 | 0.9888 | -0.2134 | 0 | 0
7 | 0.9935 | -0.12338 | 0 | 0
8 | 0.99318 | -0.12958 | 0.0019591 | 0.00049099
9 | 0.99372 | -0.11908 | 0 | 0
10 | 0.99027 | -0.18508 | 0 | 0
11 | 0.98916 | -0.2064 | 0 | 0
12 | 0.99081 | -0.17481 | 0.0039541 | 0.00099098
13 | 0.9887 | -0.21541 | 0.0026435 | 0.00066251
14 | 0.98886 | -0.21218 | 0.0025252 | 0.00063288
15 | 0.98872 | -0.21484 | 0 | 0
16 | 0.99218 | -0.1485 | 0.0066918 | 0.0016771
17 | 0.99228 | -0.14671 | 0 | 0
18 | 0.99162 | -0.15922 | 0 | 0
19 | 0.99441 | -0.10603 | 0.016025 | 0.0040162
20 | 0.97314 | -0.51813 | 0 | 0
21 | 0.97493 | -0.48291 | 0 | 0
22 | 0.97176 | -0.54539 | 0.063889 | 0.016012
23 | 0.97604 | -0.46109 | 0 | 0
24 | 0.97648 | -0.45249 | 0 | 0
25 | 0.97564 | -0.46894 | 0.006903 | 0.0017301
26 | 0.99493 | -0.096042 | 0.013878 | 0.0034782
27 | 0.97894 | -0.40492 | 0 | 0
28 | 0.97852 | -0.41312 | 0.0037306 | 0.00093498
29 | 0.97932 | -0.39738 | 0.0024951 | 0.00062534
30 | 0.9835 | -0.31585 | 0 | 0
31 | 0.98529 | -0.28113 | 0 | 0
32 | 0.98199 | -0.34521 | 0.016732 | 0.0041935
33 | 0.98114 | -0.36178 | 0 | 0
34 | 0.98015 | -0.38125 | 0 | 0
35 | 0.98789 | -0.23086 | 0 | 0
36 | 0.98845 | -0.22021 | 0 | 0
37 | 0.98663 | -0.25524 | 0.0067044 | 0.0016803
38 | 0.98003 | -0.38358 | 0 | 0
39 | 0.9801 | -0.38209 | 0.0024695 | 0.00061892
40 | 0.97999 | -0.3844 | 0.002216 | 0.00055539
41 | 0.98073 | -0.3699 | 0 | 0
42 | 0.98156 | -0.35379 | 0.012094 | 0.003031
43 | 0.98012 | -0.38181 | 0.011271 | 0.0028248
44 | 0.99277 | -0.13762 | 0.0028931 | 0.00072508
45 | 0.98743 | -0.23974 | 0.001681 | 0.00042129
46 | 0.98866 | -0.216 | 0.0012442 | 0.00031182
47 | 0.97924 | -0.39854 | 0 | 0
48 | 0.97921 | -0.39908 | 0 | 0
49 | 0.98003 | -0.38314 | 0 | 0
50 | 0.97913 | -0.4007 | 0.0043156 | 0.0010816
51 | 0.97915 | -0.40023 | 0.00091149 | 0.00022844
52 | 0.97785 | -0.42632 | 0 | 0
53 | 0.98842 | -0.22065 | 0.0021743 | 0.00054494
54 | 0.9903 | -0.18454 | 0 | 0
55 | 0.9801 | -0.38209 | 0.0027222 | 0.00068224
56 | 0.97999 | -0.38441 | 0.0027641 | 0.00069274
57 | 0.99586 | -0.078434 | 0 | 0
58 | 0.99947 | -0.010046 | 0.0038304 | 0.00096
59 | 0.99525 | -0.090033 | 0 | 0
60 | 1 | 0 | -0.57746 | -0.14784
61 | 0.99366 | -0.12033 | 0 | 0
62 | 0.99472 | -0.10033 | 0.020876 | 0.005232
63 | 0.97996 | -0.385 | 0.010089 | 0.0025284
64 | 0.9801 | -0.38231 | 0 | 0
65 | 0.98134 | -0.3581 | 0 | 0
66 | 0.9797 | -0.38997 | 0 | 0
67 | 0.98092 | -0.36623 | 0 | 0
68 | 0.98339 | -0.31818 | 0.0050844 | 0.0012743
69 | 0.97959 | -0.39214 | 0.0092125 | 0.0023089
70 | 0.9794 | -0.39584 | 0.0096924 | 0.0024291
71 | 0.98083 | -0.36799 | 0.006515 | 0.0016328
72 | 0.98051 | -0.37425 | 0.0071644 | 0.0017956
73 | 0.98639 | -0.26006 | 0 | 0
74 | 0.97512 | -0.47959 | 0 | 0
75 | 0.98797 | -0.22952 | 0.0057446 | 0.0014397
76 | 0.9866 | -0.2559 | 0 | 0
77 | 0.99158 | -0.15998 | 0.006898 | 0.0017288
78 | 0.98526 | -0.28192 | 0 | 0
79 | 0.99222 | -0.14787 | 0 | 0
80 | 0.98495 | -0.28802 | 0 | 0
81 | 0.98491 | -0.28881 | 0.0038265 | 0.00095901
82 | 0.99331 | -0.12702 | 0.026933 | 0.0067501
83 | 0.98034 | -0.37765 | 0 | 0
84 | 0.98025 | -0.37949 | 0.00981 | 0.0024586
85 | 0.98007 | -0.38301 | 0.0086513 | 0.0021682
86 | 0.98491 | -0.28877 | 0.012082 | 0.003028
87 | 0.98453 | -0.29622 | 0 | 0
88 | 0.98852 | -0.21883 | 0.003706 | 0.00092881
89 | 0.9886 | -0.21724 | 0 | 0
90 | 0.97905 | -0.40241 | 0 | 0
91 | 0.98027 | -0.3784 | 0.005958 | 0.0014932
92 | 0.97709 | -0.44121 | 0 | 0
93 | 0.98447 | -0.29739 | 0.002183 | 0.00054711
94 | 0.98416 | -0.30341 | 0.0014025 | 0.00035151
95 | 0.98415 | -0.30366 | 0.0024847 | 0.00062273
96 | 0.98382 | -0.31019 | 0.0041359 | 0.0010366
97 | 0.98364 | -0.31355 | 0.0030354 | 0.00076074
98 | 0.97591 | -0.46434 | 0 | 0
99 | 0.9758 | -0.46655 | 0.014465 | 0.0036254
100 | 0.97643 | -0.45411 | 0 | 0
101 | 0.98324 | -0.32153 | 0 | 0
102 | 0.98301 | -0.32603 | 0 | 0
103 | 0.983 | -0.32609 | 0.00021808 | 5.4655e-05
104 | 0.98279 | -0.33036 | 0.00028766 | 7.2095e-05
105 | 0.97705 | -0.44188 | 0.01476 | 0.0036992
106 | 0.97636 | -0.45546 | 0.013839 | 0.0034684
107 | 0.99276 | -0.13783 | 0.0025959 | 0.0006506
108 | 0.99259 | -0.14097 | 0.0016724 | 0.00041914
109 | 0.99249 | -0.14296 | 0.0077202 | 0.0019349
110 | 0.99249 | -0.14298 | 0.001676 | 0.00042003
111 | 0.99244 | -0.14399 | 0.001676 | 0.00042003
112 | 0.99239 | -0.14481 | 0.001676 | 0.00042003
113 | 0.99238 | -0.14513 | 0.0058592 | 0.0014685
114 | 0.98226 | -0.33995 | 0 | 0
115 | 0.97964 | -0.39137 | 0.0055341 | 0.001387
116 | 0.98648 | -0.25792 | 0.0042767 | 0.0010718
117 | 0.97951 | -0.3938 | 0.0026422 | 0.00066221
118 | 0.97956 | -0.39297 | 0.01032 | 0.0025864
119 | 0.97951 | -0.39386 | 0.0026422 | 0.00066221
120 | 0.98532 | -0.28035 | 0 | 0
121 | 0.98408 | -0.30444 | 0 | 0
122 | 0.98173 | -0.3503 | 0.0034782 | 0.00087172
123 | 0.98308 | -0.32386 | 0.0073514 | 0.0018424
124 | 0.98119 | -0.361 | 0.0021914 | 0.00054922
125 | 0.98185 | -0.34766 | 0.013019 | 0.0032629
126 | 0.98105 | -0.36371 | 0.00088813 | 0.00022259
127 | 0.98153 | -0.354 | 0.015763 | 0.0039506
128 | 0.9809 | -0.36628 | 0.011812 | 0.0029604
129 | 0.98063 | -0.37142 | 0.0026113 | 0.00065446
130 | 0.97898 | -0.40382 | 0 | 0
131 | 0.97877 | -0.40779 | 0.002926 | 0.00073332
132 | 0.97892 | -0.405 | 0.0021947 | 0.00055003
133 | 0.97862 | -0.41077 | 0 | 0
134 | 0.97816 | -0.41985 | 0.00091746 | 0.00022994
135 | 0.97817 | -0.41967 | 0.0011693 | 0.00029304
136 | 0.97825 | -0.41815 | 0.0010008 | 0.00025082
137 | 0.97819 | -0.41921 | 0.0021008 | 0.00052651
138 | 0.97831 | -0.41692 | 0 | 0
139 | 0.97824 | -0.41824 | 0.0017412 | 0.0004364
140 | 0.9785 | -0.41321 | 0 | 0
141 | 0.97822 | -0.41876 | 0.0013511 | 0.00033861
142 | 0.97846 | -0.41392 | 0.0045254 | 0.0011342
143 | 0.98273 | -0.33147 | 0.0011049 | 0.00027691
144 | 0.98265 | -0.33294 | 0.00068042 | 0.00017053
145 | 0.98255 | -0.33498 | 0.0022222 | 0.00055694
146 | 0.98104 | -0.36389 | 0.00065597 | 0.0001644
147 | 0.98096 | -0.36541 | 0.0033979 | 0.0008516
148 | 0.98095 | -0.36564 | 0.00045454 | 0.00011392
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.017806 | -0.0044626 | 0.017872 | 0.0045019 | 6.6016e-05 | 3.9323e-05 | 0.027309 | 0.027308 | 0.027309 | 0.97022 | -0.57621 | 0.97414 | -0.49868 | 7.5025
1 | -0.017872 | -0.0045019 | 0.017882 | 0.0045076 | 9.5252e-06 | 5.6718e-06 | 0.027308 | 0.027308 | 0.027308 | 0.97414 | -0.49868 | 0.97471 | -0.48754 | 7.5022
2 | -0.019463 | -0.0049039 | 0.01947 | 0.0049084 | 7.4055e-06 | 4.4608e-06 | 0.029722 | 0.029722 | 0.029722 | 0.97471 | -0.48754 | 0.97512 | -0.47959 | 8.1654
3 | -0.0045314 | -0.0011357 | 0.0045332 | 0.0011355 | 1.8028e-06 | -1.666e-07 | 0.0068274 | 0.0068269 | 0.0068274 | 0.9876 | -0.23666 | 0.98803 | -0.22831 | 1.8757
4 | -0.0075226 | -0.0018847 | 0.007526 | 0.001886 | 3.4011e-06 | 1.2712e-06 | 0.011329 | 0.011329 | 0.011329 | 0.98803 | -0.22831 | 0.98852 | -0.21882 | 3.1124
5 | -0.007526 | -0.001886 | 0.007528 | 0.0018867 | 1.9425e-06 | 7.2562e-07 | 0.011329 | 0.011329 | 0.011329 | 0.98852 | -0.21882 | 0.9888 | -0.2134 | 3.1123
6 | 0.0026437 | 0.00066213 | -0.0026435 | -0.00066251 | 2.5318e-07 | -3.8507e-07 | 0.0039783 | 0.0039785 | 0.0039785 | 0.9888 | -0.2134 | 0.9887 | -0.21541 | 1.093
7 | -0.010172 | -0.0025489 | 0.010172 | 0.0025491 | 5.9188e-07 | 2.9239e-07 | 0.015307 | 0.015307 | 0.015307 | 0.9888 | -0.2134 | 0.98886 | -0.21218 | 4.2052
8 | 0.027752 | 0.0069638 | -0.027744 | -0.0069587 | 8.2025e-06 | 5.0858e-06 | 0.041568 | 0.041568 | 0.041568 | 0.9935 | -0.12338 | 0.99318 | -0.12958 | 11.4198
9 | -0.027752 | -0.0069638 | 0.027757 | 0.0069673 | 5.6937e-06 | 3.5301e-06 | 0.041568 | 0.041568 | 0.041568 | 0.9935 | -0.12338 | 0.99372 | -0.11908 | 11.4198
10 | 0.025784 | 0.0064677 | -0.025775 | -0.0064616 | 9.8717e-06 | 6.0897e-06 | 0.038633 | 0.038633 | 0.038633 | 0.99318 | -0.12958 | 0.99277 | -0.13762 | 10.6135
11 | -0.27128 | -0.069219 | 0.27145 | 0.069328 | 0.00017111 | 0.00010862 | 0.40665 | 0.40665 | 0.40665 | 0.99372 | -0.11908 | 0.99441 | -0.10603 | 22.3435
12 | 0.24352 | 0.062252 | -0.24319 | -0.062046 | 0.00032502 | 0.00020591 | 0.36508 | 0.36508 | 0.36508 | 0.99372 | -0.11908 | 0.99228 | -0.14671 | 20.0596
13 | 0.23211 | 0.059102 | -0.23187 | -0.058951 | 0.00023836 | 0.00015088 | 0.34911 | 0.34911 | 0.34911 | 0.99027 | -0.18508 | 0.98916 | -0.2064 | 19.182
14 | -0.23211 | -0.059102 | 0.23223 | 0.059175 | 0.00011505 | 7.2825e-05 | 0.34911 | 0.34911 | 0.34911 | 0.99027 | -0.18508 | 0.99081 | -0.17481 | 19.182
15 | 0.21917 | 0.055767 | -0.21908 | -0.055711 | 8.916e-05 | 5.6362e-05 | 0.33001 | 0.33001 | 0.33001 | 0.98916 | -0.2064 | 0.98872 | -0.21484 | 18.1322
16 | 0.012701 | 0.0031839 | -0.012697 | -0.003182 | 3.4992e-06 | 1.9115e-06 | 0.019107 | 0.019107 | 0.019107 | 0.98916 | -0.2064 | 0.98886 | -0.21218 | 5.2491
17 | -0.23618 | -0.060166 | 0.23636 | 0.060279 | 0.00017778 | 0.00011257 | 0.35505 | 0.35505 | 0.35505 | 0.99081 | -0.17481 | 0.99162 | -0.15922 | 19.5082
18 | 0.21413 | 0.054471 | -0.21388 | -0.054308 | 0.00025655 | 0.00016209 | 0.32256 | 0.32256 | 0.32256 | 0.98872 | -0.21484 | 0.98743 | -0.23974 | 17.7229
19 | 0.0049509 | 0.0012404 | -0.0049507 | -0.0012404 | 2.7358e-07 | 6.5699e-09 | 0.007451 | 0.007451 | 0.007451 | 0.98872 | -0.21484 | 0.98866 | -0.216 | 2.047
20 | -0.0066918 | -0.0016771 | 0.0066923 | 0.0016773 | 5.7041e-07 | 1.7e-07 | 0.010036 | 0.010036 | 0.010036 | 0.99218 | -0.1485 | 0.99228 | -0.14671 | 2.7571
21 | 0.2365 | 0.060369 | -0.23636 | -0.060279 | 0.00014283 | 9.0436e-05 | 0.35505 | 0.35505 | 0.35505 | 0.99228 | -0.14671 | 0.99162 | -0.15922 | 19.5082
22 | -0.28747 | -0.073344 | 0.28761 | 0.073432 | 0.00013878 | 8.8173e-05 | 0.43063 | 0.43063 | 0.43063 | 0.99441 | -0.10603 | 0.99493 | -0.096042 | 23.661
23 | -0.063972 | -0.016065 | 0.06408 | 0.016133 | 0.0001077 | 6.8552e-05 | 0.09783 | 0.09783 | 0.09783 | 0.97314 | -0.51813 | 0.97493 | -0.48291 | 26.8765
24 | 0.063972 | 0.016065 | -0.063889 | -0.016012 | 8.3082e-05 | 5.2885e-05 | 0.09783 | 0.09783 | 0.09783 | 0.97314 | -0.51813 | 0.97176 | -0.54539 | 26.8765
25 | -0.06408 | -0.016133 | 0.064122 | 0.016161 | 4.2835e-05 | 2.7265e-05 | 0.09783 | 0.09783 | 0.09783 | 0.97493 | -0.48291 | 0.97564 | -0.46894 | 26.8764
26 | -0.071052 | -0.017908 | 0.071081 | 0.017926 | 2.9236e-05 | 1.8628e-05 | 0.10836 | 0.10836 | 0.10836 | 0.97604 | -0.46109 | 0.97648 | -0.45249 | 29.7688
27 | 0.071052 | 0.017908 | -0.071025 | -0.017891 | 2.6669e-05 | 1.6993e-05 | 0.10836 | 0.10836 | 0.10836 | 0.97604 | -0.46109 | 0.97564 | -0.46894 | 29.7688
28 | -0.071081 | -0.017926 | 0.071265 | 0.018044 | 0.00018409 | 0.00011729 | 0.10836 | 0.10836 | 0.10836 | 0.97648 | -0.45249 | 0.97924 | -0.39854 | 29.7688
29 | -0.30149 | -0.076911 | 0.30175 | 0.077074 | 0.00025662 | 0.00016315 | 0.45139 | 0.45139 | 0.45139 | 0.99493 | -0.096042 | 0.99586 | -0.078434 | 24.8014
30 | 0.046898 | 0.011793 | -0.04688 | -0.011781 | 1.8353e-05 | 1.1625e-05 | 0.071301 | 0.071301 | 0.071301 | 0.97894 | -0.40492 | 0.97852 | -0.41312 | 19.5882
31 | -0.046898 | -0.011793 | 0.046915 | 0.011803 | 1.6896e-05 | 1.0702e-05 | 0.071301 | 0.071301 | 0.071301 | 0.97894 | -0.40492 | 0.97932 | -0.39738 | 19.5882
32 | 0.043149 | 0.010846 | -0.043122 | -0.010829 | 2.7169e-05 | 1.7177e-05 | 0.065628 | 0.065628 | 0.065628 | 0.97852 | -0.41312 | 0.97785 | -0.42632 | 18.0297
33 | -0.04941 | -0.012429 | 0.049449 | 0.012453 | 3.8123e-05 | 2.4172e-05 | 0.075092 | 0.075092 | 0.075092 | 0.97932 | -0.39738 | 0.98015 | -0.38125 | 20.6297
34 | -0.076564 | -0.01933 | 0.076692 | 0.019411 | 0.00012761 | 8.1347e-05 | 0.11589 | 0.11589 | 0.11589 | 0.9835 | -0.31585 | 0.98529 | -0.28113 | 31.838
35 | 0.076564 | 0.01933 | -0.076457 | -0.019261 | 0.00010753 | 6.8549e-05 | 0.11589 | 0.11589 | 0.11589 | 0.9835 | -0.31585 | 0.98199 | -0.34521 | 31.838
36 | -0.076692 | -0.019411 | 0.076787 | 0.019472 | 9.543e-05 | 6.0833e-05 | 0.11589 | 0.11589 | 0.11589 | 0.98529 | -0.28113 | 0.98663 | -0.25524 | 31.8379
37 | 0.059724 | 0.015068 | -0.059677 | -0.015037 | 4.7327e-05 | 3.0095e-05 | 0.090536 | 0.090536 | 0.090536 | 0.98199 | -0.34521 | 0.98114 | -0.36178 | 24.8725
38 | 0.059677 | 0.015037 | -0.059621 | -0.015002 | 5.5518e-05 | 3.5304e-05 | 0.090536 | 0.090536 | 0.090536 | 0.98114 | -0.36178 | 0.98015 | -0.38125 | 24.8725
39 | 0.0049809 | 0.0012482 | -0.0049803 | -0.0012481 | 5.5282e-07 | 2.8904e-08 | 0.0075617 | 0.0075618 | 0.0075618 | 0.98015 | -0.38125 | 0.98003 | -0.38358 | 2.0774
40 | 0.0051919 | 0.0013012 | -0.0051917 | -0.0013012 | 2.0804e-07 | 2.0607e-08 | 0.0078821 | 0.0078822 | 0.0078822 | 0.98015 | -0.38125 | 0.9801 | -0.38209 | 2.1654
41 | -0.083589 | -0.021215 | 0.083632 | 0.021242 | 4.2842e-05 | 2.7327e-05 | 0.126 | 0.126 | 0.126 | 0.98789 | -0.23086 | 0.98845 | -0.22021 | 34.6158
42 | 0.083589 | 0.021215 | -0.083492 | -0.021152 | 9.7906e-05 | 6.245e-05 | 0.126 | 0.126 | 0.126 | 0.98789 | -0.23086 | 0.98663 | -0.25524 | 34.6158
43 | 0.0021744 | 0.00054483 | -0.0021743 | -0.00054494 | 4.6127e-08 | -1.1762e-07 | 0.0032733 | 0.0032734 | 0.0032734 | 0.98845 | -0.22021 | 0.98842 | -0.22065 | 0.89927
44 | -0.085807 | -0.021787 | 0.085954 | 0.021881 | 0.00014756 | 9.4137e-05 | 0.12927 | 0.12927 | 0.12927 | 0.98845 | -0.22021 | 0.9903 | -0.18454 | 35.515
45 | 0.0049803 | 0.0012481 | -0.0049801 | -0.0012481 | 1.9503e-07 | 1.0218e-08 | 0.0075618 | 0.0075618 | 0.0075618 | 0.98003 | -0.38358 | 0.97999 | -0.3844 | 2.0774
46 | 0.0027222 | 0.00068224 | -0.0027222 | -0.00068224 | 7.2946e-10 | -9.6968e-10 | 0.0041329 | 0.0041329 | 0.0041329 | 0.9801 | -0.38209 | 0.9801 | -0.38209 | 1.1354
47 | 0.0027641 | 0.00069274 | -0.0027641 | -0.00069274 | 8.7222e-10 | -1.1064e-09 | 0.004197 | 0.004197 | 0.004197 | 0.97999 | -0.3844 | 0.97999 | -0.38441 | 1.153
48 | -0.032439 | -0.0081406 | 0.032464 | 0.0081563 | 2.4945e-05 | 1.5618e-05 | 0.049222 | 0.049222 | 0.049222 | 0.98073 | -0.3699 | 0.98156 | -0.35379 | 13.5225
49 | 0.032439 | 0.0081406 | -0.03242 | -0.0081291 | 1.8401e-05 | 1.1521e-05 | 0.049222 | 0.049222 | 0.049222 | 0.98073 | -0.3699 | 0.98012 | -0.38181 | 13.5225
50 | -0.044558 | -0.011187 | 0.044587 | 0.011206 | 2.9448e-05 | 1.8629e-05 | 0.067556 | 0.067556 | 0.067556 | 0.98156 | -0.35379 | 0.98226 | -0.33995 | 18.5592
51 | 0.021149 | 0.0053043 | -0.02114 | -0.0052984 | 9.6338e-06 | 5.8518e-06 | 0.03211 | 0.03211 | 0.03211 | 0.98012 | -0.38181 | 0.97964 | -0.39137 | 8.8215
52 | 0.022882 | 0.0057365 | -0.022881 | -0.0057364 | 2.3625e-07 | 1.4428e-07 | 0.034297 | 0.034297 | 0.034297 | 0.99277 | -0.13762 | 0.99276 | -0.13783 | 9.4222
53 | 0.2122 | 0.053887 | -0.21201 | -0.05377 | 0.00018556 | 0.00011722 | 0.32002 | 0.32002 | 0.32002 | 0.98743 | -0.23974 | 0.98648 | -0.25792 | 17.5837
54 | 0.0037065 | 0.00092858 | -0.0037063 | -0.00092868 | 2.1854e-07 | -1.0026e-07 | 0.0055785 | 0.0055786 | 0.0055786 | 0.98866 | -0.216 | 0.9886 | -0.21724 | 1.5326
55 | 0.00091157 | 0.00022721 | -0.00091154 | -0.0002276 | 2.3325e-08 | -3.9309e-07 | 0.0013847 | 0.0013849 | 0.0013849 | 0.97924 | -0.39854 | 0.97921 | -0.39908 | 0.38046
56 | -0.076493 | -0.019352 | 0.07655 | 0.019388 | 5.6586e-05 | 3.5653e-05 | 0.1163 | 0.1163 | 0.1163 | 0.97924 | -0.39854 | 0.98003 | -0.38314 | 15.9754
57 | 0.0043161 | 0.0010815 | -0.0043156 | -0.0010816 | 4.433e-07 | -6.1986e-08 | 0.0065584 | 0.0065586 | 0.0065586 | 0.97924 | -0.39854 | 0.97913 | -0.4007 | 1.8018
58 | 0.00091154 | 0.0002276 | -0.00091149 | -0.00022844 | 4.9712e-08 | -8.3744e-07 | 0.0013849 | 0.0013852 | 0.0013852 | 0.97921 | -0.39908 | 0.97915 | -0.40023 | 0.38055
59 | 0.017953 | 0.0045061 | -0.017937 | -0.0044963 | 1.6488e-05 | 9.8076e-06 | 0.027261 | 0.027262 | 0.027262 | 0.98003 | -0.38314 | 0.97905 | -0.40241 | 7.4894
60 | -0.094503 | -0.023894 | 0.094524 | 0.023907 | 2.1462e-05 | 1.2861e-05 | 0.14356 | 0.14356 | 0.14356 | 0.98003 | -0.38314 | 0.98027 | -0.3784 | 7.888
61 | 0.043122 | 0.010829 | -0.043092 | -0.010809 | 3.061e-05 | 1.9353e-05 | 0.065628 | 0.065628 | 0.065628 | 0.97785 | -0.42632 | 0.97709 | -0.44121 | 18.0297
62 | -0.21215 | -0.053952 | 0.2124 | 0.054112 | 0.00025135 | 0.0001601 | 0.31905 | 0.31905 | 0.31905 | 0.9903 | -0.18454 | 0.99158 | -0.15998 | 29.2172
63 | 0.1262 | 0.032071 | -0.12592 | -0.031897 | 0.00027269 | 0.00017426 | 0.18978 | 0.18978 | 0.18978 | 0.9903 | -0.18454 | 0.98797 | -0.22952 | 52.1368
64 | -0.5698 | -0.1455 | 0.5717 | 0.14671 | 0.0018902 | 0.0012075 | 0.85236 | 0.85236 | 0.85236 | 0.99586 | -0.078434 | 0.99947 | -0.010046 | 46.8331
65 | 0.26806 | 0.068424 | -0.26791 | -0.068329 | 0.00015014 | 9.5281e-05 | 0.40098 | 0.40098 | 0.40098 | 0.99586 | -0.078434 | 0.99525 | -0.090033 | 22.0317
66 | -0.57553 | -0.14767 | 0.57581 | 0.14784 | 0.00028064 | 0.00017928 | 0.85806 | 0.85806 | 0.85806 | 0.99947 | -0.010046 | 1 | 0 | 47.1464
67 | 0.24702 | 0.063091 | -0.24666 | -0.062862 | 0.00036122 | 0.0002289 | 0.36975 | 0.36975 | 0.36975 | 0.99525 | -0.090033 | 0.99366 | -0.12033 | 20.3159
68 | 0.020886 | 0.0052382 | -0.020876 | -0.005232 | 1.0243e-05 | 6.1918e-06 | 0.031228 | 0.031229 | 0.031229 | 0.99525 | -0.090033 | 0.99472 | -0.10033 | 8.5793
69 | 0.026942 | 0.0067555 | -0.026933 | -0.0067501 | 8.5824e-06 | 5.3107e-06 | 0.040347 | 0.040347 | 0.040347 | 0.99366 | -0.12033 | 0.99331 | -0.12702 | 11.0844
70 | 0.21972 | 0.056106 | -0.21943 | -0.055922 | 0.00029202 | 0.00018457 | 0.3294 | 0.3294 | 0.3294 | 0.99366 | -0.12033 | 0.99222 | -0.14787 | 18.0991
71 | -0.010089 | -0.0025284 | 0.01009 | 0.0025291 | 1.2916e-06 | 6.4168e-07 | 0.015319 | 0.015319 | 0.015319 | 0.97996 | -0.385 | 0.9801 | -0.38231 | 4.2085
72 | -0.048567 | -0.012237 | 0.048623 | 0.012273 | 5.6314e-05 | 3.5693e-05 | 0.073759 | 0.073759 | 0.073759 | 0.9801 | -0.38231 | 0.98134 | -0.3581 | 20.2635
73 | 0.038477 | 0.009708 | -0.038463 | -0.0096991 | 1.4108e-05 | 8.8906e-06 | 0.05844 | 0.05844 | 0.05844 | 0.9801 | -0.38231 | 0.9797 | -0.38997 | 16.055
74 | 0.03217 | 0.0080724 | -0.032157 | -0.0080646 | 1.2469e-05 | 7.8036e-06 | 0.048783 | 0.048783 | 0.048783 | 0.98134 | -0.3581 | 0.98092 | -0.36623 | 13.4019
75 | -0.080793 | -0.020345 | 0.080947 | 0.020444 | 0.00015454 | 9.8559e-05 | 0.12254 | 0.12254 | 0.12254 | 0.98134 | -0.3581 | 0.98339 | -0.31818 | 33.6653
76 | 0.0092135 | 0.0023093 | -0.0092125 | -0.0023089 | 9.5217e-07 | 4.4614e-07 | 0.013994 | 0.013994 | 0.013994 | 0.9797 | -0.38997 | 0.97959 | -0.39214 | 3.8445
77 | 0.029249 | 0.0073898 | -0.029241 | -0.0073847 | 8.2185e-06 | 5.1202e-06 | 0.044446 | 0.044446 | 0.044446 | 0.9797 | -0.38997 | 0.9794 | -0.39584 | 12.2105
78 | 0.0065156 | 0.001633 | -0.006515 | -0.0016328 | 5.4567e-07 | 1.6122e-07 | 0.0098839 | 0.009884 | 0.009884 | 0.98092 | -0.36623 | 0.98083 | -0.36799 | 2.7154
79 | 0.025642 | 0.0064316 | -0.025632 | -0.0064256 | 9.7927e-06 | 6.0496e-06 | 0.038899 | 0.038899 | 0.038899 | 0.98092 | -0.36623 | 0.98051 | -0.37425 | 10.6866
80 | -0.086032 | -0.021718 | 0.086272 | 0.021871 | 0.00024024 | 0.00015327 | 0.13024 | 0.13024 | 0.13024 | 0.98339 | -0.31818 | 0.98639 | -0.26006 | 35.7789
81 | 0.019549 | 0.0049556 | -0.01947 | -0.0049084 | 7.8356e-05 | 4.7184e-05 | 0.029721 | 0.029722 | 0.029722 | 0.9794 | -0.39584 | 0.97512 | -0.47959 | 8.1653
82 | 0.018467 | 0.00463 | -0.018464 | -0.0046283 | 2.9926e-06 | 1.7871e-06 | 0.028027 | 0.028027 | 0.028027 | 0.98051 | -0.37425 | 0.98034 | -0.37765 | 7.6996
83 | 0.03373 | 0.0084733 | -0.033695 | -0.0084512 | 3.5148e-05 | 2.2033e-05 | 0.050891 | 0.050891 | 0.050891 | 0.98639 | -0.26006 | 0.98526 | -0.28192 | 13.9811
84 | -0.12 | -0.030345 | 0.12003 | 0.03036 | 2.3953e-05 | 1.5305e-05 | 0.18113 | 0.18113 | 0.18113 | 0.98639 | -0.26006 | 0.9866 | -0.2559 | 49.7598
85 | 0.12018 | 0.030457 | -0.12003 | -0.03036 | 0.00015215 | 9.7217e-05 | 0.18113 | 0.18113 | 0.18113 | 0.98797 | -0.22952 | 0.9866 | -0.2559 | 49.7598
86 | -0.2193 | -0.055841 | 0.21943 | 0.055922 | 0.00012815 | 8.1001e-05 | 0.3294 | 0.3294 | 0.3294 | 0.99158 | -0.15998 | 0.99222 | -0.14787 | 18.0991
87 | 0.012086 | 0.0030301 | -0.012082 | -0.0030282 | 3.511e-06 | 1.8893e-06 | 0.018253 | 0.018253 | 0.018253 | 0.98526 | -0.28192 | 0.98495 | -0.28802 | 5.0146
88 | 0.021609 | 0.0054211 | -0.021602 | -0.0054168 | 7.0894e-06 | 4.3113e-06 | 0.032638 | 0.032638 | 0.032638 | 0.98526 | -0.28192 | 0.98491 | -0.28881 | 8.9665
89 | 0.012082 | 0.0030282 | -0.012082 | -0.003028 | 4.328e-07 | 2.3291e-07 | 0.018253 | 0.018253 | 0.018253 | 0.98495 | -0.28802 | 0.98491 | -0.28877 | 5.0146
90 | 0.017776 | 0.0044578 | -0.017769 | -0.0044541 | 6.2827e-06 | 3.7254e-06 | 0.026857 | 0.026857 | 0.026857 | 0.98491 | -0.28881 | 0.98453 | -0.29622 | 7.3783
91 | 0.0098109 | 0.002459 | -0.00981 | -0.0024586 | 8.583e-07 | 4.1919e-07 | 0.014892 | 0.014892 | 0.014892 | 0.98034 | -0.37765 | 0.98025 | -0.37949 | 4.0911
92 | 0.0086535 | 0.0021692 | -0.0086513 | -0.0021682 | 2.2082e-06 | 9.8302e-07 | 0.013135 | 0.013135 | 0.013135 | 0.98034 | -0.37765 | 0.98007 | -0.38301 | 3.6086
93 | 0.017769 | 0.0044541 | -0.017769 | -0.0044535 | 9.825e-07 | 5.8261e-07 | 0.026857 | 0.026857 | 0.026857 | 0.98453 | -0.29622 | 0.98447 | -0.29739 | 7.3783
94 | -0.003706 | -0.00092881 | 0.0037063 | 0.00092868 | 2.8143e-07 | -1.2906e-07 | 0.0055787 | 0.0055786 | 0.0055787 | 0.98852 | -0.21883 | 0.9886 | -0.21724 | 1.5326
95 | 0.0021949 | 0.00054939 | -0.0021948 | -0.00054974 | 1.4736e-07 | -3.4974e-07 | 0.0033357 | 0.0033359 | 0.0033359 | 0.97905 | -0.40241 | 0.97898 | -0.40382 | 0.91645
96 | 0.015742 | 0.0039469 | -0.015738 | -0.0039446 | 4.0351e-06 | 2.3462e-06 | 0.023926 | 0.023926 | 0.023926 | 0.97905 | -0.40241 | 0.97877 | -0.40779 | 6.573
97 | -0.10048 | -0.0254 | 0.10052 | 0.025421 | 3.3634e-05 | 2.0311e-05 | 0.15261 | 0.15261 | 0.15261 | 0.98027 | -0.3784 | 0.98063 | -0.37142 | 8.3849
98 | 0.028331 | 0.00711 | -0.028314 | -0.0070991 | 1.7426e-05 | 1.0841e-05 | 0.043149 | 0.043149 | 0.043149 | 0.97709 | -0.44121 | 0.97643 | -0.45411 | 11.8542
99 | 0.01476 | 0.0036995 | -0.01476 | -0.0036992 | 4.7352e-07 | 2.7176e-07 | 0.022479 | 0.022479 | 0.022479 | 0.97709 | -0.44121 | 0.97705 | -0.44188 | 6.1755
100 | 0.015586 | 0.0039064 | -0.015581 | -0.0039038 | 4.4722e-06 | 2.589e-06 | 0.023557 | 0.023558 | 0.023558 | 0.98447 | -0.29739 | 0.98416 | -0.30341 | 6.4719
101 | 0.014179 | 0.0035523 | -0.014178 | -0.0035522 | 1.7045e-07 | 9.652e-08 | 0.021437 | 0.021437 | 0.021437 | 0.98416 | -0.30341 | 0.98415 | -0.30366 | 5.8893
102 | 0.011694 | 0.0029295 | -0.01169 | -0.0029275 | 3.6357e-06 | 1.9329e-06 | 0.01768 | 0.01768 | 0.01768 | 0.98415 | -0.30366 | 0.98382 | -0.31019 | 4.8572
103 | 0.0075541 | 0.001891 | -0.0075529 | -0.0018905 | 1.2084e-06 | 4.5993e-07 | 0.011425 | 0.011425 | 0.011425 | 0.98382 | -0.31019 | 0.98364 | -0.31355 | 3.1387
104 | 0.0045175 | 0.0011298 | -0.0045157 | -0.0011299 | 1.7141e-06 | -1.451e-07 | 0.006833 | 0.0068334 | 0.0068334 | 0.98364 | -0.31355 | 0.98324 | -0.32153 | 1.8773
105 | 0.014467 | 0.0036262 | -0.014465 | -0.0036254 | 1.5258e-06 | 8.7203e-07 | 0.022058 | 0.022059 | 0.022059 | 0.97591 | -0.46434 | 0.9758 | -0.46655 | 6.06
106 | -0.014467 | -0.0036262 | 0.014474 | 0.0036303 | 7.0493e-06 | 4.0286e-06 | 0.022058 | 0.022058 | 0.022058 | 0.97591 | -0.46434 | 0.97643 | -0.45411 | 6.06
107 | 0.01384 | 0.0034689 | -0.013839 | -0.0034684 | 8.8878e-07 | 5.0218e-07 | 0.021091 | 0.021091 | 0.021091 | 0.97643 | -0.45411 | 0.97636 | -0.45546 | 5.7943
108 | 0.0045157 | 0.0011299 | -0.0045148 | -0.00113 | 9.6672e-07 | -8.1308e-08 | 0.0068334 | 0.0068337 | 0.0068337 | 0.98324 | -0.32153 | 0.98301 | -0.32603 | 1.8774
109 | 0.00021808 | 5.446e-05 | -0.00021808 | -5.4655e-05 | 6.2981e-10 | -1.9502e-07 | 0.00033004 | 0.00033011 | 0.00033011 | 0.98301 | -0.32603 | 0.983 | -0.32609 | 0.09069
110 | 0.0042967 | 0.0010755 | -0.0042958 | -0.0010757 | 8.8429e-07 | -1.4064e-07 | 0.0065036 | 0.0065039 | 0.0065039 | 0.98301 | -0.32603 | 0.98279 | -0.33036 | 1.7868
111 | 0.0040082 | 0.0010036 | -0.0040079 | -0.0010036 | 2.13e-07 | -5.9117e-08 | 0.0060683 | 0.0060684 | 0.0060684 | 0.98279 | -0.33036 | 0.98273 | -0.33147 | 1.6671
112 | 0.020285 | 0.0050858 | -0.020282 | -0.005084 | 3.0291e-06 | 1.8257e-06 | 0.030406 | 0.030406 | 0.030406 | 0.99276 | -0.13783 | 0.99259 | -0.14097 | 8.3533
113 | 0.01861 | 0.0046648 | -0.018608 | -0.0046638 | 1.7617e-06 | 1.0495e-06 | 0.027899 | 0.027899 | 0.027899 | 0.99259 | -0.14097 | 0.99249 | -0.14296 | 7.6645
114 | 0.010888 | 0.0027289 | -0.010888 | -0.0027289 | 1.4002e-08 | 7.1496e-09 | 0.016324 | 0.016324 | 0.016324 | 0.99249 | -0.14296 | 0.99249 | -0.14298 | 4.4846
115 | 0.0092119 | 0.0023089 | -0.0092115 | -0.0023087 | 4.4211e-07 | 2.0308e-07 | 0.013811 | 0.013811 | 0.013811 | 0.99249 | -0.14298 | 0.99244 | -0.14399 | 3.7943
116 | 0.0075355 | 0.0018886 | -0.0075352 | -0.0018885 | 2.9593e-07 | 1.0952e-07 | 0.011298 | 0.011298 | 0.011298 | 0.99244 | -0.14399 | 0.99239 | -0.14481 | 3.104
117 | 0.0058593 | 0.0014685 | -0.0058592 | -0.0014685 | 8.6793e-08 | 1.6805e-08 | 0.0087855 | 0.0087856 | 0.0087856 | 0.99239 | -0.14481 | 0.99238 | -0.14513 | 2.4136
118 | 0.011077 | 0.0027774 | -0.011071 | -0.0027746 | 5.4603e-06 | 2.8404e-06 | 0.01678 | 0.01678 | 0.01678 | 0.98226 | -0.33995 | 0.98173 | -0.3503 | 4.61
119 | -0.055664 | -0.013983 | 0.055822 | 0.014084 | 0.0001588 | 0.00010088 | 0.084336 | 0.084335 | 0.084336 | 0.98226 | -0.33995 | 0.98532 | -0.28035 | 23.1692
120 | 0.015606 | 0.0039115 | -0.015604 | -0.0039108 | 1.1882e-06 | 6.8943e-07 | 0.023704 | 0.023704 | 0.023704 | 0.97964 | -0.39137 | 0.97956 | -0.39297 | 6.5121
121 | 0.20773 | 0.052698 | -0.20751 | -0.052557 | 0.00022379 | 0.00014129 | 0.31357 | 0.31357 | 0.31357 | 0.98648 | -0.25792 | 0.98532 | -0.28035 | 17.2293
122 | -0.0052845 | -0.0013244 | 0.0052847 | 0.0013244 | 2.1014e-07 | 2.5036e-08 | 0.0080279 | 0.0080278 | 0.0080279 | 0.97951 | -0.3938 | 0.97956 | -0.39297 | 2.2055
123 | 0.0026422 | 0.0006622 | -0.0026422 | -0.00066221 | 6.785e-09 | -9.793e-09 | 0.0040139 | 0.0040139 | 0.0040139 | 0.97951 | -0.3938 | 0.97951 | -0.39386 | 1.1027
124 | 0.15169 | 0.038473 | -0.15151 | -0.038363 | 0.00017541 | 0.00010943 | 0.22924 | 0.22924 | 0.22924 | 0.98532 | -0.28035 | 0.98408 | -0.30444 | 12.5955
125 | 0.15151 | 0.038363 | -0.15137 | -0.038275 | 0.00014118 | 8.8082e-05 | 0.22924 | 0.22924 | 0.22924 | 0.98408 | -0.30444 | 0.98308 | -0.32386 | 12.5956
126 | 0.0075929 | 0.0019029 | -0.007589 | -0.0019014 | 3.8691e-06 | 1.4918e-06 | 0.011508 | 0.011509 | 0.011509 | 0.98173 | -0.3503 | 0.98119 | -0.361 | 3.1618
127 | 0.14402 | 0.036433 | -0.14385 | -0.036331 | 0.00016425 | 0.0001022 | 0.21811 | 0.21811 | 0.21811 | 0.98308 | -0.32386 | 0.98185 | -0.34766 | 11.9843
128 | 0.0053976 | 0.0013522 | -0.0053969 | -0.0013521 | 6.9774e-07 | 9.5865e-08 | 0.0081855 | 0.0081856 | 0.0081856 | 0.98119 | -0.361 | 0.98105 | -0.36371 | 2.2488
129 | 0.13084 | 0.033068 | -0.1308 | -0.033043 | 3.9767e-05 | 2.4599e-05 | 0.19838 | 0.19838 | 0.19838 | 0.98185 | -0.34766 | 0.98153 | -0.354 | 10.9002
130 | 0.0045088 | 0.0011295 | -0.0045087 | -0.0011295 | 3.9008e-08 | -3.1206e-09 | 0.0068385 | 0.0068385 | 0.0068385 | 0.98105 | -0.36371 | 0.98104 | -0.36389 | 1.8787
131 | 0.11503 | 0.029092 | -0.11496 | -0.029051 | 6.7713e-05 | 4.1463e-05 | 0.17449 | 0.17449 | 0.17449 | 0.98153 | -0.354 | 0.9809 | -0.36628 | 9.5872
132 | 0.10315 | 0.026091 | -0.10313 | -0.026075 | 2.5461e-05 | 1.5421e-05 | 0.15657 | 0.15657 | 0.15657 | 0.9809 | -0.36628 | 0.98063 | -0.37142 | 8.6026
133 | 0.0021948 | 0.00054974 | -0.0021947 | -0.00055003 | 1.2336e-07 | -2.927e-07 | 0.0033359 | 0.003336 | 0.003336 | 0.97898 | -0.40382 | 0.97892 | -0.405 | 0.91649
134 | 0.012812 | 0.0032113 | -0.01281 | -0.0032103 | 1.817e-06 | 1.0024e-06 | 0.019478 | 0.019478 | 0.019478 | 0.97877 | -0.40779 | 0.97862 | -0.41077 | 5.351
135 | 0.01281 | 0.0032103 | -0.012808 | -0.0032094 | 1.4907e-06 | 8.224e-07 | 0.019478 | 0.019478 | 0.019478 | 0.97862 | -0.41077 | 0.9785 | -0.41321 | 5.351
136 | -0.00091746 | -0.00022994 | 0.00091747 | 0.00022981 | 7.5282e-09 | -1.2456e-07 | 0.0013957 | 0.0013956 | 0.0013957 | 0.97816 | -0.41985 | 0.97817 | -0.41967 | 0.38343
137 | -0.0020867 | -0.00052286 | 0.0020868 | 0.00052273 | 4.5991e-08 | -1.2335e-07 | 0.0031743 | 0.0031743 | 0.0031743 | 0.97817 | -0.41967 | 0.97819 | -0.41921 | 0.87207
138 | 0.0041878 | 0.0010492 | -0.0041876 | -0.0010492 | 2.1235e-07 | -3.9294e-08 | 0.0063699 | 0.00637 | 0.00637 | 0.97825 | -0.41815 | 0.97819 | -0.41921 | 1.75
139 | -0.0051886 | -0.0013 | 0.0051889 | 0.0013001 | 3.031e-07 | 3.1057e-08 | 0.0078922 | 0.0078922 | 0.0078922 | 0.97825 | -0.41815 | 0.97831 | -0.41692 | 2.1682
140 | 0.0030925 | 0.00077459 | -0.0030923 | -0.00077477 | 1.9495e-07 | -1.7025e-07 | 0.0047036 | 0.0047037 | 0.0047037 | 0.97831 | -0.41692 | 0.97824 | -0.41824 | 1.2922
141 | -0.0082814 | -0.0020747 | 0.0082829 | 0.0020753 | 1.4626e-06 | 6.2733e-07 | 0.012596 | 0.012596 | 0.012596 | 0.97831 | -0.41692 | 0.9785 | -0.41321 | 3.4604
142 | 0.0013511 | 0.00033837 | -0.0013511 | -0.00033861 | 3.3116e-08 | -2.413e-07 | 0.0020551 | 0.0020552 | 0.0020552 | 0.97824 | -0.41824 | 0.97822 | -0.41876 | 0.56461
143 | 0.0045255 | 0.0011341 | -0.0045254 | -0.0011342 | 1.5196e-07 | -1.0215e-08 | 0.006882 | 0.006882 | 0.006882 | 0.9785 | -0.41321 | 0.97846 | -0.41392 | 1.8907
144 | 0.0029031 | 0.00072674 | -0.0029029 | -0.00072697 | 2.0321e-07 | -2.2529e-07 | 0.0043954 | 0.0043956 | 0.0043956 | 0.98273 | -0.33147 | 0.98265 | -0.33294 | 1.2076
145 | 0.0022224 | 0.00055644 | -0.0022222 | -0.00055694 | 2.1531e-07 | -5.0438e-07 | 0.0033652 | 0.0033654 | 0.0033654 | 0.98265 | -0.33294 | 0.98255 | -0.33498 | 0.92457
146 | 0.0038528 | 0.00096507 | -0.0038525 | -0.00096517 | 2.7752e-07 | -9.6007e-08 | 0.0058436 | 0.0058437 | 0.0058437 | 0.98104 | -0.36389 | 0.98096 | -0.36541 | 1.6054
147 | 0.00045454 | 0.00011356 | -0.00045454 | -0.00011392 | 5.0555e-09 | -3.5483e-07 | 0.00068937 | 0.0006895 | 0.0006895 | 0.98096 | -0.36541 | 0.98095 | -0.36564 | 0.18942

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60522 | 0.1548

## res_load
| p_mw | q_mvar
0 | 0.017806 | 0.0044626
1 | 0.0015813 | 0.0003963
2 | 0.0045314 | 0.0011357
3 | 0.0029895 | 0.00074923
4 | 0.0019591 | 0.00049099
5 | 0.0039541 | 0.00099098
6 | 0.0026435 | 0.00066251
7 | 0.0025252 | 0.00063288
8 | 0.0066918 | 0.0016771
9 | 0.016025 | 0.0040162
10 | 0.063889 | 0.016012
11 | 0.006903 | 0.0017301
12 | 0.013878 | 0.0034782
13 | 0.0037306 | 0.00093498
14 | 0.0024951 | 0.00062534
15 | 0.016732 | 0.0041935
16 | 0.0067044 | 0.0016803
17 | 0.0024695 | 0.00061892
18 | 0.002216 | 0.00055539
19 | 0.012094 | 0.003031
20 | 0.011271 | 0.0028248
21 | 0.0028931 | 0.00072508
22 | 0.001681 | 0.00042129
23 | 0.0012442 | 0.00031182
24 | 0.0043156 | 0.0010816
25 | 0.00091149 | 0.00022844
26 | 0.0021743 | 0.00054494
27 | 0.0027222 | 0.00068224
28 | 0.0027641 | 0.00069274
29 | 0.0038304 | 0.00096
30 | 0.027762 | 0.0069579
31 | 0.020876 | 0.005232
32 | 0.010089 | 0.0025284
33 | 0.0050844 | 0.0012743
34 | 0.0092125 | 0.0023089
35 | 0.0096924 | 0.0024291
36 | 0.006515 | 0.0016328
37 | 0.0071644 | 0.0017956
38 | 0.0057446 | 0.0014397
39 | 0.006898 | 0.0017288
40 | 0.0038265 | 0.00095901
41 | 0.026933 | 0.0067501
42 | 0.00981 | 0.0024586
43 | 0.0086513 | 0.0021682
44 | 0.012082 | 0.003028
45 | 0.003706 | 0.00092881
46 | 0.005958 | 0.0014932
47 | 0.002183 | 0.00054711
48 | 0.0014025 | 0.00035151
49 | 0.0024847 | 0.00062273
50 | 0.0041359 | 0.0010366
51 | 0.0030354 | 0.00076074
52 | 0.014465 | 0.0036254
53 | 0.00021808 | 5.4655e-05
54 | 0.00028766 | 7.2095e-05
55 | 0.01476 | 0.0036992
56 | 0.013839 | 0.0034684
57 | 0.0025959 | 0.0006506
58 | 0.0016724 | 0.00041914
59 | 0.0077202 | 0.0019349
60 | 0.001676 | 0.00042003
61 | 0.001676 | 0.00042003
62 | 0.001676 | 0.00042003
63 | 0.0058592 | 0.0014685
64 | 0.0055341 | 0.001387
65 | 0.0042767 | 0.0010718
66 | 0.0026422 | 0.00066221
67 | 0.01032 | 0.0025864
68 | 0.0026422 | 0.00066221
69 | 0.0034782 | 0.00087172
70 | 0.0073514 | 0.0018424
71 | 0.0021914 | 0.00054922
72 | 0.013019 | 0.0032629
73 | 0.00088813 | 0.00022259
74 | 0.015763 | 0.0039506
75 | 0.011812 | 0.0029604
76 | 0.0026113 | 0.00065446
77 | 0.002926 | 0.00073332
78 | 0.0021947 | 0.00055003
79 | 0.00091746 | 0.00022994
80 | 0.0011693 | 0.00029304
81 | 0.0010008 | 0.00025082
82 | 0.0021008 | 0.00052651
83 | 0.0017412 | 0.0004364
84 | 0.0013511 | 0.00033861
85 | 0.0045254 | 0.0011342
86 | 0.0011049 | 0.00027691
87 | 0.00068042 | 0.00017053
88 | 0.0022222 | 0.00055694
89 | 0.00065597 | 0.0001644
90 | 0.0033979 | 0.0008516
91 | 0.00045454 | 0.00011392

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1