## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1707-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1707-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1707-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1707-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1707-9_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1707-9_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1707-9_0_4_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_1707-9_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1707-9_0_4_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_1707-9_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1707-9_0_4_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1707-9_0_4_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_1707-9_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1707-9_0_4_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_1707-9_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1707-9_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1707-9_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1707-9_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1707-9_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1707-9_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1707-9_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1707-9_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1707-9_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1707-9_0_4_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1707-9_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1707-9_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1707-9_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1707-9_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1707-9_0_4_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_1707-9_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1707-9_0_4_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_1707-9_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1707-9_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1707-9_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1707-9_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1707-9_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_MV_0_0_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1707-9_0_4_load_0 | 0 | 0.069617 | 0.017448 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1707-9_0_4_load_2 | 2 | 0.024654 | 0.0061789 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1707-9_0_4_load_14 | 6 | 0.0096637 | 0.002422 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1707-9_0_4_load_38 | 8 | 0.06646 | 0.016657 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1707-9_0_4_load_13 | 9 | 0.029371 | 0.0073611 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1707-9_0_4_load_25 | 10 | 0.0071722 | 0.0017975 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1707-9_0_4_load_7 | 14 | 0.0049299 | 0.0012355 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1707-9_0_4_load_8 | 15 | 0.0049967 | 0.0012523 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1707-9_0_4_load_10 | 17 | 0.0025919 | 0.00064958 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1707-9_0_4_load_20 | 20 | 0.0023829 | 0.0005972 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1707-9_0_4_load_15 | 21 | 0.024266 | 0.0060817 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1707-9_0_4_load_16 | 22 | 0.009657 | 0.0024203 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1707-9_0_4_load_37 | 23 | 0.01155 | 0.0028947 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1707-9_0_4_load_21 | 24 | 0.0036355 | 0.00091115 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1707-9_0_4_load_17 | 25 | 0.050218 | 0.012586 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1707-9_0_4_load_18 | 26 | 0.0052287 | 0.0013104 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1707-9_0_4_load_35 | 29 | 0.048057 | 0.012044 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1707-9_0_4_load_33 | 30 | 0.0040949 | 0.0010263 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1707-9_0_4_load_22 | 31 | 0.00318 | 0.000797 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1707-9_0_4_load_28 | 33 | 0.0058039 | 0.0014546 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1707-9_0_4_load_30 | 34 | 0.0057102 | 0.0014311 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1707-9_0_4_load_29 | 35 | 0.0032641 | 0.00081805 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1707-9_0_4_line_0 |  | 0 | 1 | 0.023053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1707-9_0_4_line_1 |  | 1 | 2 | 0.037916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1707-9_0_4_line_2 |  | 1 | 3 | 0.003777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1707-9_0_4_line_3 |  | 2 | 4 | 0.029904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1707-9_0_4_line_4 |  | 3 | 5 | 0.04603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1707-9_0_4_line_5 |  | 3 | 6 | 0.030797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1707-9_0_4_line_6 |  | 4 | 7 | 0.10447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1707-9_0_4_line_7 |  | 5 | 8 | 0.010491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1707-9_0_4_line_8 |  | 6 | 9 | 0.03233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1707-9_0_4_line_9 |  | 7 | 10 | 0.010759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1707-9_0_4_line_10 |  | 8 | 12 | 0.013715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1707-9_0_4_line_11 |  | 10 | 11 | 0.025482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1707-9_0_4_line_12 |  | 11 | 32 | 0.014633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1707-9_0_4_line_13 |  | 11 | 33 | 0.02554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1707-9_0_4_line_14 |  | 12 | 13 | 0.022263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1707-9_0_4_line_15 |  | 13 | 31 | 0.0085398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1707-9_0_4_line_16 |  | 14 | 15 | 0.025607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1707-9_0_4_line_17 |  | 14 | 16 | 0.025101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1707-9_0_4_line_18 |  | 15 | 17 | 0.028074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1707-9_0_4_line_19 |  | 16 | 18 | 0.008771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1707-9_0_4_line_20 |  | 16 | 19 | 0.011588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1707-9_0_4_line_21 |  | 17 | 20 | 0.017766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1707-9_0_4_line_22 |  | 18 | 21 | 0.01549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1707-9_0_4_line_23 |  | 18 | 22 | 0.045805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1707-9_0_4_line_24 |  | 19 | 23 | 0.010559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1707-9_0_4_line_25 |  | 20 | 24 | 0.018949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1707-9_0_4_line_26 |  | 21 | 25 | 0.023311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1707-9_0_4_line_27 |  | 24 | 31 | 0.016607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1707-9_0_4_line_28 |  | 25 | 26 | 0.039121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1707-9_0_4_line_29 |  | 26 | 27 | 0.019332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1707-9_0_4_line_30 |  | 27 | 28 | 0.01803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1707-9_0_4_line_31 |  | 28 | 29 | 0.058887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1707-9_0_4_line_32 |  | 28 | 30 | 0.035422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1707-9_0_4_line_33 |  | 32 | 34 | 0.0255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1707-9_0_4_line_34 |  | 33 | 35 | 0.00027509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1707-9_0_4_trafo_14 | 0.63 MVA 20/0.4 kV | 36 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2674982.3529 | 1221514.3938 | 2674984.2007 | 1221512.8494 | 2675000.1251 | 1221499.7116
1 | 2674982.3529 | 1221514.3938 | 2674972.2367 | 1221500.2239 | 2674969.9248 | 1221492.234 | 2674962.3566 | 1221482.68
2 | 2674979.4546 | 1221516.8256 | 2674982.3529 | 1221514.3938
3 | 2674943.7878 | 1221459.2391 | 2674962.3566 | 1221482.68
4 | 2674946.006 | 1221522.2749 | 2674959.4538 | 1221512.2598 | 2674965.0843 | 1221507.3274 | 2674968.7384 | 1221503.9156 | 2674979.4546 | 1221516.8256
5 | 2674979.4546 | 1221516.8256 | 2674988.8034 | 1221528.6844 | 2674993.5212 | 1221534.1696 | 2674999.1884 | 1221540.4521
6 | 2674943.7878 | 1221459.2391 | 2674941.9236 | 1221448.2306 | 2674948.8734 | 1221437.3332 | 2674945.2811 | 1221434.0302 | 2674956.1885 | 1221420.9256 | 2674970.2552 | 1221407.5716 | 2674986.5847 | 1221395.258 | 2675001.3614 | 1221383.9589
7 | 2674946.006 | 1221522.2749 | 2674939.2516 | 1221530.3174
8 | 2674999.1884 | 1221540.4521 | 2675020.8431 | 1221564.4585
9 | 2675001.3614 | 1221383.9589 | 2675009.6937 | 1221377.1519
10 | 2674939.2516 | 1221530.3174 | 2674930.5229 | 1221540.9145
11 | 2675028.3694 | 1221359.8832 | 2675019.3216 | 1221369.2865 | 2675009.6937 | 1221377.1519
12 | 2675028.3694 | 1221359.8832 | 2675038.4944 | 1221349.2927
13 | 2675028.3694 | 1221359.8832 | 2675051.686 | 1221370.3049
14 | 2674921.6177 | 1221561.3158 | 2674926.2208 | 1221549.9997 | 2674930.5229 | 1221540.9145
15 | 2674921.6177 | 1221561.3158 | 2674929.643 | 1221564.2349
16 | 2675029.6727 | 1221601.2797 | 2675005.1184 | 1221594.0143
17 | 2675054.0388 | 1221606.8683 | 2675050.0887 | 1221606.685 | 2675046.2953 | 1221606.1035 | 2675035.796 | 1221603.0915 | 2675029.6727 | 1221601.2797
18 | 2675005.1184 | 1221594.0143 | 2675002.0038 | 1221593.0927 | 2674990.079 | 1221585.8045 | 2674979.8111 | 1221582.2963
19 | 2675054.0388 | 1221606.8683 | 2675055.9522 | 1221598.309
20 | 2675059.7378 | 1221616.9578 | 2675055.4529 | 1221609.0319 | 2675054.0388 | 1221606.8683
21 | 2674963.0572 | 1221576.3888 | 2674971.3608 | 1221579.4091 | 2674979.8111 | 1221582.2963
22 | 2675055.9522 | 1221598.309 | 2675060.5269 | 1221594.0861 | 2675065.6753 | 1221586.3838
23 | 2675055.9522 | 1221598.309 | 2675066.3673 | 1221598.3736 | 2675093.5728 | 1221597.0823 | 2675101.7186 | 1221596.7213
24 | 2675059.7378 | 1221616.9578 | 2675066.4592 | 1221620.5671 | 2675068.7994 | 1221622.3301
25 | 2674963.0572 | 1221576.3888 | 2674945.2493 | 1221569.9115
26 | 2675065.6753 | 1221586.3838 | 2675072.1638 | 1221576.6769 | 2675078.84 | 1221567.1477
27 | 2674945.2493 | 1221569.9115 | 2674929.643 | 1221564.2349
28 | 2675103.8543 | 1221537.5879 | 2675101.065 | 1221540.1951 | 2675092.1601 | 1221547.2986 | 2675087.3209 | 1221555.0427 | 2675078.84 | 1221567.1477
29 | 2675117.9772 | 1221524.3869 | 2675103.8543 | 1221537.5879
30 | 2675117.9772 | 1221524.3869 | 2675116.5881 | 1221506.4131
31 | 2675116.5881 | 1221506.4131 | 2675087.963 | 1221505.3404 | 2675079.9615 | 1221505.1728 | 2675073.3439 | 1221499.3411 | 2675062.2676 | 1221507.1733
32 | 2675116.5881 | 1221506.4131 | 2675115.0247 | 1221495.6419 | 2675110.7754 | 1221471.4748
33 | 2675038.4944 | 1221349.2927 | 2675050.6348 | 1221333.502 | 2675053.7877 | 1221328.8958
34 | 2675051.9372 | 1221370.4171 | 2675051.686 | 1221370.3049

## bus_geodata
| x | y | coords
0 | 2675000.1251 | 1221499.7116
1 | 2674982.3529 | 1221514.3938
2 | 2674962.3566 | 1221482.68
3 | 2674979.4546 | 1221516.8256
4 | 2674943.7878 | 1221459.2391
5 | 2674946.006 | 1221522.2749
6 | 2674999.1884 | 1221540.4521
7 | 2675001.3614 | 1221383.9589
8 | 2674939.2516 | 1221530.3174
9 | 2675020.8431 | 1221564.4585
10 | 2675009.6937 | 1221377.1519
11 | 2675028.3694 | 1221359.8832
12 | 2674930.5229 | 1221540.9145
13 | 2674921.6177 | 1221561.3158
14 | 2675029.6727 | 1221601.2797
15 | 2675005.1184 | 1221594.0143
16 | 2675054.0388 | 1221606.8682
17 | 2674979.8111 | 1221582.2963
18 | 2675055.9522 | 1221598.309
19 | 2675059.7378 | 1221616.9578
20 | 2674963.0572 | 1221576.3888
21 | 2675065.6753 | 1221586.3838
22 | 2675101.7186 | 1221596.7213
23 | 2675068.7994 | 1221622.3301
24 | 2674945.2493 | 1221569.9115
25 | 2675078.84 | 1221567.1477
26 | 2675103.8543 | 1221537.5879
27 | 2675117.9772 | 1221524.3869
28 | 2675116.5881 | 1221506.4131
29 | 2675062.2676 | 1221507.1733
30 | 2675110.7754 | 1221471.4748
31 | 2674929.643 | 1221564.2349
32 | 2675038.4944 | 1221349.2927
33 | 2675051.686 | 1221370.3049
34 | 2675053.7877 | 1221328.8958
35 | 2675051.9372 | 1221370.4171
36 | 2674979.4546 | 1221516.8256

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99476 | -0.10012 | 0.069617 | 0.017448
1 | 0.99622 | -0.071891 | 0 | 0
2 | 0.99461 | -0.10298 | 0.024654 | 0.0061789
3 | 0.99662 | -0.064184 | 0 | 0
4 | 0.99401 | -0.11456 | 0 | 0
5 | 0.9932 | -0.12937 | 0 | 0
6 | 1 | 0 | -0.39322 | -0.099958
7 | 0.99191 | -0.1551 | 0 | 0
8 | 0.99242 | -0.14429 | 0.06646 | 0.016657
9 | 0.99914 | -0.016565 | 0.029371 | 0.0073611
10 | 0.99169 | -0.15929 | 0.0071722 | 0.0017975
11 | 0.99135 | -0.16597 | 0 | 0
12 | 0.99168 | -0.15844 | 0 | 0
13 | 0.99047 | -0.18146 | 0 | 0
14 | 0.98456 | -0.2952 | 0.0049299 | 0.0012355
15 | 0.98582 | -0.27098 | 0.0049967 | 0.0012523
16 | 0.98278 | -0.32981 | 0 | 0
17 | 0.98723 | -0.24366 | 0.0025919 | 0.00064958
18 | 0.9822 | -0.34102 | 0 | 0
19 | 0.98266 | -0.33222 | 0 | 0
20 | 0.98814 | -0.22614 | 0.0023829 | 0.0005972
21 | 0.9803 | -0.37799 | 0.024266 | 0.0060817
22 | 0.98179 | -0.34901 | 0.009657 | 0.0024203
23 | 0.98254 | -0.33443 | 0.01155 | 0.0028947
24 | 0.98913 | -0.20722 | 0.0036355 | 0.00091115
25 | 0.97797 | -0.4236 | 0.050218 | 0.012586
26 | 0.97587 | -0.46459 | 0.0052287 | 0.0013104
27 | 0.97493 | -0.48307 | 0 | 0
28 | 0.97406 | -0.50032 | 0 | 0
29 | 0.97141 | -0.55245 | 0.048057 | 0.012044
30 | 0.97392 | -0.50299 | 0.0040949 | 0.0010263
31 | 0.99001 | -0.19031 | 0.00318 | 0.000797
32 | 0.99127 | -0.16745 | 0 | 0
33 | 0.99114 | -0.17007 | 0.0058039 | 0.0014546
34 | 0.99114 | -0.17003 | 0.0057102 | 0.0014311
35 | 0.99114 | -0.17009 | 0.0032641 | 0.00081805
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.069617 | -0.017448 | 0.069711 | 0.017507 | 9.3748e-05 | 5.9699e-05 | 0.10414 | 0.10414 | 0.10414 | 0.99476 | -0.10012 | 0.99622 | -0.071891 | 28.6091
1 | 0.04674 | 0.011764 | -0.046671 | -0.01172 | 6.9337e-05 | 4.3883e-05 | 0.069832 | 0.069832 | 0.069832 | 0.99622 | -0.071891 | 0.99461 | -0.10298 | 19.1846
2 | -0.11645 | -0.029271 | 0.11649 | 0.029298 | 4.2867e-05 | 2.7386e-05 | 0.17397 | 0.17397 | 0.17397 | 0.99622 | -0.071891 | 0.99662 | -0.064184 | 47.7937
3 | 0.022017 | 0.0055409 | -0.022005 | -0.0055335 | 1.2173e-05 | 7.4031e-06 | 0.032947 | 0.032948 | 0.032948 | 0.99461 | -0.10298 | 0.99401 | -0.11456 | 9.0515
4 | 0.24456 | 0.062568 | -0.24379 | -0.062078 | 0.00076905 | 0.0004904 | 0.36559 | 0.3656 | 0.3656 | 0.99662 | -0.064184 | 0.9932 | -0.12937 | 33.4794
5 | -0.36105 | -0.091867 | 0.36217 | 0.092583 | 0.0011207 | 0.00071605 | 0.53956 | 0.53956 | 0.53956 | 0.99662 | -0.064184 | 1 | 0 | 49.4105
6 | 0.022005 | 0.0055335 | -0.021962 | -0.0055076 | 4.2528e-05 | 2.5867e-05 | 0.032948 | 0.032948 | 0.032948 | 0.99401 | -0.11456 | 0.99191 | -0.1551 | 9.0517
7 | 0.24379 | 0.062078 | -0.24361 | -0.061966 | 0.00017528 | 0.00011177 | 0.3656 | 0.3656 | 0.3656 | 0.9932 | -0.12937 | 0.99242 | -0.14429 | 33.4794
8 | 0.029394 | 0.0073755 | -0.029371 | -0.0073611 | 2.3198e-05 | 1.4423e-05 | 0.043742 | 0.043743 | 0.043743 | 1 | 0 | 0.99914 | -0.016565 | 12.0172
9 | 0.021962 | 0.0055076 | -0.021958 | -0.005505 | 4.38e-06 | 2.6644e-06 | 0.032948 | 0.032948 | 0.032948 | 0.99191 | -0.1551 | 0.99169 | -0.15929 | 9.0517
10 | 0.17715 | 0.04531 | -0.17703 | -0.045232 | 0.00012125 | 7.7071e-05 | 0.26595 | 0.26595 | 0.26595 | 0.99242 | -0.14429 | 0.99168 | -0.15844 | 24.3541
11 | 0.014786 | 0.0037074 | -0.014781 | -0.0037047 | 4.7036e-06 | 2.6817e-06 | 0.022186 | 0.022186 | 0.022186 | 0.99169 | -0.15929 | 0.99135 | -0.16597 | 6.0952
12 | 0.0057113 | 0.0014313 | -0.0057109 | -0.0014312 | 4.0327e-07 | 6.9442e-08 | 0.0085727 | 0.0085727 | 0.0085727 | 0.99135 | -0.16597 | 0.99127 | -0.16745 | 2.3551
13 | 0.0090697 | 0.0022734 | -0.0090679 | -0.0022726 | 1.775e-06 | 8.0681e-07 | 0.013614 | 0.013614 | 0.013614 | 0.99135 | -0.16597 | 0.99114 | -0.17007 | 3.7401
14 | 0.17703 | 0.045232 | -0.17684 | -0.045107 | 0.00019683 | 0.00012511 | 0.26595 | 0.26595 | 0.26595 | 0.99168 | -0.15844 | 0.99047 | -0.18146 | 24.3541
15 | 0.17684 | 0.045107 | -0.17676 | -0.045059 | 7.55e-05 | 4.799e-05 | 0.26595 | 0.26595 | 0.26595 | 0.99047 | -0.18146 | 0.99001 | -0.19031 | 24.3541
16 | -0.15913 | -0.040319 | 0.15932 | 0.040437 | 0.00018539 | 0.00011767 | 0.24066 | 0.24066 | 0.24066 | 0.98456 | -0.2952 | 0.98582 | -0.27098 | 22.0387
17 | 0.1542 | 0.039084 | -0.15395 | -0.03892 | 0.00025597 | 0.00016318 | 0.23321 | 0.23321 | 0.23321 | 0.98456 | -0.2952 | 0.98278 | -0.32981 | 32.0346
18 | -0.16432 | -0.041689 | 0.16453 | 0.041826 | 0.00021619 | 0.00013729 | 0.2482 | 0.2482 | 0.2482 | 0.98582 | -0.27098 | 0.98723 | -0.24366 | 22.7293
19 | 0.1424 | 0.036024 | -0.14232 | -0.035976 | 7.653e-05 | 4.8757e-05 | 0.21572 | 0.21572 | 0.21572 | 0.98278 | -0.32981 | 0.9822 | -0.34102 | 29.6319
20 | 0.011553 | 0.0028961 | -0.011551 | -0.0028954 | 1.3296e-06 | 7.0413e-07 | 0.017492 | 0.017492 | 0.017492 | 0.98278 | -0.32981 | 0.98266 | -0.33222 | 4.8055
21 | -0.16712 | -0.042476 | 0.16727 | 0.042566 | 0.00014115 | 8.9653e-05 | 0.25211 | 0.25211 | 0.25211 | 0.98723 | -0.24366 | 0.98814 | -0.22614 | 23.0871
22 | 0.13266 | 0.033554 | -0.13242 | -0.033403 | 0.00023488 | 0.00015013 | 0.20108 | 0.20108 | 0.20108 | 0.9822 | -0.34102 | 0.9803 | -0.37799 | 55.2429
23 | 0.0096607 | 0.0024221 | -0.009657 | -0.0024203 | 3.6796e-06 | 1.7755e-06 | 0.014636 | 0.014636 | 0.014636 | 0.9822 | -0.34102 | 0.98179 | -0.34901 | 4.021
24 | 0.011551 | 0.0028954 | -0.01155 | -0.0028947 | 1.2116e-06 | 6.4165e-07 | 0.017492 | 0.017492 | 0.017492 | 0.98266 | -0.33222 | 0.98254 | -0.33443 | 4.8055
25 | -0.16965 | -0.043163 | 0.1698 | 0.043261 | 0.00015487 | 9.8386e-05 | 0.2557 | 0.2557 | 0.2557 | 0.98814 | -0.22614 | 0.98913 | -0.20722 | 23.4156
26 | 0.10816 | 0.027322 | -0.10792 | -0.027171 | 0.00023583 | 0.00015064 | 0.16425 | 0.16425 | 0.16425 | 0.9803 | -0.37799 | 0.97797 | -0.4236 | 45.1237
27 | -0.17344 | -0.044172 | 0.17358 | 0.044262 | 0.00014159 | 8.9977e-05 | 0.26117 | 0.26117 | 0.26117 | 0.98913 | -0.20722 | 0.99001 | -0.19031 | 23.9164
28 | 0.057703 | 0.014585 | -0.05759 | -0.014513 | 0.0001132 | 7.1958e-05 | 0.087842 | 0.087842 | 0.087842 | 0.97797 | -0.4236 | 0.97587 | -0.46459 | 24.1324
29 | 0.052361 | 0.013203 | -0.052315 | -0.013174 | 4.6245e-05 | 2.9356e-05 | 0.079869 | 0.079869 | 0.079869 | 0.97587 | -0.46459 | 0.97493 | -0.48307 | 21.9421
30 | 0.052315 | 0.013174 | -0.052272 | -0.013146 | 4.3131e-05 | 2.7379e-05 | 0.079869 | 0.079869 | 0.079869 | 0.97493 | -0.48307 | 0.97406 | -0.50032 | 21.9421
31 | 0.048176 | 0.01212 | -0.048057 | -0.012044 | 0.00011966 | 7.5854e-05 | 0.073613 | 0.073613 | 0.073613 | 0.97406 | -0.50032 | 0.97141 | -0.55245 | 20.2235
32 | 0.0040954 | 0.0010262 | -0.0040949 | -0.0010263 | 5.1992e-07 | -1.081e-07 | 0.0062562 | 0.0062564 | 0.0062564 | 0.97406 | -0.50032 | 0.97392 | -0.50299 | 1.7188
33 | 0.0057109 | 0.0014312 | -0.0057102 | -0.0014311 | 7.0278e-07 | 1.2109e-07 | 0.0085727 | 0.0085728 | 0.0085728 | 0.99127 | -0.16745 | 0.99114 | -0.17003 | 2.3552
34 | 0.0032641 | 0.00081805 | -0.0032641 | -0.00081805 | 2.4775e-09 | -1.9595e-09 | 0.0049004 | 0.0049004 | 0.0049004 | 0.99114 | -0.17007 | 0.99114 | -0.17009 | 1.3463

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40288 | 0.10238

## res_load
| p_mw | q_mvar
0 | 0.069617 | 0.017448
1 | 0.024654 | 0.0061789
2 | 0.0096637 | 0.002422
3 | 0.06646 | 0.016657
4 | 0.029371 | 0.0073611
5 | 0.0071722 | 0.0017975
6 | 0.0049299 | 0.0012355
7 | 0.0049967 | 0.0012523
8 | 0.0025919 | 0.00064958
9 | 0.0023829 | 0.0005972
10 | 0.024266 | 0.0060817
11 | 0.009657 | 0.0024203
12 | 0.01155 | 0.0028947
13 | 0.0036355 | 0.00091115
14 | 0.050218 | 0.012586
15 | 0.0052287 | 0.0013104
16 | 0.048057 | 0.012044
17 | 0.0040949 | 0.0010263
18 | 0.00318 | 0.000797
19 | 0.0058039 | 0.0014546
20 | 0.0057102 | 0.0014311
21 | 0.0032641 | 0.00081805

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1