## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1708-12_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1708-12_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1708-12_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1708-12_0_8_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_1708-12_0_8_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_1708-12_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1708-12_0_8_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1708-12_0_8_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_1708-12_0_8_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1708-12_0_8_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1708-12_0_8_node_43 | 0.4 | n |  | TRUE
11 | bus_LV_1708-12_0_8_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1708-12_0_8_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_1708-12_0_8_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1708-12_0_8_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1708-12_0_8_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1708-12_0_8_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1708-12_0_8_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1708-12_0_8_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1708-12_0_8_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1708-12_0_8_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1708-12_0_8_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1708-12_0_8_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1708-12_0_8_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_1708-12_0_8_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_1708-12_0_8_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1708-12_0_8_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1708-12_0_8_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1708-12_0_8_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1708-12_0_8_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1708-12_0_8_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1708-12_0_8_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1708-12_0_8_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1708-12_0_8_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_1708-12_0_8_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_1708-12_0_8_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1708-12_0_8_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1708-12_0_8_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_1708-12_0_8_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1708-12_0_8_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_1708-12_0_8_node_41 | 0.4 | n |  | TRUE
41 | bus_MV_231_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1708-12_0_8_load_0 | 0 | 0.0052171 | 0.0013075 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1708-12_0_8_load_12 | 3 | 0.037773 | 0.0094667 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1708-12_0_8_load_10 | 4 | 0.027738 | 0.0069517 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1708-12_0_8_load_4 | 6 | 0.010025 | 0.0025125 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1708-12_0_8_load_3 | 7 | 0.014203 | 0.0035597 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1708-12_0_8_load_43 | 10 | 0.075637 | 0.018956 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1708-12_0_8_load_7 | 13 | 0.02562 | 0.006421 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1708-12_0_8_load_8 | 14 | 0.0039472 | 0.00098926 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1708-12_0_8_load_13 | 16 | 0.021771 | 0.0054563 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1708-12_0_8_load_11 | 17 | 0.0068423 | 0.0017148 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1708-12_0_8_load_14 | 18 | 0.011565 | 0.0028986 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1708-12_0_8_load_17 | 20 | 0.05683 | 0.014243 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1708-12_0_8_load_18 | 21 | 0.075637 | 0.018957 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1708-12_0_8_load_31 | 23 | 0.014473 | 0.0036272 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1708-12_0_8_load_32 | 24 | 0.051983 | 0.013028 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1708-12_0_8_load_20 | 25 | 0.019165 | 0.0048033 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1708-12_0_8_load_27 | 29 | 0.0076154 | 0.0019086 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1708-12_0_8_load_23 | 31 | 0.014462 | 0.0036244 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1708-12_0_8_load_40 | 33 | 0.031449 | 0.007882 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1708-12_0_8_load_37 | 34 | 0.026303 | 0.006592 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1708-12_0_8_load_33 | 35 | 0.025972 | 0.0065092 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1708-12_0_8_load_35 | 37 | 0.010582 | 0.0026521 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1708-12_0_8_load_41 | 40 | 0.029258 | 0.0073327 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1708-12_0_8_line_0 |  | 0 | 1 | 0.020654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1708-12_0_8_line_1 |  | 1 | 2 | 0.030875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1708-12_0_8_line_2 |  | 2 | 5 | 0.054134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1708-12_0_8_line_3 |  | 3 | 4 | 0.0081603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1708-12_0_8_line_4 |  | 4 | 15 | 0.093832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1708-12_0_8_line_5 |  | 5 | 8 | 0.10171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1708-12_0_8_line_6 |  | 5 | 7 | 0.033702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1708-12_0_8_line_7 |  | 6 | 7 | 0.0398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1708-12_0_8_line_8 |  | 8 | 9 | 0.061905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1708-12_0_8_line_9 |  | 8 | 10 | 0.075386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1708-12_0_8_line_10 |  | 9 | 11 | 0.036457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1708-12_0_8_line_11 |  | 10 | 12 | 0.067369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1708-12_0_8_line_12 |  | 11 | 18 | 0.037121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1708-12_0_8_line_13 |  | 12 | 21 | 0.031563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1708-12_0_8_line_14 |  | 13 | 14 | 0.016446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1708-12_0_8_line_15 |  | 13 | 15 | 0.039937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1708-12_0_8_line_16 |  | 14 | 16 | 0.16478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1708-12_0_8_line_17 |  | 15 | 17 | 0.063802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1708-12_0_8_line_18 |  | 16 | 18 | 0.0477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1708-12_0_8_line_19 |  | 17 | 22 | 0.034146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1708-12_0_8_line_20 |  | 19 | 20 | 0.029684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1708-12_0_8_line_21 |  | 19 | 21 | 0.035779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1708-12_0_8_line_22 |  | 22 | 23 | 0.084677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1708-12_0_8_line_23 |  | 22 | 24 | 0.041152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1708-12_0_8_line_24 |  | 23 | 27 | 0.057472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1708-12_0_8_line_25 |  | 24 | 32 | 0.039014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1708-12_0_8_line_26 |  | 25 | 26 | 0.081633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1708-12_0_8_line_27 |  | 26 | 27 | 0.10155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1708-12_0_8_line_28 |  | 27 | 28 | 0.005169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1708-12_0_8_line_29 |  | 28 | 29 | 0.15838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1708-12_0_8_line_30 |  | 28 | 30 | 0.002054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1708-12_0_8_line_31 |  | 30 | 31 | 0.031113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1708-12_0_8_line_32 |  | 32 | 33 | 0.084808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1708-12_0_8_line_33 |  | 32 | 34 | 0.027888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1708-12_0_8_line_34 |  | 33 | 40 | 0.010872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1708-12_0_8_line_35 |  | 34 | 39 | 0.003546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1708-12_0_8_line_36 |  | 35 | 36 | 0.060347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1708-12_0_8_line_37 |  | 36 | 37 | 0.0058098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1708-12_0_8_line_38 |  | 37 | 38 | 0.028783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1708-12_0_8_line_39 |  | 38 | 39 | 0.042584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1708-12_0_8_trafo_7 | 0.63 MVA 20/0.4 kV | 41 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2678810.2838 | 1226932.7322 | 2678811.98 | 1226946.5863 | 2678811.5627 | 1226953.2695
1 | 2678810.2838 | 1226932.7322 | 2678840.9679 | 1226928.5803
2 | 2678840.9679 | 1226928.5803 | 2678843.4129 | 1226913.9584 | 2678881.5347 | 1226903.9457
3 | 2678950.2444 | 1227136.8367 | 2678942.0842 | 1227136.7828
4 | 2679041.1515 | 1227128.8154 | 2679004.6285 | 1227127.5406 | 2678990.3281 | 1227137.1017 | 2678950.2444 | 1227136.8367
5 | 2678881.5347 | 1226903.9457 | 2678881.7687 | 1226881.7338 | 2678878.8416 | 1226854.977 | 2678881.6415 | 1226854.1802 | 2678884.9968 | 1226853.224 | 2678886.0768 | 1226844.3768 | 2678902.8441 | 1226846.0113 | 2678902.021 | 1226854.9175 | 2678904.9276 | 1226855.2229 | 2678906.2252 | 1226863.6792
6 | 2678881.5347 | 1226903.9457 | 2678877.1144 | 1226937.3563
7 | 2678877.1144 | 1226937.3563 | 2678871.8943 | 1226976.8121
8 | 2678899.8676 | 1226925.2475 | 2678906.2252 | 1226863.6792
9 | 2678906.2252 | 1226863.6792 | 2678908.0515 | 1226857.4214 | 2678910.3429 | 1226852.6819 | 2678917.3703 | 1226848.6057 | 2678969.2209 | 1226828.8729
10 | 2678899.8676 | 1226925.2475 | 2678897.0418 | 1226952.573 | 2678898.0283 | 1226959.9132 | 2678898.3109 | 1226961.4625
11 | 2679032.1844 | 1226804.9109 | 2678969.2209 | 1226828.8729
12 | 2678898.3109 | 1226961.4625 | 2678908.7205 | 1226968.672 | 2678918.2196 | 1226969.6653 | 2678932.7306 | 1226966.2483
13 | 2679032.1844 | 1226804.9109 | 2679043.5949 | 1226834.3393
14 | 2679061.1783 | 1227094.4471 | 2679073.2289 | 1227083.2552
15 | 2679041.1515 | 1227128.8154 | 2679042.2437 | 1227125.9057 | 2679050.6986 | 1227109.0733 | 2679061.1783 | 1227094.4471
16 | 2679073.2289 | 1227083.2552 | 2678977.3061 | 1226949.2729
17 | 2679041.1515 | 1227128.8154 | 2679031.9664 | 1227151.5532 | 2679018.074 | 1227188.2931
18 | 2678977.3061 | 1226949.2729 | 2678932.97 | 1226966.1919 | 2678932.7306 | 1226966.2483
19 | 2679005.9968 | 1227220.2325 | 2679018.074 | 1227188.2931
20 | 2679056.5297 | 1226867.6989 | 2679028.6659 | 1226877.9344
21 | 2679056.5297 | 1226867.6989 | 2679043.5949 | 1226834.3393
22 | 2679005.9968 | 1227220.2325 | 2678977.0585 | 1227298.479 | 2678976.629 | 1227299.6539
23 | 2679005.9968 | 1227220.2325 | 2679044.6373 | 1227234.3872
24 | 2678957.0065 | 1227353.6725 | 2678965.3714 | 1227330.4455 | 2678976.629 | 1227299.6539
25 | 2679081.2707 | 1227247.8066 | 2679044.6373 | 1227234.3872
26 | 2678859.6031 | 1227324.9059 | 2678859.995 | 1227316.5054 | 2678860.2484 | 1227273.3908 | 2678863.4572 | 1227243.4541
27 | 2678859.6031 | 1227324.9059 | 2678886.2393 | 1227336.0887 | 2678909.884 | 1227342.5177 | 2678948.0121 | 1227351.2404 | 2678957.0065 | 1227353.6725
28 | 2678957.0065 | 1227353.6725 | 2678954.5661 | 1227358.2321
29 | 2678954.5661 | 1227358.2321 | 2678960.9344 | 1227361.5188 | 2678999.4 | 1227384.7561 | 2679008.4807 | 1227390.3805 | 2679011.5821 | 1227396.5369 | 2679014.7769 | 1227412.7792 | 2679016.7609 | 1227428.305 | 2679017.2437 | 1227441.02 | 2679013.9428 | 1227477.8344 | 2679012.1116 | 1227484.3955
30 | 2678953.5947 | 1227360.0426 | 2678954.5661 | 1227358.2321
31 | 2678953.5947 | 1227360.0426 | 2678949.3424 | 1227357.7958 | 2678940.9002 | 1227355.4489 | 2678923.8358 | 1227351.3877
32 | 2679081.2707 | 1227247.8066 | 2679052.8556 | 1227327.7128
33 | 2679081.2707 | 1227247.8066 | 2679107.5875 | 1227257.0345
34 | 2679050.0188 | 1227338.1476 | 2679050.4931 | 1227334.3561 | 2679052.8556 | 1227327.7128
35 | 2679110.9337 | 1227258.2079 | 2679107.5875 | 1227257.0345
36 | 2679161.6706 | 1227298.4876 | 2679144.1147 | 1227340.8271 | 2679139.1824 | 1227354.4754
37 | 2679161.6706 | 1227298.4876 | 2679156.4445 | 1227295.9497
38 | 2679151.2025 | 1227272.3974 | 2679148.6992 | 1227277.1117 | 2679154.8955 | 1227280.7855 | 2679157.5518 | 1227284.5011 | 2679157.9716 | 1227290.5441 | 2679156.4445 | 1227295.9497
39 | 2679110.9337 | 1227258.2079 | 2679151.2025 | 1227272.3974

## bus_geodata
| x | y | coords
0 | 2678811.5627 | 1226953.2695
1 | 2678810.2838 | 1226932.7322
2 | 2678840.9679 | 1226928.5803
3 | 2678942.0842 | 1227136.7828
4 | 2678950.2444 | 1227136.8367
5 | 2678881.5347 | 1226903.9457
6 | 2678871.8943 | 1226976.8121
7 | 2678877.1144 | 1226937.3563
8 | 2678906.2252 | 1226863.6792
9 | 2678899.8676 | 1226925.2475
10 | 2678969.2209 | 1226828.8729
11 | 2678898.3109 | 1226961.4625
12 | 2679032.1844 | 1226804.9109
13 | 2679061.1783 | 1227094.4471
14 | 2679073.2289 | 1227083.2552
15 | 2679041.1515 | 1227128.8154
16 | 2678977.3061 | 1226949.2729
17 | 2679018.0739 | 1227188.2931
18 | 2678932.7306 | 1226966.2483
19 | 2679056.5297 | 1226867.6989
20 | 2679028.6659 | 1226877.9344
21 | 2679043.5949 | 1226834.3393
22 | 2679005.9968 | 1227220.2325
23 | 2678976.629 | 1227299.6539
24 | 2679044.6373 | 1227234.3872
25 | 2678863.4572 | 1227243.4541
26 | 2678859.6031 | 1227324.9059
27 | 2678957.0065 | 1227353.6725
28 | 2678954.5661 | 1227358.2321
29 | 2679012.1116 | 1227484.3955
30 | 2678953.5947 | 1227360.0426
31 | 2678923.8358 | 1227351.3877
32 | 2679081.2707 | 1227247.8066
33 | 2679052.8556 | 1227327.7128
34 | 2679107.5875 | 1227257.0345
35 | 2679139.1824 | 1227354.4754
36 | 2679161.6706 | 1227298.4876
37 | 2679156.4445 | 1227295.9497
38 | 2679151.2024 | 1227272.3974
39 | 2679110.9337 | 1227258.2079
40 | 2679050.0188 | 1227338.1476
41 | 2679041.1515 | 1227128.8154

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97496 | -0.48015 | 0.0052171 | 0.0013075
1 | 0.97506 | -0.47818 | 0 | 0
2 | 0.97521 | -0.47522 | 0 | 0
3 | 0.9913 | -0.16681 | 0.037773 | 0.0094667
4 | 0.99158 | -0.16135 | 0.027738 | 0.0069517
5 | 0.97548 | -0.47005 | 0 | 0
6 | 0.97435 | -0.49234 | 0.010025 | 0.0025125
7 | 0.97472 | -0.48502 | 0.014203 | 0.0035597
8 | 0.97826 | -0.41533 | 0 | 0
9 | 0.98169 | -0.3486 | 0 | 0
10 | 0.9746 | -0.48704 | 0.075637 | 0.018956
11 | 0.98371 | -0.30951 | 0 | 0
12 | 0.97252 | -0.52807 | 0 | 0
13 | 1 | 0 | -0.59127 | -0.15207
14 | 0.99895 | -0.019722 | 0.0039472 | 0.00098926
15 | 0.9972 | -0.052992 | 0 | 0
16 | 0.98854 | -0.21673 | 0.021771 | 0.0054563
17 | 0.99369 | -0.1198 | 0.0068423 | 0.0017148
18 | 0.98577 | -0.26988 | 0.011565 | 0.0028986
19 | 0.97107 | -0.55674 | 0 | 0
20 | 0.97028 | -0.57235 | 0.05683 | 0.014243
21 | 0.97155 | -0.54735 | 0.075637 | 0.018957
22 | 0.99003 | -0.18977 | 0 | 0
23 | 0.98568 | -0.27405 | 0.014473 | 0.0036272
24 | 0.98669 | -0.25422 | 0.051983 | 0.013028
25 | 0.98024 | -0.38016 | 0.019165 | 0.0048033
26 | 0.98169 | -0.35182 | 0 | 0
27 | 0.98349 | -0.31668 | 0 | 0
28 | 0.98338 | -0.31874 | 0 | 0
29 | 0.98227 | -0.34051 | 0.0076154 | 0.0019086
30 | 0.98336 | -0.31928 | 0 | 0
31 | 0.98294 | -0.32739 | 0.014462 | 0.0036244
32 | 0.98222 | -0.34092 | 0 | 0
33 | 0.97744 | -0.43439 | 0.031449 | 0.007882
34 | 0.98059 | -0.37264 | 0.026303 | 0.006592
35 | 0.97646 | -0.45377 | 0.025972 | 0.0065092
36 | 0.97791 | -0.42516 | 0 | 0
37 | 0.97805 | -0.42241 | 0.010582 | 0.0026521
38 | 0.97903 | -0.40326 | 0 | 0
39 | 0.98047 | -0.37499 | 0 | 0
40 | 0.97715 | -0.44019 | 0.029258 | 0.0073327
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0052171 | -0.0013075 | 0.0052176 | 0.0013076 | 4.9104e-07 | 5.6674e-08 | 0.0079624 | 0.0079623 | 0.0079624 | 0.97496 | -0.48015 | 0.97506 | -0.47818 | 2.1875
1 | -0.0052176 | -0.0013076 | 0.0052183 | 0.0013077 | 7.3403e-07 | 8.4609e-08 | 0.0079623 | 0.0079622 | 0.0079623 | 0.97506 | -0.47818 | 0.97521 | -0.47522 | 2.1875
2 | -0.0052183 | -0.0013077 | 0.0052196 | 0.0013078 | 1.2869e-06 | 1.4802e-07 | 0.0079622 | 0.007962 | 0.0079622 | 0.97521 | -0.47522 | 0.97548 | -0.47005 | 2.1874
3 | -0.037773 | -0.0094667 | 0.037783 | 0.0094729 | 9.8379e-06 | 6.1911e-06 | 0.0567 | 0.0567 | 0.0567 | 0.9913 | -0.16681 | 0.99158 | -0.16135 | 15.5769
4 | -0.06552 | -0.016425 | 0.06586 | 0.016641 | 0.00034018 | 0.0002165 | 0.098325 | 0.098324 | 0.098325 | 0.99158 | -0.16135 | 0.9972 | -0.052992 | 27.0123
5 | -0.029469 | -0.0073925 | 0.029546 | 0.0074405 | 7.7082e-05 | 4.8059e-05 | 0.044955 | 0.044955 | 0.044955 | 0.97548 | -0.47005 | 0.97826 | -0.41533 | 12.3503
6 | 0.024249 | 0.0060846 | -0.024232 | -0.006074 | 1.7295e-05 | 1.0649e-05 | 0.036993 | 0.036993 | 0.036993 | 0.97548 | -0.47005 | 0.97472 | -0.48502 | 10.163
7 | -0.010025 | -0.0025125 | 0.010029 | 0.0025143 | 3.4984e-06 | 1.7431e-06 | 0.01531 | 0.01531 | 0.01531 | 0.97435 | -0.49234 | 0.97472 | -0.48502 | 4.2061
8 | -0.23882 | -0.060332 | 0.23958 | 0.060819 | 0.00076656 | 0.00048748 | 0.36343 | 0.36343 | 0.36343 | 0.97826 | -0.41533 | 0.98169 | -0.3486 | 24.961
9 | 0.20927 | 0.052891 | -0.20855 | -0.052436 | 0.00071684 | 0.000455 | 0.31848 | 0.31848 | 0.31848 | 0.97826 | -0.41533 | 0.9746 | -0.48704 | 21.8736
10 | -0.23958 | -0.060819 | 0.24004 | 0.061107 | 0.00045144 | 0.00028707 | 0.36343 | 0.36343 | 0.36343 | 0.98169 | -0.3486 | 0.98371 | -0.30951 | 24.961
11 | 0.13292 | 0.03348 | -0.13266 | -0.033317 | 0.00026026 | 0.00016322 | 0.203 | 0.203 | 0.203 | 0.9746 | -0.48704 | 0.97252 | -0.52807 | 13.9422
12 | -0.24004 | -0.061107 | 0.2405 | 0.061399 | 0.00045966 | 0.00029229 | 0.36343 | 0.36343 | 0.36343 | 0.98371 | -0.30951 | 0.98577 | -0.26988 | 24.9609
13 | 0.13266 | 0.033317 | -0.13254 | -0.03324 | 0.00012194 | 7.6475e-05 | 0.203 | 0.203 | 0.203 | 0.97252 | -0.52807 | 0.97155 | -0.54735 | 13.9423
14 | 0.28134 | 0.073012 | -0.28107 | -0.072839 | 0.00027137 | 0.00017282 | 0.41953 | 0.41953 | 0.41953 | 1 | 0 | 0.99895 | -0.019722 | 28.8141
15 | 0.30827 | 0.079055 | -0.30748 | -0.078552 | 0.00079003 | 0.00050353 | 0.45935 | 0.45935 | 0.45935 | 1 | 0 | 0.9972 | -0.052992 | 31.5489
16 | 0.27712 | 0.07185 | -0.27448 | -0.070166 | 0.0026433 | 0.0016832 | 0.41365 | 0.41366 | 0.41366 | 0.99895 | -0.019722 | 0.98854 | -0.21673 | 28.4105
17 | 0.24162 | 0.06191 | -0.24084 | -0.061415 | 0.00077963 | 0.00049565 | 0.36103 | 0.36103 | 0.36103 | 0.9972 | -0.052992 | 0.99369 | -0.1198 | 24.796
18 | 0.25271 | 0.06471 | -0.25206 | -0.064297 | 0.00064877 | 0.00041277 | 0.38089 | 0.38089 | 0.38089 | 0.98854 | -0.21673 | 0.98577 | -0.26988 | 26.1599
19 | 0.234 | 0.0597 | -0.23321 | -0.059197 | 0.00078782 | 0.00050332 | 0.35078 | 0.35078 | 0.35078 | 0.99369 | -0.1198 | 0.99003 | -0.18977 | 48.1847
20 | 0.056872 | 0.014269 | -0.05683 | -0.014243 | 4.2277e-05 | 2.6323e-05 | 0.087154 | 0.087154 | 0.087154 | 0.97107 | -0.55674 | 0.97028 | -0.57235 | 11.9717
21 | -0.056872 | -0.014269 | 0.056898 | 0.014284 | 2.5479e-05 | 1.4535e-05 | 0.087154 | 0.087153 | 0.087154 | 0.97107 | -0.55674 | 0.97155 | -0.54735 | 5.9858
22 | 0.0561 | 0.014203 | -0.055874 | -0.014059 | 0.00022603 | 0.00014357 | 0.084368 | 0.084369 | 0.084369 | 0.99003 | -0.18977 | 0.98568 | -0.27405 | 23.1782
23 | 0.17711 | 0.044994 | -0.17657 | -0.044644 | 0.00054766 | 0.00034945 | 0.26642 | 0.26642 | 0.26642 | 0.99003 | -0.18977 | 0.98669 | -0.25422 | 36.5957
24 | 0.041401 | 0.010432 | -0.041317 | -0.010379 | 8.4243e-05 | 5.3185e-05 | 0.06252 | 0.062521 | 0.062521 | 0.98568 | -0.27405 | 0.98349 | -0.31668 | 17.176
25 | 0.12458 | 0.031616 | -0.12407 | -0.031286 | 0.00051721 | 0.00033052 | 0.18802 | 0.18802 | 0.18802 | 0.98669 | -0.25422 | 0.98222 | -0.34092 | 51.6543
26 | -0.019165 | -0.0048033 | 0.019191 | 0.0048189 | 2.5911e-05 | 1.5552e-05 | 0.029093 | 0.029093 | 0.029093 | 0.98024 | -0.38016 | 0.98169 | -0.35182 | 7.9927
27 | -0.019191 | -0.0048189 | 0.019224 | 0.0048382 | 3.2231e-05 | 1.9342e-05 | 0.029093 | 0.029093 | 0.029093 | 0.98169 | -0.35182 | 0.98349 | -0.31668 | 7.9926
28 | 0.022093 | 0.0055408 | -0.022091 | -0.0055395 | 2.166e-06 | 1.3207e-06 | 0.033428 | 0.033428 | 0.033428 | 0.98349 | -0.31668 | 0.98338 | -0.31874 | 9.1835
29 | 0.0076233 | 0.0019117 | -0.0076154 | -0.0019086 | 7.9042e-06 | 3.0515e-06 | 0.011536 | 0.011536 | 0.011536 | 0.98338 | -0.31874 | 0.98227 | -0.34051 | 3.1693
30 | 0.014468 | 0.0036278 | -0.014467 | -0.0036276 | 3.6916e-07 | 2.1021e-07 | 0.021892 | 0.021892 | 0.021892 | 0.98338 | -0.31874 | 0.98336 | -0.31928 | 6.0144
31 | 0.014467 | 0.0036276 | -0.014462 | -0.0036244 | 5.5919e-06 | 3.1843e-06 | 0.021892 | 0.021893 | 0.021893 | 0.98336 | -0.31928 | 0.98294 | -0.32739 | 6.0144
32 | 0.060987 | 0.015393 | -0.060715 | -0.01522 | 0.00027171 | 0.00017283 | 0.092431 | 0.092431 | 0.092431 | 0.98222 | -0.34092 | 0.97744 | -0.43439 | 25.3933
33 | 0.063078 | 0.015893 | -0.062983 | -0.015832 | 9.556e-05 | 6.0806e-05 | 0.095591 | 0.095591 | 0.095591 | 0.98222 | -0.34092 | 0.98059 | -0.37264 | 26.2612
34 | 0.029266 | 0.0073377 | -0.029258 | -0.0073327 | 8.0932e-06 | 5.0434e-06 | 0.044554 | 0.044554 | 0.044554 | 0.97744 | -0.43439 | 0.97715 | -0.44019 | 12.2402
35 | 0.03668 | 0.0092401 | -0.036676 | -0.0092376 | 4.1222e-06 | 2.5935e-06 | 0.055678 | 0.055678 | 0.055678 | 0.98059 | -0.37264 | 0.98047 | -0.37499 | 15.296
36 | -0.025972 | -0.0065092 | 0.026007 | 0.0065311 | 3.5449e-05 | 2.1931e-05 | 0.039578 | 0.039578 | 0.039578 | 0.97646 | -0.45377 | 0.97791 | -0.42516 | 10.8732
37 | -0.026007 | -0.0065311 | 0.026011 | 0.0065332 | 3.4127e-06 | 2.1112e-06 | 0.039578 | 0.039578 | 0.039578 | 0.97791 | -0.42516 | 0.97805 | -0.42241 | 10.8731
38 | -0.036593 | -0.0091854 | 0.036626 | 0.0092064 | 3.3461e-05 | 2.1053e-05 | 0.055678 | 0.055678 | 0.055678 | 0.97805 | -0.42241 | 0.97903 | -0.40326 | 15.2961
39 | -0.036626 | -0.0092064 | 0.036676 | 0.0092376 | 4.9504e-05 | 3.1146e-05 | 0.055678 | 0.055678 | 0.055678 | 0.97903 | -0.40326 | 0.98047 | -0.37499 | 15.2961

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61689 | 0.15849

## res_load
| p_mw | q_mvar
0 | 0.0052171 | 0.0013075
1 | 0.037773 | 0.0094667
2 | 0.027738 | 0.0069517
3 | 0.010025 | 0.0025125
4 | 0.014203 | 0.0035597
5 | 0.075637 | 0.018956
6 | 0.02562 | 0.006421
7 | 0.0039472 | 0.00098926
8 | 0.021771 | 0.0054563
9 | 0.0068423 | 0.0017148
10 | 0.011565 | 0.0028986
11 | 0.05683 | 0.014243
12 | 0.075637 | 0.018957
13 | 0.014473 | 0.0036272
14 | 0.051983 | 0.013028
15 | 0.019165 | 0.0048033
16 | 0.0076154 | 0.0019086
17 | 0.014462 | 0.0036244
18 | 0.031449 | 0.007882
19 | 0.026303 | 0.006592
20 | 0.025972 | 0.0065092
21 | 0.010582 | 0.0026521
22 | 0.029258 | 0.0073327

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1