## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_191-11_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_191-11_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_191-11_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_191-11_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_191-11_0_5_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_191-11_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_191-11_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_191-11_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_191-11_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_191-11_0_5_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_191-11_0_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_191-11_0_5_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_191-11_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_191-11_0_5_node_112 | 0.4 | n |  | TRUE
14 | bus_LV_191-11_0_5_node_111 | 0.4 | n |  | TRUE
15 | bus_LV_191-11_0_5_node_108 | 0.4 | n |  | TRUE
16 | bus_LV_191-11_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_191-11_0_5_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_191-11_0_5_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_191-11_0_5_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_191-11_0_5_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_191-11_0_5_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_191-11_0_5_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_191-11_0_5_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_191-11_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_191-11_0_5_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_191-11_0_5_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_191-11_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_191-11_0_5_node_73 | 0.4 | n |  | TRUE
29 | bus_LV_191-11_0_5_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_191-11_0_5_node_93 | 0.4 | n |  | TRUE
31 | bus_LV_191-11_0_5_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_191-11_0_5_node_158 | 0.4 | n |  | TRUE
33 | bus_LV_191-11_0_5_node_110 | 0.4 | n |  | TRUE
34 | bus_LV_191-11_0_5_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_191-11_0_5_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_191-11_0_5_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_191-11_0_5_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_191-11_0_5_node_98 | 0.4 | n |  | TRUE
39 | bus_LV_191-11_0_5_node_106 | 0.4 | n |  | TRUE
40 | bus_LV_191-11_0_5_node_95 | 0.4 | n |  | TRUE
41 | bus_LV_191-11_0_5_node_92 | 0.4 | n |  | TRUE
42 | bus_LV_191-11_0_5_node_156 | 0.4 | n |  | TRUE
43 | bus_LV_191-11_0_5_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_191-11_0_5_node_75 | 0.4 | n |  | TRUE
45 | bus_LV_191-11_0_5_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_191-11_0_5_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_191-11_0_5_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_191-11_0_5_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_191-11_0_5_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_191-11_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_191-11_0_5_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_191-11_0_5_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_191-11_0_5_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_191-11_0_5_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_191-11_0_5_node_55 | 0.4 | n |  | TRUE
56 | bus_LV_191-11_0_5_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_191-11_0_5_node_102 | 0.4 | n |  | TRUE
58 | bus_LV_191-11_0_5_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_191-11_0_5_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_191-11_0_5_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_191-11_0_5_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_191-11_0_5_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_191-11_0_5_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_191-11_0_5_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_191-11_0_5_node_149 | 0.4 | n |  | TRUE
66 | bus_LV_191-11_0_5_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_191-11_0_5_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_191-11_0_5_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_191-11_0_5_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_191-11_0_5_node_68 | 0.4 | n |  | TRUE
71 | bus_LV_191-11_0_5_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_191-11_0_5_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_191-11_0_5_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_191-11_0_5_node_159 | 0.4 | n |  | TRUE
75 | bus_LV_191-11_0_5_node_152 | 0.4 | n |  | TRUE
76 | bus_LV_191-11_0_5_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_191-11_0_5_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_191-11_0_5_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_191-11_0_5_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_191-11_0_5_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_191-11_0_5_node_61 | 0.4 | n |  | TRUE
82 | bus_LV_191-11_0_5_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_191-11_0_5_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_191-11_0_5_node_70 | 0.4 | n |  | TRUE
85 | bus_LV_191-11_0_5_node_155 | 0.4 | n |  | TRUE
86 | bus_LV_191-11_0_5_node_161 | 0.4 | n |  | TRUE
87 | bus_LV_191-11_0_5_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_191-11_0_5_node_153 | 0.4 | n |  | TRUE
89 | bus_LV_191-11_0_5_node_160 | 0.4 | n |  | TRUE
90 | bus_LV_191-11_0_5_node_150 | 0.4 | n |  | TRUE
91 | bus_LV_191-11_0_5_node_151 | 0.4 | n |  | TRUE
92 | bus_LV_191-11_0_5_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_191-11_0_5_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_191-11_0_5_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_191-11_0_5_node_80 | 0.4 | n |  | TRUE
96 | bus_LV_191-11_0_5_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_191-11_0_5_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_191-11_0_5_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_191-11_0_5_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_191-11_0_5_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_191-11_0_5_node_117 | 0.4 | n |  | TRUE
102 | bus_LV_191-11_0_5_node_135 | 0.4 | n |  | TRUE
103 | bus_LV_191-11_0_5_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_191-11_0_5_node_86 | 0.4 | n |  | TRUE
105 | bus_LV_191-11_0_5_node_87 | 0.4 | n |  | TRUE
106 | bus_LV_191-11_0_5_node_88 | 0.4 | n |  | TRUE
107 | bus_LV_191-11_0_5_node_89 | 0.4 | n |  | TRUE
108 | bus_LV_191-11_0_5_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_191-11_0_5_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_191-11_0_5_node_115 | 0.4 | n |  | TRUE
111 | bus_LV_191-11_0_5_node_134 | 0.4 | n |  | TRUE
112 | bus_LV_191-11_0_5_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_191-11_0_5_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_191-11_0_5_node_97 | 0.4 | n |  | TRUE
115 | bus_LV_191-11_0_5_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_191-11_0_5_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_191-11_0_5_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_191-11_0_5_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_191-11_0_5_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_191-11_0_5_node_144 | 0.4 | n |  | TRUE
121 | bus_LV_191-11_0_5_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_191-11_0_5_node_143 | 0.4 | n |  | TRUE
123 | bus_LV_191-11_0_5_node_137 | 0.4 | n |  | TRUE
124 | bus_LV_191-11_0_5_node_138 | 0.4 | n |  | TRUE
125 | bus_LV_191-11_0_5_node_141 | 0.4 | n |  | TRUE
126 | bus_LV_191-11_0_5_node_122 | 0.4 | n |  | TRUE
127 | bus_LV_191-11_0_5_node_142 | 0.4 | n |  | TRUE
128 | bus_LV_191-11_0_5_node_124 | 0.4 | n |  | TRUE
129 | bus_LV_191-11_0_5_node_121 | 0.4 | n |  | TRUE
130 | bus_LV_191-11_0_5_node_113 | 0.4 | n |  | TRUE
131 | bus_LV_191-11_0_5_node_114 | 0.4 | n |  | TRUE
132 | bus_LV_191-11_0_5_node_116 | 0.4 | n |  | TRUE
133 | bus_LV_191-11_0_5_node_118 | 0.4 | n |  | TRUE
134 | bus_LV_191-11_0_5_node_119 | 0.4 | n |  | TRUE
135 | bus_LV_191-11_0_5_node_120 | 0.4 | n |  | TRUE
136 | bus_LV_191-11_0_5_node_123 | 0.4 | n |  | TRUE
137 | bus_LV_191-11_0_5_node_125 | 0.4 | n |  | TRUE
138 | bus_LV_191-11_0_5_node_132 | 0.4 | n |  | TRUE
139 | bus_LV_191-11_0_5_node_136 | 0.4 | n |  | TRUE
140 | bus_LV_191-11_0_5_node_130 | 0.4 | n |  | TRUE
141 | bus_LV_191-11_0_5_node_126 | 0.4 | n |  | TRUE
142 | bus_LV_191-11_0_5_node_127 | 0.4 | n |  | TRUE
143 | bus_LV_191-11_0_5_node_128 | 0.4 | n |  | TRUE
144 | bus_LV_191-11_0_5_node_129 | 0.4 | n |  | TRUE
145 | bus_LV_191-11_0_5_node_131 | 0.4 | n |  | TRUE
146 | bus_LV_191-11_0_5_node_133 | 0.4 | n |  | TRUE
147 | bus_LV_191-11_0_5_node_139 | 0.4 | n |  | TRUE
148 | bus_LV_191-11_0_5_node_140 | 0.4 | n |  | TRUE
149 | bus_LV_191-11_0_5_node_145 | 0.4 | n |  | TRUE
150 | bus_LV_191-11_0_5_node_154 | 0.4 | n |  | TRUE
151 | bus_MV_365_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_191-11_0_5_load_0 | 0 | 0.0070574 | 0.0017687 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_191-11_0_5_load_1 | 1 | 0.0052543 | 0.0013169 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_191-11_0_5_load_7 | 5 | 0.004218 | 0.0010571 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_191-11_0_5_load_9 | 8 | 0.042385 | 0.010623 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_191-11_0_5_load_12 | 9 | 0.035527 | 0.0089039 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_191-11_0_5_load_112 | 13 | 0.039384 | 0.0098706 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_191-11_0_5_load_111 | 14 | 0.02002 | 0.0050176 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_191-11_0_5_load_14 | 16 | 0.0063979 | 0.0016035 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_191-11_0_5_load_15 | 17 | 0.0081341 | 0.0020386 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_191-11_0_5_load_24 | 22 | 0.0058763 | 0.0014727 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_191-11_0_5_load_25 | 23 | 0.0094322 | 0.0023639 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_191-11_0_5_load_19 | 24 | 0.013081 | 0.0032784 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_191-11_0_5_load_66 | 26 | 0.011994 | 0.0030059 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_191-11_0_5_load_73 | 28 | 0.0022881 | 0.00057345 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_191-11_0_5_load_158 | 32 | 0.058793 | 0.014735 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_191-11_0_5_load_39 | 34 | 0.0056567 | 0.0014177 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_191-11_0_5_load_44 | 35 | 0.0055439 | 0.0013894 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_191-11_0_5_load_42 | 36 | 0.0021981 | 0.00055091 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_191-11_0_5_load_74 | 37 | 0.0018671 | 0.00046794 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_191-11_0_5_load_98 | 38 | 0.015492 | 0.0038827 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_191-11_0_5_load_95 | 40 | 0.0077846 | 0.001951 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_191-11_0_5_load_92 | 41 | 0.0020821 | 0.00052182 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_191-11_0_5_load_156 | 42 | 0.020922 | 0.0052437 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_191-11_0_5_load_27 | 45 | 0.0059845 | 0.0014998 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_191-11_0_5_load_30 | 48 | 0.0035068 | 0.00087889 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_191-11_0_5_load_32 | 49 | 0.013089 | 0.0032805 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_191-11_0_5_load_33 | 50 | 0.0025087 | 0.00062874 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_191-11_0_5_load_34 | 51 | 0.0045516 | 0.0011407 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_191-11_0_5_load_35 | 52 | 0.0015931 | 0.00039926 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_191-11_0_5_load_38 | 54 | 0.01047 | 0.002624 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_191-11_0_5_load_55 | 55 | 0.0094712 | 0.0023737 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_191-11_0_5_load_52 | 56 | 0.012723 | 0.0031886 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_191-11_0_5_load_102 | 57 | 0.011509 | 0.0028845 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_191-11_0_5_load_53 | 59 | 0.0033143 | 0.00083065 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_191-11_0_5_load_41 | 60 | 0.002738 | 0.00068621 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_191-11_0_5_load_46 | 61 | 0.0027398 | 0.00068667 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_191-11_0_5_load_50 | 62 | 0.0027398 | 0.00068667 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_191-11_0_5_load_47 | 64 | 0.0031493 | 0.0007893 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_191-11_0_5_load_48 | 67 | 0.002943 | 0.00073759 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_191-11_0_5_load_49 | 68 | 0.0027409 | 0.00068695 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_191-11_0_5_load_51 | 69 | 0.0027399 | 0.00068667 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_191-11_0_5_load_69 | 71 | 0.0048441 | 0.0012141 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_191-11_0_5_load_56 | 73 | 0.0020494 | 0.00051364 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_191-11_0_5_load_159 | 74 | 0.013549 | 0.0033958 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_191-11_0_5_load_152 | 75 | 0.0072617 | 0.0018199 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_191-11_0_5_load_59 | 76 | 0.010105 | 0.0025325 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_191-11_0_5_load_65 | 77 | 0.004125 | 0.0010338 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_191-11_0_5_load_64 | 79 | 0.00073559 | 0.00018436 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_191-11_0_5_load_60 | 80 | 0.0044692 | 0.0011201 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_191-11_0_5_load_61 | 81 | 0.001514 | 0.00037946 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_191-11_0_5_load_63 | 82 | 0.0010624 | 0.00026627 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_191-11_0_5_load_67 | 83 | 0.00073499 | 0.00018421 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_191-11_0_5_load_70 | 84 | 0.00045528 | 0.0001141 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_191-11_0_5_load_155 | 85 | 0.0051644 | 0.0012943 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_191-11_0_5_load_161 | 86 | 0.0028011 | 0.00070202 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_191-11_0_5_load_71 | 87 | 0.00050732 | 0.00012715 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_191-11_0_5_load_153 | 88 | 0.0062388 | 0.0015636 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_191-11_0_5_load_160 | 89 | 0.0017655 | 0.00044249 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_191-11_0_5_load_150 | 90 | 0.0026996 | 0.00067659 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_191-11_0_5_load_151 | 91 | 0.0014368 | 0.0003601 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_191-11_0_5_load_76 | 92 | 0.001069 | 0.00026792 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_191-11_0_5_load_77 | 93 | 0.0016288 | 0.00040821 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_191-11_0_5_load_78 | 94 | 0.0011111 | 0.00027846 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_191-11_0_5_load_80 | 95 | 0.00091145 | 0.00022843 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_191-11_0_5_load_83 | 96 | 0.0010469 | 0.00026238 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_191-11_0_5_load_82 | 97 | 0.0017333 | 0.00043442 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_191-11_0_5_load_91 | 98 | 0.0015379 | 0.00038544 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_191-11_0_5_load_84 | 99 | 0.00091883 | 0.00023028 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_191-11_0_5_load_90 | 100 | 0.0014285 | 0.00035802 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_191-11_0_5_load_117 | 101 | 0.0015223 | 0.00038153 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_191-11_0_5_load_135 | 102 | 0.0019379 | 0.00048569 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_191-11_0_5_load_85 | 103 | 0.00091971 | 0.0002305 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_191-11_0_5_load_86 | 104 | 0.0017424 | 0.00043669 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_191-11_0_5_load_87 | 105 | 0.0018682 | 0.00046823 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_191-11_0_5_load_88 | 106 | 0.0011224 | 0.00028131 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_191-11_0_5_load_89 | 107 | 0.001741 | 0.00043634 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_191-11_0_5_load_103 | 108 | 0.00094233 | 0.00023617 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_191-11_0_5_load_104 | 109 | 0.0028892 | 0.0007241 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_191-11_0_5_load_115 | 110 | 0.0015671 | 0.00039275 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_191-11_0_5_load_134 | 111 | 0.0015379 | 0.00038543 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_191-11_0_5_load_96 | 113 | 0.0026015 | 0.000652 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_191-11_0_5_load_97 | 114 | 0.0018687 | 0.00046833 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_191-11_0_5_load_99 | 115 | 0.0075463 | 0.0018913 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_191-11_0_5_load_101 | 117 | 0.0045573 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_191-11_0_5_load_107 | 118 | 0.0013895 | 0.00034823 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_191-11_0_5_load_105 | 119 | 0.0024064 | 0.00060309 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_191-11_0_5_load_144 | 120 | 0.0007842 | 0.00019654 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_191-11_0_5_load_143 | 122 | 0.0028004 | 0.00070186 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_191-11_0_5_load_137 | 123 | 0.0022075 | 0.00055325 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_191-11_0_5_load_138 | 124 | 0.0046442 | 0.0011639 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_191-11_0_5_load_142 | 127 | 0.00093494 | 0.00023432 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_191-11_0_5_load_124 | 128 | 0.0015272 | 0.00038274 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_191-11_0_5_load_113 | 130 | 0.0015391 | 0.00038574 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_191-11_0_5_load_114 | 131 | 0.0024983 | 0.00062612 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_191-11_0_5_load_116 | 132 | 0.0010733 | 0.00026899 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_191-11_0_5_load_118 | 133 | 0.0016705 | 0.00041867 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_191-11_0_5_load_119 | 134 | 0.00089676 | 0.00022475 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_191-11_0_5_load_120 | 135 | 0.0013153 | 0.00032964 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_191-11_0_5_load_125 | 137 | 0.0012735 | 0.00031917 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_191-11_0_5_load_136 | 139 | 0.0045208 | 0.001133 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_191-11_0_5_load_130 | 140 | 0.0017294 | 0.00043342 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_191-11_0_5_load_126 | 141 | 0.00056285 | 0.00014106 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_191-11_0_5_load_127 | 142 | 0.0012383 | 0.00031034 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_191-11_0_5_load_128 | 143 | 0.0024149 | 0.00060522 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_191-11_0_5_load_129 | 144 | 0.001201 | 0.000301 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_191-11_0_5_load_131 | 145 | 0.0016257 | 0.00040743 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_191-11_0_5_load_133 | 146 | 0.00065464 | 0.00016407 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_191-11_0_5_load_139 | 147 | 0.0021872 | 0.00054817 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_191-11_0_5_load_140 | 148 | 0.0032785 | 0.00082167 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_191-11_0_5_load_145 | 149 | 0.0064838 | 0.001625 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_191-11_0_5_load_154 | 150 | 0.0033545 | 0.00084071 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_191-11_0_5_line_0 |  | 0 | 1 | 0.0036071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_191-11_0_5_line_1 |  | 0 | 2 | 0.035248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_191-11_0_5_line_2 |  | 2 | 3 | 0.030646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_191-11_0_5_line_3 |  | 3 | 4 | 0.027106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_191-11_0_5_line_4 |  | 3 | 5 | 0.03519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_191-11_0_5_line_5 |  | 4 | 9 | 0.07528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_191-11_0_5_line_6 |  | 5 | 7 | 0.040175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_191-11_0_5_line_7 |  | 6 | 7 | 0.022762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_191-11_0_5_line_8 |  | 6 | 8 | 0.052592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_191-11_0_5_line_9 |  | 9 | 10 | 0.033061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_191-11_0_5_line_10 |  | 10 | 11 | 0.099513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_191-11_0_5_line_11 |  | 10 | 12 | 0.066903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_191-11_0_5_line_12 |  | 11 | 14 | 0.05233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_191-11_0_5_line_13 |  | 12 | 13 | 0.012645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_191-11_0_5_line_14 |  | 14 | 15 | 0.050673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_191-11_0_5_line_15 |  | 15 | 33 | 0.03728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_191-11_0_5_line_16 |  | 15 | 39 | 0.021536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_191-11_0_5_line_17 |  | 16 | 17 | 0.027537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_191-11_0_5_line_18 |  | 16 | 18 | 0.012393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_191-11_0_5_line_19 |  | 17 | 19 | 0.0015047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_191-11_0_5_line_20 |  | 18 | 20 | 0.030743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_191-11_0_5_line_21 |  | 19 | 21 | 0.014056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_191-11_0_5_line_22 |  | 20 | 22 | 0.037934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_191-11_0_5_line_23 |  | 20 | 23 | 0.01819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_191-11_0_5_line_24 |  | 21 | 26 | 0.018936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_191-11_0_5_line_25 |  | 23 | 34 | 0.01486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_191-11_0_5_line_26 |  | 24 | 25 | 0.0071196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_191-11_0_5_line_27 |  | 25 | 35 | 0.022925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_191-11_0_5_line_28 |  | 25 | 36 | 0.02363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_191-11_0_5_line_29 |  | 26 | 27 | 0.029684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_191-11_0_5_line_30 |  | 27 | 28 | 0.0098031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_191-11_0_5_line_31 |  | 27 | 29 | 0.024082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_191-11_0_5_line_32 |  | 28 | 37 | 0.0079119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_191-11_0_5_line_33 |  | 29 | 30 | 0.001806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_191-11_0_5_line_34 |  | 30 | 40 | 0.030399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_191-11_0_5_line_35 |  | 30 | 41 | 0.014652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_191-11_0_5_line_36 |  | 31 | 32 | 0.047761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_191-11_0_5_line_37 |  | 31 | 33 | 0.027165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_191-11_0_5_line_38 |  | 33 | 42 | 0.027062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_191-11_0_5_line_39 |  | 34 | 43 | 0.019892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_191-11_0_5_line_40 |  | 35 | 44 | 0.0032848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_191-11_0_5_line_41 |  | 36 | 43 | 0.0043708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_191-11_0_5_line_42 |  | 37 | 57 | 0.025763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_191-11_0_5_line_43 |  | 38 | 39 | 0.040937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_191-11_0_5_line_44 |  | 39 | 119 | 0.030327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_191-11_0_5_line_45 |  | 40 | 115 | 0.033554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_191-11_0_5_line_46 |  | 41 | 112 | 0.017653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_191-11_0_5_line_47 |  | 43 | 60 | 0.01043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_191-11_0_5_line_48 |  | 44 | 65 | 0.026581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_191-11_0_5_line_49 |  | 44 | 66 | 0.022835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_191-11_0_5_line_50 |  | 45 | 46 | 0.0014142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_191-11_0_5_line_51 |  | 45 | 47 | 0.017104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_191-11_0_5_line_52 |  | 46 | 48 | 0.04834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_191-11_0_5_line_53 |  | 47 | 49 | 0.039228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_191-11_0_5_line_54 |  | 47 | 50 | 0.008695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_191-11_0_5_line_55 |  | 47 | 51 | 0.02801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_191-11_0_5_line_56 |  | 48 | 52 | 0.00095357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_191-11_0_5_line_57 |  | 50 | 53 | 0.011569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_191-11_0_5_line_58 |  | 51 | 54 | 0.021734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_191-11_0_5_line_59 |  | 53 | 55 | 0.027265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_191-11_0_5_line_60 |  | 53 | 56 | 0.030312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_191-11_0_5_line_61 |  | 54 | 57 | 0.0059371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_191-11_0_5_line_62 |  | 55 | 58 | 0.036457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_191-11_0_5_line_63 |  | 56 | 59 | 0.0045104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_191-11_0_5_line_64 |  | 58 | 76 | 0.01109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_191-11_0_5_line_65 |  | 60 | 61 | 0.018565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_191-11_0_5_line_66 |  | 61 | 62 | 0.018794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_191-11_0_5_line_67 |  | 62 | 63 | 0.026476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_191-11_0_5_line_68 |  | 63 | 64 | 0.029744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_191-11_0_5_line_69 |  | 64 | 67 | 0.018583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_191-11_0_5_line_70 |  | 65 | 90 | 0.010075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_191-11_0_5_line_71 |  | 65 | 91 | 0.0093948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_191-11_0_5_line_72 |  | 66 | 75 | 0.0015318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_191-11_0_5_line_73 |  | 66 | 72 | 0.017617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_191-11_0_5_line_74 |  | 68 | 69 | 0.020437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_191-11_0_5_line_75 |  | 69 | 70 | 0.01681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_191-11_0_5_line_76 |  | 70 | 71 | 0.010259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_191-11_0_5_line_77 |  | 71 | 75 | 0.03447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_191-11_0_5_line_78 |  | 72 | 73 | 0.021658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_191-11_0_5_line_79 |  | 73 | 74 | 0.023804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_191-11_0_5_line_80 |  | 74 | 77 | 0.0082972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_191-11_0_5_line_81 |  | 76 | 80 | 0.027318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_191-11_0_5_line_82 |  | 77 | 78 | 0.019029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_191-11_0_5_line_83 |  | 78 | 79 | 0.0084962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_191-11_0_5_line_84 |  | 79 | 85 | 0.0092344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_191-11_0_5_line_85 |  | 80 | 81 | 0.030602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_191-11_0_5_line_86 |  | 81 | 82 | 0.037383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_191-11_0_5_line_87 |  | 82 | 83 | 0.031436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_191-11_0_5_line_88 |  | 82 | 84 | 0.046273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_191-11_0_5_line_89 |  | 83 | 86 | 0.092742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_191-11_0_5_line_90 |  | 84 | 87 | 0.00025572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_191-11_0_5_line_91 |  | 85 | 88 | 0.022704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_191-11_0_5_line_92 |  | 86 | 89 | 0.0045319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_191-11_0_5_line_93 |  | 88 | 150 | 0.0029615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_191-11_0_5_line_94 |  | 92 | 93 | 0.026054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_191-11_0_5_line_95 |  | 92 | 94 | 0.018175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_191-11_0_5_line_96 |  | 94 | 95 | 0.012318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_191-11_0_5_line_97 |  | 95 | 96 | 0.011416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_191-11_0_5_line_98 |  | 96 | 99 | 0.013122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_191-11_0_5_line_99 |  | 97 | 98 | 0.027941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_191-11_0_5_line_100 |  | 98 | 102 | 0.026048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_191-11_0_5_line_101 |  | 99 | 103 | 0.016914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_191-11_0_5_line_102 |  | 100 | 101 | 0.031148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_191-11_0_5_line_103 |  | 101 | 110 | 0.026527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_191-11_0_5_line_104 |  | 102 | 111 | 0.030009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_191-11_0_5_line_105 |  | 103 | 104 | 0.0064331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_191-11_0_5_line_106 |  | 104 | 105 | 0.017475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_191-11_0_5_line_107 |  | 105 | 106 | 0.0023586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_191-11_0_5_line_108 |  | 106 | 107 | 0.021886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_191-11_0_5_line_109 |  | 107 | 108 | 0.0071161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_191-11_0_5_line_110 |  | 108 | 109 | 0.024694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_191-11_0_5_line_111 |  | 109 | 123 | 0.0031313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_191-11_0_5_line_112 |  | 110 | 130 | 0.026165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_191-11_0_5_line_113 |  | 111 | 146 | 0.014577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_191-11_0_5_line_114 |  | 112 | 113 | 0.011743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_191-11_0_5_line_115 |  | 112 | 114 | 0.016401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_191-11_0_5_line_116 |  | 113 | 116 | 0.01411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_191-11_0_5_line_117 |  | 114 | 117 | 0.014248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_191-11_0_5_line_118 |  | 116 | 118 | 0.022513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_191-11_0_5_line_119 |  | 116 | 119 | 0.038606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_191-11_0_5_line_120 |  | 117 | 120 | 0.010479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_191-11_0_5_line_121 |  | 118 | 121 | 0.016666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_191-11_0_5_line_122 |  | 120 | 122 | 0.017831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_191-11_0_5_line_123 |  | 121 | 125 | 0.00911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_191-11_0_5_line_124 |  | 121 | 126 | 0.025558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_191-11_0_5_line_125 |  | 122 | 149 | 0.03236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_191-11_0_5_line_126 |  | 123 | 124 | 0.021391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_191-11_0_5_line_127 |  | 124 | 148 | 0.0011571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_191-11_0_5_line_128 |  | 125 | 127 | 0.024566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_191-11_0_5_line_129 |  | 126 | 128 | 0.01705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_191-11_0_5_line_130 |  | 126 | 129 | 0.016294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_191-11_0_5_line_131 |  | 128 | 138 | 0.010861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_191-11_0_5_line_132 |  | 129 | 136 | 0.040522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_191-11_0_5_line_133 |  | 129 | 135 | 0.016039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_191-11_0_5_line_134 |  | 130 | 131 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_191-11_0_5_line_135 |  | 131 | 132 | 0.028068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_191-11_0_5_line_136 |  | 132 | 133 | 0.02397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_191-11_0_5_line_137 |  | 133 | 134 | 0.027645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_191-11_0_5_line_138 |  | 134 | 135 | 0.031713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_191-11_0_5_line_139 |  | 136 | 137 | 0.0044688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_191-11_0_5_line_140 |  | 138 | 139 | 0.030796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_191-11_0_5_line_141 |  | 138 | 140 | 0.019292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_191-11_0_5_line_142 |  | 139 | 147 | 0.020171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_191-11_0_5_line_143 |  | 140 | 143 | 0.028589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_191-11_0_5_line_144 |  | 141 | 142 | 0.0068775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_191-11_0_5_line_145 |  | 141 | 143 | 0.019168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_191-11_0_5_line_146 |  | 142 | 144 | 0.027191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_191-11_0_5_line_147 |  | 144 | 145 | 0.010809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_191-11_0_5_line_148 |  | 145 | 146 | 0.0062681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_191-11_0_5_line_149 |  | 147 | 148 | 0.033581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_191-11_0_5_trafo_158 | 0.63 MVA 20/0.4 kV | 151 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2690833.1105 | 1249929.9816 | 2690831.2778 | 1249926.8748
1 | 2690851.0196 | 1249960.3409 | 2690833.1105 | 1249929.9816
2 | 2690851.0196 | 1249960.3409 | 2690866.4123 | 1249946.2661 | 2690873.3302 | 1249939.2779
3 | 2690892.4274 | 1249919.9894 | 2690873.3302 | 1249939.2779
4 | 2690873.3302 | 1249939.2779 | 2690855.6491 | 1249908.8523
5 | 2690892.4274 | 1249919.9894 | 2690930.7426 | 1249896.6814 | 2690916.1611 | 1249869.9699
6 | 2690835.3747 | 1249874.1688 | 2690846.8982 | 1249893.7937 | 2690855.6491 | 1249908.8523
7 | 2690815.7384 | 1249885.7768 | 2690835.3747 | 1249874.1688
8 | 2690815.7384 | 1249885.7768 | 2690796.4807 | 1249850.0324 | 2690798.2629 | 1249838.1951 | 2690798.2798 | 1249838.185
9 | 2690910.095 | 1249838.387 | 2690910.377 | 1249859.374 | 2690916.1611 | 1249869.9699
10 | 2690910.095 | 1249838.387 | 2690917.0413 | 1249836.4476 | 2690919.5328 | 1249839.4214 | 2690923.2056 | 1249840.6898 | 2690927.6415 | 1249856.6923 | 2690929.6663 | 1249864.4848 | 2690933.605 | 1249874.9977 | 2690939.1719 | 1249886.6698 | 2690943.6462 | 1249893.2768 | 2690950.1972 | 1249899.3819 | 2690967.4105 | 1249906.9074
11 | 2690861.7275 | 1249821.4548 | 2690870.4468 | 1249836.3442 | 2690877.8766 | 1249849.646 | 2690891.1378 | 1249843.1221 | 2690900.2413 | 1249839.8592 | 2690910.095 | 1249838.387
12 | 2690967.4105 | 1249906.9074 | 2690996.6995 | 1249917.7429 | 2691016.7427 | 1249924.3404
13 | 2690861.7275 | 1249821.4548 | 2690855.2823 | 1249810.5759
14 | 2691065.0043 | 1249939.7753 | 2691048.755 | 1249934.8775 | 2691016.7427 | 1249924.3404
15 | 2691070.8912 | 1249903.6048 | 2691071.6417 | 1249906.8522 | 2691069.5936 | 1249925.635 | 2691068.6905 | 1249929.8577 | 2691066.9233 | 1249932.3325 | 2691066.4935 | 1249934.2607 | 2691065.7875 | 1249937.4522 | 2691065.0043 | 1249939.7753
16 | 2691065.0043 | 1249939.7753 | 2691085.601 | 1249946.2634
17 | 2691133.4094 | 1249860.7386 | 2691109.6364 | 1249846.8419
18 | 2691098.9373 | 1249840.5877 | 2691109.6364 | 1249846.8419
19 | 2691134.7085 | 1249861.498 | 2691133.4094 | 1249860.7386
20 | 2691098.9373 | 1249840.5877 | 2691087.9518 | 1249834.1474 | 2691072.0226 | 1249825.5961
21 | 2691147.001 | 1249868.3811 | 2691134.7085 | 1249861.498
22 | 2691072.0226 | 1249825.5961 | 2691048.8141 | 1249815.0983 | 2691036.9695 | 1249811.224
23 | 2691072.0226 | 1249825.5961 | 2691082.304 | 1249810.5904
24 | 2691147.001 | 1249868.3811 | 2691163.2102 | 1249878.1713
25 | 2691082.304 | 1249810.5904 | 2691090.703 | 1249798.3321
26 | 2691128.3993 | 1249791.1029 | 2691125.1905 | 1249797.4584
27 | 2691128.3993 | 1249791.1029 | 2691138.7398 | 1249770.6429
28 | 2691128.3993 | 1249791.1029 | 2691106.0754 | 1249783.3556
29 | 2691188.619 | 1249893.5181 | 2691163.2102 | 1249878.1713
30 | 2691188.619 | 1249893.5181 | 2691192.9906 | 1249884.7436
31 | 2691177.9872 | 1249915.1266 | 2691186.4521 | 1249897.9215 | 2691188.619 | 1249893.5181
32 | 2691192.9906 | 1249884.7436 | 2691196.5188 | 1249877.662
33 | 2691177.9872 | 1249915.1266 | 2691177.192 | 1249916.7489
34 | 2691177.192 | 1249916.7489 | 2691201.2864 | 1249935.2842
35 | 2691177.192 | 1249916.7489 | 2691170.41 | 1249929.737
36 | 2691086.8542 | 1249882.4451 | 2691085.029 | 1249878.8699 | 2691080.9355 | 1249874.0255 | 2691074.235 | 1249867.8289 | 2691062.5008 | 1249861.9553 | 2691053.6595 | 1249857.4939 | 2691048.6655 | 1249855.8646
37 | 2691086.8542 | 1249882.4451 | 2691085.1175 | 1249888.334 | 2691074.5279 | 1249901.3256 | 2691070.8912 | 1249903.6048
38 | 2691070.8912 | 1249903.6048 | 2691067.2888 | 1249903.1603 | 2691046.4395 | 1249892.4652
39 | 2691101.9462 | 1249781.9226 | 2691090.703 | 1249798.3321
40 | 2691140.2214 | 1249767.7112 | 2691138.7398 | 1249770.6429
41 | 2691101.9462 | 1249781.9226 | 2691106.0754 | 1249783.3556
42 | 2691208.1889 | 1249854.6944 | 2691202.5503 | 1249865.5555 | 2691196.5188 | 1249877.662
43 | 2691085.601 | 1249946.2634 | 2691090.737 | 1249936.8351 | 2691096.5217 | 1249927.4502 | 2691104.0275 | 1249916.6239 | 2691109.1894 | 1249913.5601
44 | 2691085.601 | 1249946.2634 | 2691114.4221 | 1249955.7023
45 | 2691229.2151 | 1249953.712 | 2691214.9514 | 1249945.7964 | 2691201.2864 | 1249935.2842
46 | 2691162.2388 | 1249945.3852 | 2691170.41 | 1249929.737
47 | 2691101.9462 | 1249781.9226 | 2691092.0966 | 1249778.4933
48 | 2691116.3695 | 1249755.8355 | 2691140.2214 | 1249767.7112
49 | 2691140.2214 | 1249767.7112 | 2691150.525 | 1249747.3208
50 | 2691248.538 | 1249819.2613 | 2691247.5385 | 1249818.2608
51 | 2691235.4503 | 1249806.161 | 2691247.5385 | 1249818.2608
52 | 2691248.538 | 1249819.2613 | 2691245.5684 | 1249823.3187 | 2691244.6871 | 1249825.1398 | 2691244.1871 | 1249827.2115 | 2691244.5317 | 1249829.3517 | 2691245.3779 | 1249831.2774 | 2691249.5271 | 1249836.9122 | 2691266.7753 | 1249858.8278
53 | 2691235.4503 | 1249806.161 | 2691241.3068 | 1249798.0227 | 2691247.247 | 1249792.2875 | 2691256.0867 | 1249788.0314 | 2691266.4397 | 1249783.935
54 | 2691235.4503 | 1249806.161 | 2691230.3109 | 1249800.5887 | 2691229.6486 | 1249799.6923
55 | 2691235.4503 | 1249806.161 | 2691229.9362 | 1249815.1163 | 2691221.3221 | 1249830.3419
56 | 2691266.7753 | 1249858.8278 | 2691267.6426 | 1249859.2241
57 | 2691222.7737 | 1249790.3872 | 2691229.6486 | 1249799.6923
58 | 2691210.9245 | 1249849.4251 | 2691212.8532 | 1249845.71 | 2691218.0989 | 1249836.0389 | 2691221.3221 | 1249830.3419
59 | 2691222.7737 | 1249790.3872 | 2691219.7836 | 1249777.1422 | 2691218.1688 | 1249766.7761 | 2691217.8525 | 1249763.5966
60 | 2691222.7737 | 1249790.3872 | 2691196.9193 | 1249774.564
61 | 2691208.1889 | 1249854.6944 | 2691210.9245 | 1249849.4251
62 | 2691214.6768 | 1249727.2811 | 2691215.9064 | 1249744.035 | 2691217.8525 | 1249763.5966
63 | 2691196.9193 | 1249774.564 | 2691193.0722 | 1249772.2096
64 | 2691214.6768 | 1249727.2811 | 2691223.4789 | 1249720.5353
65 | 2691092.0966 | 1249778.4933 | 2691074.5641 | 1249772.3892
66 | 2691056.8148 | 1249766.2096 | 2691074.5641 | 1249772.3892
67 | 2691031.8113 | 1249757.5044 | 2691056.8148 | 1249766.2096
68 | 2691031.8113 | 1249757.5044 | 2691023.5239 | 1249753.3406 | 2691032.4717 | 1249734.9306
69 | 2691032.4717 | 1249734.9306 | 2691040.5951 | 1249718.2167
70 | 2691116.3695 | 1249755.8355 | 2691121.0042 | 1249746.8903
71 | 2691116.3695 | 1249755.8355 | 2691111.9495 | 1249764.1256
72 | 2691150.525 | 1249747.3208 | 2691149.2024 | 1249746.5481
73 | 2691165.808 | 1249756.1625 | 2691150.525 | 1249747.3208
74 | 2691075.3877 | 1249712.9214 | 2691083.4864 | 1249714.9991 | 2691094.8834 | 1249718.9916
75 | 2691111.1495 | 1249723.097 | 2691100.1523 | 1249720.8374 | 2691094.8834 | 1249718.9916
76 | 2691111.1495 | 1249723.097 | 2691119.5695 | 1249728.9572
77 | 2691119.5695 | 1249728.9572 | 2691122.0795 | 1249730.7041 | 2691149.2024 | 1249746.5481
78 | 2691165.808 | 1249756.1625 | 2691175.3232 | 1249736.7062
79 | 2691175.3232 | 1249736.7062 | 2691176.4032 | 1249734.4978 | 2691176.5898 | 1249726.2945 | 2691183.0905 | 1249714.8751
80 | 2691183.0905 | 1249714.8751 | 2691185.2432 | 1249711.0938 | 2691181.7372 | 1249709.2829 | 2691181.7372 | 1249709.2829
81 | 2691223.4789 | 1249720.5353 | 2691224.2206 | 1249719.9669 | 2691228.3432 | 1249716.0607 | 2691232.4651 | 1249711.7097 | 2691236.461 | 1249705.244 | 2691239.2971 | 1249698.7239
82 | 2691192.9679 | 1249693.9217 | 2691181.7372 | 1249709.2829
83 | 2691192.9679 | 1249693.9217 | 2691187.2509 | 1249689.5638 | 2691186.1206 | 1249688.9061
84 | 2691186.1206 | 1249688.9061 | 2691178.139 | 1249684.2621
85 | 2691248.4532 | 1249669.6089 | 2691247.629 | 1249674.359 | 2691246.1555 | 1249679.8183 | 2691244.2476 | 1249686.027 | 2691240.5786 | 1249695.778 | 2691239.2971 | 1249698.7239
86 | 2691248.4532 | 1249669.6089 | 2691248.6565 | 1249668.437 | 2691249.311 | 1249661.7309 | 2691249.456 | 1249650.847 | 2691249.3658 | 1249640.0374 | 2691249.1118 | 1249632.281
87 | 2691248.083 | 1249600.8616 | 2691249.1118 | 1249632.281
88 | 2691249.1118 | 1249632.281 | 2691293.7962 | 1249620.2586
89 | 2691248.083 | 1249600.8616 | 2691166.2879 | 1249557.1501
90 | 2691293.7962 | 1249620.2586 | 2691293.9972 | 1249620.1006
91 | 2691158.5148 | 1249672.8438 | 2691178.139 | 1249684.2621
92 | 2691162.6359 | 1249559.8335 | 2691166.2879 | 1249557.1501
93 | 2691158.5148 | 1249672.8438 | 2691155.955 | 1249671.3544
94 | 2690880.9295 | 1249999.3675 | 2690862.1771 | 1250017.4546
95 | 2690880.9295 | 1249999.3675 | 2690894.0112 | 1249986.7499
96 | 2690902.8773 | 1249978.1983 | 2690894.0112 | 1249986.7499
97 | 2690902.8773 | 1249978.1983 | 2690911.0941 | 1249970.273
98 | 2690920.5388 | 1249961.1634 | 2690911.0941 | 1249970.273
99 | 2690881.6098 | 1250036.8166 | 2690909.4021 | 1250033.9371
100 | 2690909.4021 | 1250033.9371 | 2690935.3116 | 1250031.2526
101 | 2690920.5388 | 1249961.1634 | 2690923.0471 | 1249958.744 | 2690926.9489 | 1249955.4236 | 2690931.577 | 1249952.5034 | 2690934.1269 | 1249951.2685
102 | 2690889.2256 | 1250070.5796 | 2690920.2094 | 1250067.3804
103 | 2690920.2094 | 1250067.3804 | 2690946.5964 | 1250064.6559
104 | 2690965.161 | 1250028.16 | 2690935.3116 | 1250031.2526
105 | 2690940.1161 | 1249948.9496 | 2690936.0501 | 1249950.3371 | 2690934.1269 | 1249951.2685
106 | 2690940.1161 | 1249948.9496 | 2690940.9459 | 1249948.6665 | 2690946.6614 | 1249947.709 | 2690952.843 | 1249947.3702 | 2690957.4444 | 1249947.691
107 | 2690959.7973 | 1249947.8551 | 2690959.7973 | 1249947.8551 | 2690957.4444 | 1249947.691
108 | 2690959.7973 | 1249947.8551 | 2690965.6241 | 1249948.9898 | 2690972.1823 | 1249950.6806 | 2690980.908 | 1249953.5245
109 | 2690987.6738 | 1249955.7296 | 2690980.908 | 1249953.5245
110 | 2690987.6738 | 1249955.7296 | 2691011.1518 | 1249963.3816
111 | 2691014.1289 | 1249964.3519 | 2691011.1518 | 1249963.3816
112 | 2690972.6235 | 1250061.9685 | 2690946.5964 | 1250064.6559
113 | 2690979.6601 | 1250026.6577 | 2690965.161 | 1250028.16
114 | 2691162.2388 | 1249945.3852 | 2691157.0455 | 1249955.9169
115 | 2691162.2388 | 1249945.3852 | 2691176.3364 | 1249953.766
116 | 2691150.8052 | 1249968.5715 | 2691157.0455 | 1249955.9169
117 | 2691188.5837 | 1249961.0468 | 2691188.5837 | 1249961.0468 | 2691176.3364 | 1249953.766
118 | 2691150.8052 | 1249968.5715 | 2691148.2424 | 1249973.6805 | 2691140.8552 | 1249988.7657
119 | 2691150.8052 | 1249968.5715 | 2691145.2239 | 1249966.2061 | 2691120.1224 | 1249957.5692 | 2691114.4221 | 1249955.7023
120 | 2691188.5837 | 1249961.0468 | 2691184.3213 | 1249970.6194
121 | 2691133.5244 | 1250003.7327 | 2691139.2385 | 1249992.0672 | 2691140.8552 | 1249988.7657
122 | 2691189.8609 | 1249982.2481 | 2691188.6183 | 1249981.8521 | 2691181.0598 | 1249977.944 | 2691184.3213 | 1249970.6194
123 | 2691133.5244 | 1250003.7327 | 2691142.3287 | 1250006.1699
124 | 2691133.5244 | 1250003.7327 | 2691125.7195 | 1250020.2586 | 2691123.1456 | 1250027.0798
125 | 2691220.9022 | 1249989.4409 | 2691204.5905 | 1249984.1329 | 2691198.3712 | 1249984.9601 | 2691189.8609 | 1249982.2481
126 | 2691014.1289 | 1249964.3519 | 2691034.4673 | 1249970.9806
127 | 2691035.5674 | 1249971.3391 | 2691034.4673 | 1249970.9806
128 | 2691142.3287 | 1250006.1699 | 2691148.2278 | 1250007.9953 | 2691166.5504 | 1250006.4165
129 | 2691123.1456 | 1250027.0798 | 2691113.2448 | 1250023.2803 | 2691107.3665 | 1250020.6381
130 | 2691123.1456 | 1250027.0798 | 2691122.2599 | 1250030.1686 | 2691121.7683 | 1250034.6422 | 2691122.4673 | 1250043.1928
131 | 2691097.2322 | 1250016.7514 | 2691104.5612 | 1250019.3772 | 2691107.3665 | 1250020.6381
132 | 2691122.4673 | 1250043.1928 | 2691123.5038 | 1250052.3824 | 2691124.0398 | 1250059.7518 | 2691124.6237 | 1250073.3267 | 2691126.1357 | 1250083.5133
133 | 2691122.4673 | 1250043.1928 | 2691107.3884 | 1250044.6955 | 2691106.6801 | 1250045.2266
134 | 2690972.6235 | 1250061.9685 | 2690996.6151 | 1250059.4913
135 | 2690996.6151 | 1250059.4913 | 2691024.5351 | 1250056.6085
136 | 2691024.5351 | 1250056.6085 | 2691035.6814 | 1250055.4576 | 2691048.363 | 1250054.0057
137 | 2691048.363 | 1250054.0057 | 2691075.8283 | 1250050.8613
138 | 2691075.8283 | 1250050.8613 | 2691100.5869 | 1250048.0268 | 2691104.7148 | 1250046.7004 | 2691106.6801 | 1250045.2266
139 | 2691126.1357 | 1250083.5133 | 2691127.3531 | 1250087.8131
140 | 2691097.2322 | 1250016.7514 | 2691093.8611 | 1249999.7978 | 2691092.7902 | 1249996.7679 | 2691091.0394 | 1249993.7609 | 2691089.0323 | 1249991.2171 | 2691086.2736 | 1249988.9396 | 2691086.2736 | 1249988.9396
141 | 2691097.2322 | 1250016.7514 | 2691092.4494 | 1250015.9885 | 2691087.6962 | 1250015.7486 | 2691082.3159 | 1250016.0217 | 2691078.0368 | 1250016.465
142 | 2691067.4957 | 1249981.7452 | 2691079.6711 | 1249985.7135 | 2691083.0702 | 1249987.1001 | 2691086.2736 | 1249988.9396
143 | 2691049.5996 | 1250019.4114 | 2691078.0368 | 1250016.465
144 | 2691030.5333 | 1250021.3868 | 2691023.6925 | 1250022.0956
145 | 2691030.5333 | 1250021.3868 | 2691049.5996 | 1250019.4114
146 | 2690996.6461 | 1250024.8978 | 2691023.6925 | 1250022.0956
147 | 2690996.6461 | 1250024.8978 | 2690985.8948 | 1250026.0118
148 | 2690979.6601 | 1250026.6577 | 2690985.8948 | 1250026.0118
149 | 2691035.5674 | 1249971.3391 | 2691067.4957 | 1249981.7452

## bus_geodata
| x | y | coords
0 | 2690833.1105 | 1249929.9816
1 | 2690831.2778 | 1249926.8748
2 | 2690851.0196 | 1249960.3409
3 | 2690873.3302 | 1249939.2779
4 | 2690892.4274 | 1249919.9894
5 | 2690855.6491 | 1249908.8523
6 | 2690815.7384 | 1249885.7768
7 | 2690835.3747 | 1249874.1688
8 | 2690798.2798 | 1249838.185
9 | 2690916.1611 | 1249869.9699
10 | 2690910.095 | 1249838.387
11 | 2690967.4105 | 1249906.9074
12 | 2690861.7275 | 1249821.4548
13 | 2690855.2823 | 1249810.5759
14 | 2691016.7427 | 1249924.3404
15 | 2691065.0043 | 1249939.7753
16 | 2691109.6364 | 1249846.8419
17 | 2691133.4094 | 1249860.7386
18 | 2691098.9373 | 1249840.5877
19 | 2691134.7085 | 1249861.498
20 | 2691072.0226 | 1249825.5961
21 | 2691147.001 | 1249868.3811
22 | 2691036.9695 | 1249811.224
23 | 2691082.304 | 1249810.5904
24 | 2691125.1905 | 1249797.4584
25 | 2691128.3993 | 1249791.1029
26 | 2691163.2102 | 1249878.1713
27 | 2691188.619 | 1249893.5181
28 | 2691192.9906 | 1249884.7436
29 | 2691177.9872 | 1249915.1266
30 | 2691177.192 | 1249916.7489
31 | 2691086.8542 | 1249882.4451
32 | 2691048.6655 | 1249855.8646
33 | 2691070.8912 | 1249903.6048
34 | 2691090.703 | 1249798.3321
35 | 2691138.7398 | 1249770.6429
36 | 2691106.0754 | 1249783.3556
37 | 2691196.5188 | 1249877.662
38 | 2691109.1894 | 1249913.5601
39 | 2691085.601 | 1249946.2634
40 | 2691201.2864 | 1249935.2842
41 | 2691170.41 | 1249929.737
42 | 2691046.4395 | 1249892.4652
43 | 2691101.9462 | 1249781.9226
44 | 2691140.2214 | 1249767.7112
45 | 2691247.5385 | 1249818.2608
46 | 2691248.538 | 1249819.2613
47 | 2691235.4503 | 1249806.161
48 | 2691266.7753 | 1249858.8278
49 | 2691266.4397 | 1249783.935
50 | 2691229.6486 | 1249799.6923
51 | 2691221.3221 | 1249830.3419
52 | 2691267.6426 | 1249859.2241
53 | 2691222.7737 | 1249790.3872
54 | 2691210.9245 | 1249849.4251
55 | 2691217.8525 | 1249763.5966
56 | 2691196.9193 | 1249774.564
57 | 2691208.1889 | 1249854.6944
58 | 2691214.6768 | 1249727.2811
59 | 2691193.0722 | 1249772.2096
60 | 2691092.0966 | 1249778.4933
61 | 2691074.5641 | 1249772.3892
62 | 2691056.8148 | 1249766.2096
63 | 2691031.8113 | 1249757.5044
64 | 2691032.4717 | 1249734.9306
65 | 2691116.3695 | 1249755.8355
66 | 2691150.525 | 1249747.3208
67 | 2691040.5951 | 1249718.2167
68 | 2691075.3877 | 1249712.9214
69 | 2691094.8834 | 1249718.9916
70 | 2691111.1495 | 1249723.097
71 | 2691119.5695 | 1249728.9572
72 | 2691165.808 | 1249756.1625
73 | 2691175.3232 | 1249736.7062
74 | 2691183.0905 | 1249714.8751
75 | 2691149.2024 | 1249746.5481
76 | 2691223.4789 | 1249720.5353
77 | 2691181.7372 | 1249709.2829
78 | 2691192.9679 | 1249693.9217
79 | 2691186.1206 | 1249688.9061
80 | 2691239.2972 | 1249698.7239
81 | 2691248.4532 | 1249669.6089
82 | 2691249.1118 | 1249632.281
83 | 2691248.083 | 1249600.8616
84 | 2691293.7962 | 1249620.2586
85 | 2691178.139 | 1249684.2621
86 | 2691166.2879 | 1249557.1501
87 | 2691293.9972 | 1249620.1006
88 | 2691158.5148 | 1249672.8438
89 | 2691162.6359 | 1249559.8335
90 | 2691121.0042 | 1249746.8903
91 | 2691111.9495 | 1249764.1256
92 | 2690880.9295 | 1249999.3675
93 | 2690862.1771 | 1250017.4546
94 | 2690894.0112 | 1249986.7499
95 | 2690902.8773 | 1249978.1983
96 | 2690911.0941 | 1249970.273
97 | 2690881.6098 | 1250036.8167
98 | 2690909.402 | 1250033.9371
99 | 2690920.5388 | 1249961.1634
100 | 2690889.2256 | 1250070.5796
101 | 2690920.2094 | 1250067.3804
102 | 2690935.3116 | 1250031.2526
103 | 2690934.1269 | 1249951.2685
104 | 2690940.1161 | 1249948.9496
105 | 2690957.4444 | 1249947.691
106 | 2690959.7973 | 1249947.8551
107 | 2690980.908 | 1249953.5245
108 | 2690987.6738 | 1249955.7296
109 | 2691011.1518 | 1249963.3816
110 | 2690946.5964 | 1250064.6559
111 | 2690965.161 | 1250028.16
112 | 2691162.2388 | 1249945.3852
113 | 2691157.0455 | 1249955.9169
114 | 2691176.3364 | 1249953.766
115 | 2691229.2151 | 1249953.712
116 | 2691150.8052 | 1249968.5715
117 | 2691188.5837 | 1249961.0468
118 | 2691140.8552 | 1249988.7657
119 | 2691114.4221 | 1249955.7023
120 | 2691184.3213 | 1249970.6194
121 | 2691133.5244 | 1250003.7327
122 | 2691189.8609 | 1249982.2481
123 | 2691014.1289 | 1249964.3519
124 | 2691034.4673 | 1249970.9806
125 | 2691142.3286 | 1250006.1699
126 | 2691123.1456 | 1250027.0798
127 | 2691166.5504 | 1250006.4166
128 | 2691107.3665 | 1250020.6381
129 | 2691122.4673 | 1250043.1928
130 | 2690972.6235 | 1250061.9685
131 | 2690996.6151 | 1250059.4913
132 | 2691024.5351 | 1250056.6085
133 | 2691048.363 | 1250054.0057
134 | 2691075.8283 | 1250050.8613
135 | 2691106.6801 | 1250045.2266
136 | 2691126.1357 | 1250083.5133
137 | 2691127.3531 | 1250087.8131
138 | 2691097.2322 | 1250016.7514
139 | 2691086.2736 | 1249988.9396
140 | 2691078.0368 | 1250016.465
141 | 2691030.5333 | 1250021.3868
142 | 2691023.6925 | 1250022.0956
143 | 2691049.5996 | 1250019.4114
144 | 2690996.6461 | 1250024.8978
145 | 2690985.8948 | 1250026.0118
146 | 2690979.6601 | 1250026.6577
147 | 2691067.4957 | 1249981.7452
148 | 2691035.5674 | 1249971.3391
149 | 2691220.9022 | 1249989.4409
150 | 2691155.955 | 1249671.3544
151 | 2691086.8542 | 1249882.4451

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97945 | -0.39412 | 0.0070574 | 0.0017687
1 | 0.97943 | -0.39446 | 0.0052543 | 0.0013169
2 | 0.97985 | -0.38624 | 0 | 0
3 | 0.9802 | -0.37939 | 0 | 0
4 | 0.98094 | -0.36491 | 0 | 0
5 | 0.97867 | -0.40919 | 0.004218 | 0.0010571
6 | 0.97619 | -0.45786 | 0 | 0
7 | 0.97709 | -0.44023 | 0 | 0
8 | 0.97411 | -0.49871 | 0.042385 | 0.010623
9 | 0.983 | -0.32482 | 0.035527 | 0.0089039
10 | 0.98358 | -0.31356 | 0 | 0
11 | 0.98605 | -0.26569 | 0 | 0
12 | 0.98114 | -0.36115 | 0 | 0
13 | 0.98068 | -0.37018 | 0.039384 | 0.0098706
14 | 0.98735 | -0.2406 | 0.02002 | 0.0050176
15 | 0.98879 | -0.21276 | 0 | 0
16 | 0.97646 | -0.45199 | 0.0063979 | 0.0016035
17 | 0.97708 | -0.43997 | 0.0081341 | 0.0020386
18 | 0.9762 | -0.45712 | 0 | 0
19 | 0.97711 | -0.43927 | 0 | 0
20 | 0.97555 | -0.46984 | 0 | 0
21 | 0.97745 | -0.43272 | 0 | 0
22 | 0.97535 | -0.47392 | 0.0058763 | 0.0014727
23 | 0.97519 | -0.47698 | 0.0094322 | 0.0023639
24 | 0.9741 | -0.49855 | 0.013081 | 0.0032784
25 | 0.97418 | -0.49684 | 0 | 0
26 | 0.9779 | -0.42391 | 0.011994 | 0.0030059
27 | 0.97867 | -0.40881 | 0 | 0
28 | 0.97847 | -0.41261 | 0.0022881 | 0.00057345
29 | 0.97977 | -0.38728 | 0 | 0
30 | 0.97985 | -0.38567 | 0 | 0
31 | 0.99517 | -0.091146 | 0 | 0
32 | 1 | 0 | -0.5576 | -0.14367
33 | 0.99242 | -0.14338 | 0 | 0
34 | 0.97492 | -0.48231 | 0.0056567 | 0.0014177
35 | 0.97392 | -0.5021 | 0.0055439 | 0.0013894
36 | 0.97452 | -0.49028 | 0.0021981 | 0.00055091
37 | 0.97832 | -0.4156 | 0.0018671 | 0.00046794
38 | 0.98673 | -0.25256 | 0.015492 | 0.0038827
39 | 0.98731 | -0.24121 | 0 | 0
40 | 0.97942 | -0.39413 | 0.0077846 | 0.001951
41 | 0.98056 | -0.37178 | 0.0020821 | 0.00052182
42 | 0.9919 | -0.15341 | 0.020922 | 0.0052437
43 | 0.97458 | -0.48903 | 0 | 0
44 | 0.97388 | -0.50279 | 0 | 0
45 | 0.97576 | -0.46589 | 0.0059845 | 0.0014998
46 | 0.97575 | -0.46602 | 0 | 0
47 | 0.97593 | -0.46242 | 0 | 0
48 | 0.97552 | -0.47053 | 0.0035068 | 0.00087889
49 | 0.97546 | -0.47182 | 0.013089 | 0.0032805
50 | 0.97552 | -0.47061 | 0.0025087 | 0.00062874
51 | 0.97692 | -0.44306 | 0.0045516 | 0.0011407
52 | 0.97552 | -0.47056 | 0.0015931 | 0.00039926
53 | 0.97499 | -0.48098 | 0 | 0
54 | 0.97773 | -0.42716 | 0.01047 | 0.002624
55 | 0.97416 | -0.49744 | 0.0094712 | 0.0023737
56 | 0.97454 | -0.4899 | 0.012723 | 0.0031886
57 | 0.97783 | -0.42519 | 0.011509 | 0.0028845
58 | 0.97336 | -0.51314 | 0 | 0
59 | 0.97452 | -0.49017 | 0.0033143 | 0.00083065
60 | 0.97444 | -0.49177 | 0.002738 | 0.00068621
61 | 0.97424 | -0.49572 | 0.0027398 | 0.00068667
62 | 0.97409 | -0.49877 | 0.0027398 | 0.00068667
63 | 0.97394 | -0.50173 | 0 | 0
64 | 0.97377 | -0.50506 | 0.0031493 | 0.0007893
65 | 0.97378 | -0.50481 | 0 | 0
66 | 0.9736 | -0.50833 | 0 | 0
67 | 0.97372 | -0.50607 | 0.002943 | 0.00073759
68 | 0.97305 | -0.51914 | 0.0027409 | 0.00068695
69 | 0.9731 | -0.51811 | 0.0027399 | 0.00068667
70 | 0.97319 | -0.51641 | 0 | 0
71 | 0.97324 | -0.51537 | 0.0048441 | 0.0012141
72 | 0.97302 | -0.51975 | 0 | 0
73 | 0.97231 | -0.5338 | 0.0020494 | 0.00051364
74 | 0.97157 | -0.54837 | 0.013549 | 0.0033958
75 | 0.97357 | -0.50883 | 0.0072617 | 0.0018199
76 | 0.97312 | -0.51792 | 0.010105 | 0.0025325
77 | 0.97142 | -0.55137 | 0.004125 | 0.0010338
78 | 0.97114 | -0.55682 | 0 | 0
79 | 0.97102 | -0.55926 | 0.00073559 | 0.00018436
80 | 0.97278 | -0.52462 | 0.0044692 | 0.0011201
81 | 0.97253 | -0.5296 | 0.001514 | 0.00037946
82 | 0.97227 | -0.53466 | 0.0010624 | 0.00026627
83 | 0.97212 | -0.53773 | 0.00073499 | 0.00018421
84 | 0.97223 | -0.53548 | 0.00045528 | 0.0001141
85 | 0.97089 | -0.56178 | 0.0051644 | 0.0012943
86 | 0.97172 | -0.54555 | 0.0028011 | 0.00070202
87 | 0.97223 | -0.53548 | 0.00050732 | 0.00012715
88 | 0.97069 | -0.5658 | 0.0062388 | 0.0015636
89 | 0.97171 | -0.5457 | 0.0017655 | 0.00044249
90 | 0.97375 | -0.50531 | 0.0026996 | 0.00067659
91 | 0.97377 | -0.50506 | 0.0014368 | 0.0003601
92 | 0.97318 | -0.51684 | 0.001069 | 0.00026792
93 | 0.97314 | -0.51763 | 0.0016288 | 0.00040821
94 | 0.97322 | -0.51594 | 0.0011111 | 0.00027846
95 | 0.97327 | -0.51508 | 0.00091145 | 0.00022843
96 | 0.97332 | -0.51409 | 0.0010469 | 0.00026238
97 | 0.97561 | -0.46891 | 0.0017333 | 0.00043442
98 | 0.97566 | -0.46803 | 0.0015379 | 0.00038544
99 | 0.97339 | -0.51269 | 0.00091883 | 0.00023028
100 | 0.9768 | -0.44555 | 0.0014285 | 0.00035802
101 | 0.97684 | -0.44473 | 0.0015223 | 0.00038153
102 | 0.97574 | -0.46647 | 0.0019379 | 0.00048569
103 | 0.97349 | -0.51061 | 0.00091971 | 0.0002305
104 | 0.97354 | -0.50971 | 0.0017424 | 0.00043669
105 | 0.97369 | -0.50671 | 0.0018682 | 0.00046823
106 | 0.97372 | -0.50622 | 0.0011224 | 0.00028131
107 | 0.97397 | -0.50126 | 0.001741 | 0.00043634
108 | 0.97406 | -0.49942 | 0.00094233 | 0.00023617
109 | 0.97441 | -0.4926 | 0.0028892 | 0.0007241
110 | 0.97692 | -0.4433 | 0.0015671 | 0.00039275
111 | 0.97588 | -0.4636 | 0.0015379 | 0.00038543
112 | 0.98143 | -0.35494 | 0 | 0
113 | 0.98204 | -0.34305 | 0.0026015 | 0.000652
114 | 0.98118 | -0.35984 | 0.0018687 | 0.00046833
115 | 0.97919 | -0.39874 | 0.0075463 | 0.0018913
116 | 0.98278 | -0.32866 | 0 | 0
117 | 0.98099 | -0.36361 | 0.0045573 | 0.0011422
118 | 0.98133 | -0.35697 | 0.0013895 | 0.00034823
119 | 0.98531 | -0.27973 | 0.0024064 | 0.00060309
120 | 0.98089 | -0.36552 | 0.0007842 | 0.00019654
121 | 0.98027 | -0.37756 | 0 | 0
122 | 0.98074 | -0.36852 | 0.0028004 | 0.00070186
123 | 0.97446 | -0.49157 | 0.0022075 | 0.00055325
124 | 0.97486 | -0.48367 | 0.0046442 | 0.0011639
125 | 0.98026 | -0.37772 | 0 | 0
126 | 0.97867 | -0.4088 | 0 | 0
127 | 0.98024 | -0.37814 | 0.00093494 | 0.00023432
128 | 0.97784 | -0.42509 | 0.0015272 | 0.00038274
129 | 0.97845 | -0.41318 | 0 | 0
130 | 0.97703 | -0.44114 | 0.0015391 | 0.00038574
131 | 0.97716 | -0.43848 | 0.0024983 | 0.00062612
132 | 0.97738 | -0.43409 | 0.0010733 | 0.00026899
133 | 0.9776 | -0.42988 | 0.0016705 | 0.00041867
134 | 0.97789 | -0.42418 | 0.00089676 | 0.00022475
135 | 0.97825 | -0.41713 | 0.0013153 | 0.00032964
136 | 0.9784 | -0.41412 | 0 | 0
137 | 0.9784 | -0.41423 | 0.0012735 | 0.00031917
138 | 0.97733 | -0.43518 | 0 | 0
139 | 0.97633 | -0.45473 | 0.0045208 | 0.001133
140 | 0.97704 | -0.44088 | 0.0017294 | 0.00043342
141 | 0.97644 | -0.45264 | 0.00056285 | 0.00014106
142 | 0.97636 | -0.45408 | 0.0012383 | 0.00031034
143 | 0.97665 | -0.44842 | 0.0024149 | 0.00060522
144 | 0.97611 | -0.45917 | 0.001201 | 0.000301
145 | 0.97602 | -0.46095 | 0.0016257 | 0.00040743
146 | 0.97597 | -0.4618 | 0.00065464 | 0.00016407
147 | 0.97576 | -0.46589 | 0.0021872 | 0.00054817
148 | 0.97489 | -0.48315 | 0.0032785 | 0.00082167
149 | 0.98054 | -0.37232 | 0.0064838 | 0.001625
150 | 0.97068 | -0.56599 | 0.0033545 | 0.00084071
151 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0052544 | 0.0013169 | -0.0052543 | -0.0013169 | 8.6196e-08 | 9.7689e-09 | 0.0079827 | 0.0079827 | 0.0079827 | 0.97945 | -0.39412 | 0.97943 | -0.39446 | 2.193
1 | -0.012312 | -0.0030856 | 0.012316 | 0.0030881 | 4.6244e-06 | 2.5158e-06 | 0.018704 | 0.018704 | 0.018704 | 0.97945 | -0.39412 | 0.97985 | -0.38624 | 5.1386
2 | -0.012316 | -0.0030881 | 0.01232 | 0.0030903 | 4.0206e-06 | 2.187e-06 | 0.018704 | 0.018704 | 0.018704 | 0.97985 | -0.38624 | 0.9802 | -0.37939 | 5.1386
3 | -0.059171 | -0.014927 | 0.059213 | 0.014953 | 4.1041e-05 | 2.5582e-05 | 0.089862 | 0.089862 | 0.089862 | 0.9802 | -0.37939 | 0.98094 | -0.36491 | 12.3437
4 | 0.046851 | 0.011837 | -0.046784 | -0.011795 | 6.6818e-05 | 4.2321e-05 | 0.071158 | 0.071158 | 0.071158 | 0.9802 | -0.37939 | 0.97867 | -0.40919 | 19.5489
5 | -0.059213 | -0.014953 | 0.059327 | 0.015024 | 0.00011398 | 7.1042e-05 | 0.089862 | 0.089861 | 0.089862 | 0.98094 | -0.36491 | 0.983 | -0.32482 | 12.3436
6 | 0.042566 | 0.010737 | -0.042503 | -0.010697 | 6.3153e-05 | 3.9914e-05 | 0.064745 | 0.064745 | 0.064745 | 0.97867 | -0.40919 | 0.97709 | -0.44023 | 17.787
7 | -0.042467 | -0.010675 | 0.042503 | 0.010697 | 3.5781e-05 | 2.2615e-05 | 0.064745 | 0.064745 | 0.064745 | 0.97619 | -0.45786 | 0.97709 | -0.44023 | 17.7871
8 | 0.042467 | 0.010675 | -0.042385 | -0.010623 | 8.2674e-05 | 5.2255e-05 | 0.064745 | 0.064745 | 0.064745 | 0.97619 | -0.45786 | 0.97411 | -0.49871 | 17.7871
9 | -0.094853 | -0.023928 | 0.094904 | 0.023958 | 5.1159e-05 | 3.0645e-05 | 0.14364 | 0.14364 | 0.14364 | 0.983 | -0.32482 | 0.98358 | -0.31356 | 7.8923
10 | -0.1344 | -0.033896 | 0.1347 | 0.034087 | 0.00030876 | 0.00019128 | 0.2034 | 0.20339 | 0.2034 | 0.98358 | -0.31356 | 0.98605 | -0.26569 | 11.1757
11 | 0.039491 | 0.0099378 | -0.039401 | -0.0098813 | 8.9594e-05 | 5.6493e-05 | 0.059758 | 0.059759 | 0.059759 | 0.98358 | -0.31356 | 0.98114 | -0.36115 | 16.4172
12 | -0.1347 | -0.034087 | 0.13487 | 0.034188 | 0.00016236 | 0.00010057 | 0.20339 | 0.20339 | 0.20339 | 0.98605 | -0.26569 | 0.98735 | -0.2406 | 11.1755
13 | 0.039401 | 0.0098813 | -0.039384 | -0.0098706 | 1.6933e-05 | 1.0678e-05 | 0.059759 | 0.059759 | 0.059759 | 0.98114 | -0.36115 | 0.98068 | -0.37018 | 16.4172
14 | -0.15489 | -0.039205 | 0.15509 | 0.039335 | 0.00020733 | 0.00012944 | 0.23357 | 0.23356 | 0.23357 | 0.98735 | -0.2406 | 0.98879 | -0.21276 | 12.8333
15 | -0.52938 | -0.13482 | 0.53116 | 0.13596 | 0.0017779 | 0.0011355 | 0.79743 | 0.79742 | 0.79743 | 0.98879 | -0.21276 | 0.99242 | -0.14338 | 43.8146
16 | 0.37429 | 0.095486 | -0.37377 | -0.095159 | 0.00051354 | 0.00032728 | 0.56386 | 0.56386 | 0.56386 | 0.98879 | -0.21276 | 0.98731 | -0.24121 | 30.9814
17 | -0.11978 | -0.030136 | 0.11985 | 0.030178 | 6.8837e-05 | 4.2332e-05 | 0.18257 | 0.18257 | 0.18257 | 0.97646 | -0.45199 | 0.97708 | -0.43997 | 10.0312
18 | 0.11338 | 0.028532 | -0.11335 | -0.028515 | 2.776e-05 | 1.6991e-05 | 0.17282 | 0.17282 | 0.17282 | 0.97646 | -0.45199 | 0.9762 | -0.45712 | 9.4955
19 | -0.12798 | -0.032216 | 0.12798 | 0.032219 | 4.2893e-06 | 2.6509e-06 | 0.19495 | 0.19495 | 0.19495 | 0.97708 | -0.43997 | 0.97711 | -0.43927 | 10.7118
20 | 0.11335 | 0.028515 | -0.11328 | -0.028473 | 6.8864e-05 | 4.2152e-05 | 0.17282 | 0.17282 | 0.17282 | 0.9762 | -0.45712 | 0.97555 | -0.46984 | 9.4956
21 | -0.12798 | -0.032219 | 0.12802 | 0.032244 | 4.0067e-05 | 2.4762e-05 | 0.19495 | 0.19495 | 0.19495 | 0.97711 | -0.43927 | 0.97745 | -0.43272 | 10.7118
22 | 0.0058774 | 0.001473 | -0.0058763 | -0.0014727 | 1.1433e-06 | 2.5817e-07 | 0.0089648 | 0.008965 | 0.008965 | 0.97555 | -0.46984 | 0.97535 | -0.47392 | 2.4629
23 | 0.1074 | 0.027 | -0.10737 | -0.026978 | 3.6628e-05 | 2.2307e-05 | 0.16385 | 0.16385 | 0.16385 | 0.97555 | -0.46984 | 0.97519 | -0.47698 | 9.003
24 | -0.12802 | -0.032244 | 0.12808 | 0.032277 | 5.3979e-05 | 3.3359e-05 | 0.19495 | 0.19495 | 0.19495 | 0.97745 | -0.43272 | 0.9779 | -0.42391 | 10.7118
25 | 0.097936 | 0.024614 | -0.097911 | -0.024599 | 2.4896e-05 | 1.5007e-05 | 0.14946 | 0.14946 | 0.14946 | 0.97519 | -0.47698 | 0.97492 | -0.48231 | 8.2122
26 | -0.013081 | -0.0032784 | 0.013082 | 0.003279 | 1.0661e-06 | 5.9365e-07 | 0.019982 | 0.019982 | 0.019982 | 0.9741 | -0.49855 | 0.97418 | -0.49684 | 5.4897
27 | 0.062599 | 0.015727 | -0.062583 | -0.015719 | 1.5724e-05 | 8.6365e-06 | 0.095631 | 0.095631 | 0.095631 | 0.97418 | -0.49684 | 0.97392 | -0.5021 | 5.2545
28 | -0.075681 | -0.019006 | 0.075705 | 0.01902 | 2.3688e-05 | 1.3689e-05 | 0.11561 | 0.11561 | 0.11561 | 0.97418 | -0.49684 | 0.97452 | -0.49028 | 6.3524
29 | -0.14007 | -0.035283 | 0.14017 | 0.035346 | 0.0001012 | 6.2903e-05 | 0.2132 | 0.2132 | 0.2132 | 0.9779 | -0.42391 | 0.97867 | -0.40881 | 11.7145
30 | 0.10663 | 0.026846 | -0.10661 | -0.026834 | 1.9336e-05 | 1.176e-05 | 0.16217 | 0.16217 | 0.16217 | 0.97867 | -0.40881 | 0.97847 | -0.41261 | 8.9105
31 | -0.2468 | -0.062192 | 0.24706 | 0.062354 | 0.0002545 | 0.00016137 | 0.37538 | 0.37537 | 0.37538 | 0.97867 | -0.40881 | 0.97977 | -0.38728 | 20.625
32 | 0.10432 | 0.026261 | -0.10431 | -0.026252 | 1.4944e-05 | 9.067e-06 | 0.15869 | 0.15869 | 0.15869 | 0.97847 | -0.41261 | 0.97832 | -0.4156 | 8.7194
33 | -0.24706 | -0.062354 | 0.24708 | 0.062366 | 1.9086e-05 | 1.2101e-05 | 0.37537 | 0.37537 | 0.37537 | 0.97977 | -0.38728 | 0.97985 | -0.38567 | 20.625
34 | 0.015339 | 0.0038465 | -0.015333 | -0.0038429 | 6.1858e-06 | 3.5762e-06 | 0.023294 | 0.023295 | 0.023295 | 0.97985 | -0.38567 | 0.97942 | -0.39413 | 6.3996
35 | -0.26242 | -0.066212 | 0.26259 | 0.066323 | 0.00017466 | 0.00011086 | 0.39867 | 0.39867 | 0.39867 | 0.97985 | -0.38567 | 0.98056 | -0.37178 | 21.9049
36 | -0.55349 | -0.1421 | 0.55595 | 0.14367 | 0.0024606 | 0.0015717 | 0.82881 | 0.82881 | 0.82881 | 0.99517 | -0.091146 | 1 | 0 | 45.539
37 | 0.55349 | 0.1421 | -0.55209 | -0.14121 | 0.0013995 | 0.00089394 | 0.82881 | 0.82881 | 0.82881 | 0.99517 | -0.091146 | 0.99242 | -0.14338 | 45.5391
38 | 0.020932 | 0.0052497 | -0.020922 | -0.0052437 | 9.9976e-06 | 6.049e-06 | 0.031387 | 0.031387 | 0.031387 | 0.99242 | -0.14338 | 0.9919 | -0.15341 | 8.6228
39 | 0.092254 | 0.023181 | -0.092225 | -0.023163 | 2.9588e-05 | 1.7697e-05 | 0.14083 | 0.14083 | 0.14083 | 0.97492 | -0.48231 | 0.97458 | -0.48903 | 7.7379
40 | 0.057039 | 0.014329 | -0.057037 | -0.014328 | 1.8716e-06 | 9.9345e-07 | 0.087161 | 0.087161 | 0.087161 | 0.97392 | -0.5021 | 0.97388 | -0.50279 | 4.7891
41 | -0.077903 | -0.019571 | 0.077907 | 0.019574 | 4.6397e-06 | 2.6971e-06 | 0.11897 | 0.11897 | 0.11897 | 0.97452 | -0.49028 | 0.97458 | -0.48903 | 6.5368
42 | 0.10244 | 0.025784 | -0.10239 | -0.025756 | 4.6935e-05 | 2.8421e-05 | 0.15585 | 0.15585 | 0.15585 | 0.97832 | -0.4156 | 0.97783 | -0.42519 | 8.5634
43 | -0.015492 | -0.0038827 | 0.015501 | 0.0038875 | 8.379e-06 | 4.8394e-06 | 0.023363 | 0.023363 | 0.023363 | 0.98673 | -0.25256 | 0.98731 | -0.24121 | 6.4183
44 | 0.35827 | 0.091271 | -0.35761 | -0.090848 | 0.00066449 | 0.00042334 | 0.5405 | 0.5405 | 0.5405 | 0.98731 | -0.24121 | 0.98531 | -0.27973 | 29.6978
45 | 0.0075479 | 0.0018919 | -0.0075463 | -0.0018913 | 1.6547e-06 | 6.3682e-07 | 0.011467 | 0.011468 | 0.011468 | 0.97942 | -0.39413 | 0.97919 | -0.39874 | 3.1505
46 | -0.26467 | -0.066845 | 0.26489 | 0.066981 | 0.00021378 | 0.0001357 | 0.40183 | 0.40183 | 0.40183 | 0.98056 | -0.37178 | 0.98143 | -0.35494 | 22.0785
47 | 0.014317 | 0.0035896 | -0.014315 | -0.0035885 | 1.8691e-06 | 1.0663e-06 | 0.021861 | 0.021861 | 0.021861 | 0.97458 | -0.48903 | 0.97444 | -0.49177 | 6.0057
48 | 0.0041369 | 0.0010364 | -0.0041365 | -0.0010365 | 3.9824e-07 | -7.5834e-08 | 0.0063208 | 0.0063209 | 0.0063209 | 0.97388 | -0.50279 | 0.97378 | -0.50481 | 1.7365
49 | 0.0529 | 0.013292 | -0.052886 | -0.013284 | 1.399e-05 | 7.8176e-06 | 0.08084 | 0.08084 | 0.08084 | 0.97388 | -0.50279 | 0.9736 | -0.50833 | 5.5522
50 | 0.005101 | 0.0012782 | -0.005101 | -0.0012782 | 3.209e-08 | 2.8734e-09 | 0.0077789 | 0.0077789 | 0.0077789 | 0.97576 | -0.46589 | 0.97575 | -0.46602 | 2.1371
51 | -0.011085 | -0.0027781 | 0.011087 | 0.002779 | 1.833e-06 | 9.5941e-07 | 0.016905 | 0.016905 | 0.016905 | 0.97576 | -0.46589 | 0.97593 | -0.46242 | 4.6443
52 | 0.005101 | 0.0012782 | -0.0050999 | -0.0012781 | 1.097e-06 | 9.8388e-08 | 0.0077789 | 0.0077791 | 0.0077791 | 0.97575 | -0.46602 | 0.97552 | -0.47053 | 2.1371
53 | 0.013095 | 0.0032837 | -0.013089 | -0.0032805 | 5.8648e-06 | 3.2635e-06 | 0.019967 | 0.019967 | 0.019967 | 0.97593 | -0.46242 | 0.97546 | -0.47182 | 5.4854
54 | 0.051542 | 0.012956 | -0.051522 | -0.012943 | 2.0144e-05 | 1.2784e-05 | 0.078601 | 0.078601 | 0.078601 | 0.97593 | -0.46242 | 0.97552 | -0.47061 | 21.5936
55 | -0.075725 | -0.019019 | 0.075795 | 0.019063 | 7.0029e-05 | 4.4118e-05 | 0.11547 | 0.11547 | 0.11547 | 0.97593 | -0.46242 | 0.97692 | -0.44306 | 15.8616
56 | 0.0015931 | 0.00039925 | -0.0015931 | -0.00039926 | 2.1114e-09 | -1.0554e-08 | 0.00243 | 0.00243 | 0.00243 | 0.97552 | -0.47053 | 0.97552 | -0.47056 | 0.66759
57 | 0.049013 | 0.012314 | -0.048989 | -0.012299 | 2.4257e-05 | 1.538e-05 | 0.074774 | 0.074774 | 0.074774 | 0.97552 | -0.47061 | 0.97499 | -0.48098 | 20.5423
58 | -0.080346 | -0.020203 | 0.080407 | 0.020242 | 6.1056e-05 | 3.8531e-05 | 0.12241 | 0.1224 | 0.12241 | 0.97692 | -0.44306 | 0.97773 | -0.42716 | 16.8139
59 | 0.032945 | 0.0082757 | -0.032919 | -0.0082595 | 2.5855e-05 | 1.6207e-05 | 0.050287 | 0.050287 | 0.050287 | 0.97499 | -0.48098 | 0.97416 | -0.49744 | 13.8152
60 | 0.016044 | 0.0040232 | -0.016037 | -0.0040193 | 6.8158e-06 | 3.9843e-06 | 0.024487 | 0.024487 | 0.024487 | 0.97499 | -0.48098 | 0.97454 | -0.4899 | 6.7272
61 | -0.090877 | -0.022866 | 0.090886 | 0.022871 | 8.5217e-06 | 5.0816e-06 | 0.13834 | 0.13834 | 0.13834 | 0.97773 | -0.42716 | 0.97783 | -0.42519 | 7.6011
62 | 0.023448 | 0.0058858 | -0.023431 | -0.005875 | 1.7542e-05 | 1.0773e-05 | 0.03582 | 0.03582 | 0.03582 | 0.97416 | -0.49744 | 0.97336 | -0.51314 | 9.8407
63 | 0.0033144 | 0.00083062 | -0.0033143 | -0.00083065 | 4.3317e-08 | -2.8474e-08 | 0.0050607 | 0.0050607 | 0.0050607 | 0.97454 | -0.4899 | 0.97452 | -0.49017 | 1.3903
64 | 0.023431 | 0.005875 | -0.023425 | -0.0058717 | 5.336e-06 | 3.2772e-06 | 0.03582 | 0.03582 | 0.03582 | 0.97336 | -0.51314 | 0.97312 | -0.51792 | 9.8408
65 | 0.011577 | 0.0029023 | -0.011575 | -0.0029011 | 2.176e-06 | 1.1614e-06 | 0.01768 | 0.01768 | 0.01768 | 0.97444 | -0.49177 | 0.97424 | -0.49572 | 4.8571
66 | 0.0088355 | 0.0022145 | -0.0088342 | -0.0022139 | 1.2835e-06 | 5.8746e-07 | 0.013495 | 0.013495 | 0.013495 | 0.97424 | -0.49572 | 0.97409 | -0.49877 | 3.7074
67 | 0.0060943 | 0.0015272 | -0.0060935 | -0.001527 | 8.6049e-07 | 2.212e-07 | 0.0093096 | 0.0093098 | 0.0093098 | 0.97409 | -0.49877 | 0.97394 | -0.50173 | 2.5576
68 | 0.0060935 | 0.001527 | -0.0060925 | -0.0015267 | 9.6674e-07 | 2.4864e-07 | 0.0093098 | 0.0093099 | 0.0093099 | 0.97394 | -0.50173 | 0.97377 | -0.50506 | 2.5577
69 | 0.0029432 | 0.00073745 | -0.002943 | -0.00073759 | 1.4096e-07 | -1.4095e-07 | 0.0044974 | 0.0044975 | 0.0044975 | 0.97377 | -0.50506 | 0.97372 | -0.50607 | 1.2356
70 | 0.0026997 | 0.0006765 | -0.0026996 | -0.00067659 | 6.4295e-08 | -8.4179e-08 | 0.0041253 | 0.0041254 | 0.0041254 | 0.97378 | -0.50481 | 0.97375 | -0.50531 | 1.1333
71 | 0.0014368 | 0.00035999 | -0.0014368 | -0.0003601 | 1.6983e-08 | -1.06e-07 | 0.0021956 | 0.0021956 | 0.0021956 | 0.97378 | -0.50481 | 0.97377 | -0.50506 | 0.60319
72 | 0.017591 | 0.0044094 | -0.017591 | -0.0044092 | 4.1521e-07 | 2.4669e-07 | 0.026886 | 0.026886 | 0.026886 | 0.9736 | -0.50833 | 0.97357 | -0.50883 | 7.3862
73 | 0.035295 | 0.0088747 | -0.035276 | -0.0088626 | 1.9232e-05 | 1.2089e-05 | 0.053955 | 0.053955 | 0.053955 | 0.9736 | -0.50833 | 0.97302 | -0.51975 | 14.8227
74 | -0.0027409 | -0.00068695 | 0.0027411 | 0.00068678 | 1.3464e-07 | -1.6771e-07 | 0.0041915 | 0.0041914 | 0.0041915 | 0.97305 | -0.51914 | 0.9731 | -0.51811 | 1.1515
75 | -0.0054809 | -0.0013735 | 0.0054814 | 0.0013735 | 4.4278e-07 | 7.4531e-08 | 0.0083811 | 0.008381 | 0.0083811 | 0.9731 | -0.51811 | 0.97319 | -0.51641 | 2.3025
76 | -0.0054814 | -0.0013735 | 0.0054816 | 0.0013736 | 2.7021e-07 | 4.5464e-08 | 0.008381 | 0.0083809 | 0.008381 | 0.97319 | -0.51641 | 0.97324 | -0.51537 | 2.3025
77 | -0.010326 | -0.0025876 | 0.010329 | 0.0025893 | 3.2216e-06 | 1.6334e-06 | 0.015787 | 0.015787 | 0.015787 | 0.97324 | -0.51537 | 0.97357 | -0.50883 | 4.3372
78 | 0.035276 | 0.0088626 | -0.035253 | -0.0088477 | 2.3644e-05 | 1.4863e-05 | 0.053955 | 0.053955 | 0.053955 | 0.97302 | -0.51975 | 0.97231 | -0.5338 | 14.8228
79 | 0.033203 | 0.0083341 | -0.03318 | -0.0083196 | 2.3053e-05 | 1.4459e-05 | 0.050818 | 0.050818 | 0.050818 | 0.97231 | -0.5338 | 0.97157 | -0.54837 | 13.9611
80 | 0.019631 | 0.0049238 | -0.019628 | -0.0049221 | 2.8128e-06 | 1.6974e-06 | 0.030067 | 0.030067 | 0.030067 | 0.97157 | -0.54837 | 0.97142 | -0.55137 | 8.2601
81 | 0.01332 | 0.0033392 | -0.013316 | -0.0033368 | 4.2503e-06 | 2.3809e-06 | 0.020369 | 0.020369 | 0.020369 | 0.97312 | -0.51792 | 0.97278 | -0.52462 | 5.5959
82 | 0.015503 | 0.0038883 | -0.015499 | -0.0038859 | 4.0244e-06 | 2.3401e-06 | 0.023748 | 0.023748 | 0.023748 | 0.97142 | -0.55137 | 0.97114 | -0.55682 | 6.5242
83 | 0.015499 | 0.0038859 | -0.015497 | -0.0038849 | 1.7969e-06 | 1.0449e-06 | 0.023748 | 0.023748 | 0.023748 | 0.97114 | -0.55682 | 0.97102 | -0.55926 | 6.5242
84 | 0.014761 | 0.0037005 | -0.01476 | -0.0036995 | 1.772e-06 | 1.0199e-06 | 0.022621 | 0.022621 | 0.022621 | 0.97102 | -0.55926 | 0.97089 | -0.56178 | 6.2146
85 | 0.0088471 | 0.0022168 | -0.008845 | -0.0022158 | 2.1016e-06 | 9.6523e-07 | 0.013533 | 0.013533 | 0.013533 | 0.97278 | -0.52462 | 0.97253 | -0.5296 | 3.7178
86 | 0.0073309 | 0.0018363 | -0.0073292 | -0.0018357 | 1.7637e-06 | 6.65e-07 | 0.011216 | 0.011217 | 0.011217 | 0.97253 | -0.5296 | 0.97227 | -0.53466 | 3.0815
87 | 0.0053041 | 0.0013287 | -0.0053033 | -0.0013286 | 7.768e-07 | 1.0735e-07 | 0.0081175 | 0.0081176 | 0.0081176 | 0.97227 | -0.53466 | 0.97212 | -0.53773 | 2.2301
88 | 0.00096264 | 0.0002407 | -0.0009626 | -0.00024125 | 3.7659e-08 | -5.4975e-07 | 0.0014731 | 0.0014733 | 0.0014733 | 0.97227 | -0.53466 | 0.97223 | -0.53548 | 0.40475
89 | 0.0045683 | 0.0011444 | -0.0045666 | -0.0011445 | 1.7006e-06 | -6.0941e-08 | 0.0069926 | 0.006993 | 0.006993 | 0.97212 | -0.53773 | 0.97172 | -0.54555 | 1.9211
90 | 0.00050732 | 0.00012714 | -0.00050732 | -0.00012715 | 5.78e-11 | -3.134e-09 | 0.00077646 | 0.00077646 | 0.00077646 | 0.97223 | -0.53548 | 0.97223 | -0.53548 | 0.21331
91 | 0.0095951 | 0.0024052 | -0.0095933 | -0.0024043 | 1.8413e-06 | 8.9772e-07 | 0.014706 | 0.014706 | 0.014706 | 0.97089 | -0.56178 | 0.97069 | -0.5658 | 4.0401
92 | 0.0017656 | 0.00044244 | -0.0017655 | -0.00044249 | 1.2422e-08 | -4.8189e-08 | 0.0027036 | 0.0027036 | 0.0027036 | 0.97172 | -0.54555 | 0.97171 | -0.5457 | 0.74276
93 | 0.0033545 | 0.00084069 | -0.0033545 | -0.00084071 | 2.9367e-08 | -1.7814e-08 | 0.0051423 | 0.0051423 | 0.0051423 | 0.97069 | -0.5658 | 0.97068 | -0.56599 | 1.4127
94 | 0.0016288 | 0.00040792 | -0.0016288 | -0.00040821 | 6.0598e-08 | -2.8492e-07 | 0.0024904 | 0.0024905 | 0.0024905 | 0.97318 | -0.51684 | 0.97314 | -0.51763 | 0.68421
95 | -0.0026978 | -0.00067584 | 0.0026979 | 0.00067569 | 1.1597e-07 | -1.5162e-07 | 0.0041249 | 0.0041248 | 0.0041249 | 0.97318 | -0.51684 | 0.97322 | -0.51594 | 1.1332
96 | -0.003809 | -0.00095414 | 0.0038091 | 0.00095409 | 1.5666e-07 | -5.2812e-08 | 0.0058236 | 0.0058235 | 0.0058236 | 0.97322 | -0.51594 | 0.97327 | -0.51508 | 1.5999
97 | -0.0047206 | -0.0011825 | 0.0047208 | 0.0011825 | 2.2298e-07 | 8.2933e-10 | 0.0072171 | 0.007217 | 0.0072171 | 0.97327 | -0.51508 | 0.97332 | -0.51409 | 1.9827
98 | -0.0057677 | -0.0014449 | 0.0057681 | 0.001445 | 3.8258e-07 | 8.1752e-08 | 0.0088175 | 0.0088175 | 0.0088175 | 0.97332 | -0.51409 | 0.97339 | -0.51269 | 2.4224
99 | -0.0017333 | -0.00043442 | 0.0017334 | 0.00043411 | 7.3229e-08 | -3.0205e-07 | 0.0026437 | 0.0026436 | 0.0026437 | 0.97561 | -0.46891 | 0.97566 | -0.46803 | 0.7263
100 | -0.0032713 | -0.00081955 | 0.0032716 | 0.00081938 | 2.4314e-07 | -1.6972e-07 | 0.0049891 | 0.004989 | 0.0049891 | 0.97566 | -0.46803 | 0.97574 | -0.46647 | 1.3706
101 | -0.0066869 | -0.0016753 | 0.0066876 | 0.0016755 | 6.6275e-07 | 2.1389e-07 | 0.010222 | 0.010222 | 0.010222 | 0.97339 | -0.51269 | 0.97349 | -0.51061 | 2.8083
102 | -0.0014285 | -0.00035802 | 0.0014286 | 0.00035766 | 5.5311e-08 | -3.5452e-07 | 0.0021761 | 0.002176 | 0.0021761 | 0.9768 | -0.44555 | 0.97684 | -0.44473 | 0.59784
103 | -0.0029509 | -0.0007392 | 0.0029511 | 0.000739 | 2.0099e-07 | -2.0348e-07 | 0.004495 | 0.0044948 | 0.004495 | 0.97684 | -0.44473 | 0.97692 | -0.4433 | 1.2349
104 | -0.0052095 | -0.0013051 | 0.0052102 | 0.0013052 | 7.1023e-07 | 7.9666e-08 | 0.0079444 | 0.0079443 | 0.0079444 | 0.97574 | -0.46647 | 0.97588 | -0.4636 | 2.1825
105 | -0.0076073 | -0.001906 | 0.0076076 | 0.0019061 | 3.2617e-07 | 1.2876e-07 | 0.011628 | 0.011628 | 0.011628 | 0.97349 | -0.51061 | 0.97354 | -0.50971 | 3.1945
106 | -0.00935 | -0.0023428 | 0.0093514 | 0.0023434 | 1.3384e-06 | 6.3923e-07 | 0.014291 | 0.014291 | 0.014291 | 0.97354 | -0.50971 | 0.97369 | -0.50671 | 3.9261
107 | -0.01122 | -0.0028117 | 0.01122 | 0.0028118 | 2.6003e-07 | 1.3708e-07 | 0.017146 | 0.017146 | 0.017146 | 0.97369 | -0.50671 | 0.97372 | -0.50622 | 4.7104
108 | -0.012342 | -0.0030931 | 0.012345 | 0.0030947 | 2.9197e-06 | 1.5963e-06 | 0.018861 | 0.018861 | 0.018861 | 0.97372 | -0.50622 | 0.97397 | -0.50126 | 5.1817
109 | -0.014086 | -0.003531 | 0.014087 | 0.0035317 | 1.2359e-06 | 7.0244e-07 | 0.021521 | 0.021521 | 0.021521 | 0.97397 | -0.50126 | 0.97406 | -0.49942 | 5.9124
110 | -0.01503 | -0.0037679 | 0.015035 | 0.0037707 | 4.8818e-06 | 2.8169e-06 | 0.022961 | 0.02296 | 0.022961 | 0.97406 | -0.49942 | 0.97441 | -0.4926 | 6.3078
111 | -0.017924 | -0.0044948 | 0.017925 | 0.0044954 | 8.7979e-07 | 5.2406e-07 | 0.027373 | 0.027373 | 0.027373 | 0.97441 | -0.4926 | 0.97446 | -0.49157 | 7.5199
112 | -0.0045182 | -0.0011317 | 0.0045187 | 0.0011317 | 4.6468e-07 | -3.0247e-08 | 0.0068818 | 0.0068817 | 0.0068818 | 0.97692 | -0.4433 | 0.97703 | -0.44114 | 1.8906
113 | -0.0067481 | -0.0016906 | 0.0067487 | 0.0016908 | 5.787e-07 | 1.8823e-07 | 0.010289 | 0.010289 | 0.010289 | 0.97588 | -0.4636 | 0.97597 | -0.4618 | 2.8267
114 | -0.28139 | -0.07112 | 0.28155 | 0.071222 | 0.00016046 | 0.00010195 | 0.42685 | 0.42685 | 0.42685 | 0.98143 | -0.35494 | 0.98204 | -0.34305 | 23.4534
115 | 0.016504 | 0.0041391 | -0.016501 | -0.0041368 | 3.8514e-06 | 2.2577e-06 | 0.025024 | 0.025025 | 0.025025 | 0.98143 | -0.35494 | 0.98118 | -0.35984 | 6.8749
116 | -0.28415 | -0.071874 | 0.28435 | 0.071998 | 0.00019639 | 0.0001248 | 0.43079 | 0.43079 | 0.43079 | 0.98204 | -0.34305 | 0.98278 | -0.32866 | 23.67
117 | 0.014632 | 0.0036685 | -0.014629 | -0.003667 | 2.631e-06 | 1.5039e-06 | 0.022191 | 0.022191 | 0.022191 | 0.98118 | -0.35984 | 0.98099 | -0.36361 | 6.0963
118 | 0.070018 | 0.017715 | -0.069923 | -0.017654 | 9.4987e-05 | 6.0507e-05 | 0.10607 | 0.10607 | 0.10607 | 0.98278 | -0.32866 | 0.98133 | -0.35697 | 29.1409
119 | -0.35437 | -0.089713 | 0.3552 | 0.090245 | 0.00083454 | 0.00053165 | 0.53687 | 0.53687 | 0.53687 | 0.98278 | -0.32866 | 0.98531 | -0.27973 | 29.4982
120 | 0.010072 | 0.0025248 | -0.010071 | -0.0025244 | 9.1719e-07 | 4.5472e-07 | 0.015278 | 0.015278 | 0.015278 | 0.98099 | -0.36361 | 0.98089 | -0.36552 | 4.1972
121 | 0.068533 | 0.017306 | -0.068466 | -0.017263 | 6.7553e-05 | 4.3023e-05 | 0.10397 | 0.10397 | 0.10397 | 0.98133 | -0.35697 | 0.98027 | -0.37756 | 28.5621
122 | 0.0092868 | 0.0023278 | -0.0092854 | -0.0023272 | 1.3272e-06 | 6.2434e-07 | 0.014088 | 0.014088 | 0.014088 | 0.98089 | -0.36552 | 0.98074 | -0.36852 | 3.8704
123 | 0.00093496 | 0.00023391 | -0.00093496 | -0.00023402 | 6.8799e-09 | -1.1044e-07 | 0.0014191 | 0.0014191 | 0.0014191 | 0.98027 | -0.37756 | 0.98026 | -0.37772 | 0.38987
124 | 0.067531 | 0.017029 | -0.06743 | -0.016965 | 0.00010079 | 6.4182e-05 | 0.10255 | 0.10255 | 0.10255 | 0.98027 | -0.37756 | 0.97867 | -0.4088 | 28.1723
125 | 0.006485 | 0.0016253 | -0.0064838 | -0.001625 | 1.1748e-06 | 3.4363e-07 | 0.0098393 | 0.0098395 | 0.0098395 | 0.98074 | -0.36852 | 0.98054 | -0.37232 | 2.7032
126 | -0.020132 | -0.0050486 | 0.02014 | 0.0050532 | 7.5818e-06 | 4.5857e-06 | 0.030743 | 0.030743 | 0.030743 | 0.97446 | -0.49157 | 0.97486 | -0.48367 | 8.446
127 | -0.024784 | -0.0062171 | 0.024785 | 0.0062175 | 6.2107e-07 | 3.8306e-07 | 0.037832 | 0.037832 | 0.037832 | 0.97486 | -0.48367 | 0.97489 | -0.48315 | 10.3935
128 | 0.00093496 | 0.00023402 | -0.00093494 | -0.00023432 | 1.8554e-08 | -2.9781e-07 | 0.0014191 | 0.0014192 | 0.0014192 | 0.98026 | -0.37772 | 0.98024 | -0.37814 | 0.3899
129 | 0.052627 | 0.013252 | -0.052586 | -0.013226 | 4.0959e-05 | 2.6e-05 | 0.080039 | 0.080039 | 0.080039 | 0.97867 | -0.4088 | 0.97784 | -0.42509 | 21.9888
130 | 0.014803 | 0.0037132 | -0.0148 | -0.0037115 | 3.0955e-06 | 1.7764e-06 | 0.022508 | 0.022508 | 0.022508 | 0.97867 | -0.4088 | 0.97845 | -0.41318 | 6.1835
131 | 0.051059 | 0.012843 | -0.051035 | -0.012828 | 2.4598e-05 | 1.5607e-05 | 0.077715 | 0.077715 | 0.077715 | 0.97784 | -0.42509 | 0.97733 | -0.43518 | 21.3504
132 | 0.0012736 | 0.00031865 | -0.0012735 | -0.00031912 | 5.6998e-08 | -4.7245e-07 | 0.0019366 | 0.0019368 | 0.0019368 | 0.97845 | -0.41318 | 0.9784 | -0.41412 | 0.53209
133 | 0.013526 | 0.0033928 | -0.013524 | -0.0033914 | 2.5453e-06 | 1.4276e-06 | 0.020571 | 0.020571 | 0.020571 | 0.97845 | -0.41318 | 0.97825 | -0.41713 | 5.6515
134 | -0.0060578 | -0.0015175 | 0.0060586 | 0.0015177 | 7.6983e-07 | 1.906e-07 | 0.0092258 | 0.0092257 | 0.0092258 | 0.97703 | -0.44114 | 0.97716 | -0.43848 | 2.5346
135 | -0.0085568 | -0.0021438 | 0.0085586 | 0.0021446 | 1.787e-06 | 7.9202e-07 | 0.01303 | 0.01303 | 0.01303 | 0.97716 | -0.43848 | 0.97738 | -0.43409 | 3.5797
136 | -0.0096319 | -0.0024136 | 0.0096338 | 0.0024145 | 1.9328e-06 | 9.3654e-07 | 0.014664 | 0.014664 | 0.014664 | 0.97738 | -0.43409 | 0.9776 | -0.42988 | 4.0285
137 | -0.011304 | -0.0028332 | 0.011307 | 0.0028348 | 3.0692e-06 | 1.6176e-06 | 0.017206 | 0.017206 | 0.017206 | 0.9776 | -0.42988 | 0.97789 | -0.42418 | 4.7271
138 | -0.012204 | -0.0030595 | 0.012208 | 0.0030618 | 4.1014e-06 | 2.2269e-06 | 0.018571 | 0.018571 | 0.018571 | 0.97789 | -0.42418 | 0.97825 | -0.41713 | 5.1019
139 | 0.0012735 | 0.00031912 | -0.0012735 | -0.00031917 | 6.2864e-09 | -5.2099e-08 | 0.0019368 | 0.0019368 | 0.0019368 | 0.9784 | -0.41412 | 0.9784 | -0.41423 | 0.5321
140 | 0.034843 | 0.0087652 | -0.03481 | -0.0087448 | 3.2515e-05 | 2.0424e-05 | 0.053061 | 0.053062 | 0.053062 | 0.97733 | -0.43518 | 0.97633 | -0.45473 | 14.5774
141 | 0.016192 | 0.0040623 | -0.016187 | -0.0040597 | 4.3972e-06 | 2.5726e-06 | 0.024654 | 0.024654 | 0.024654 | 0.97733 | -0.43518 | 0.97704 | -0.44088 | 6.7731
142 | 0.03029 | 0.0076118 | -0.030273 | -0.0076017 | 1.6125e-05 | 1.0068e-05 | 0.046172 | 0.046172 | 0.046172 | 0.97633 | -0.45473 | 0.97576 | -0.46589 | 12.6845
143 | 0.014458 | 0.0036263 | -0.014453 | -0.0036233 | 5.1986e-06 | 2.9692e-06 | 0.02202 | 0.02202 | 0.02202 | 0.97704 | -0.44088 | 0.97665 | -0.44842 | 6.0496
144 | 0.011473 | 0.0028757 | -0.011472 | -0.0028753 | 7.8835e-07 | 4.1852e-07 | 0.017484 | 0.017484 | 0.017484 | 0.97644 | -0.45264 | 0.97636 | -0.45408 | 4.8032
145 | -0.012035 | -0.0030168 | 0.012038 | 0.0030181 | 2.4181e-06 | 1.3078e-06 | 0.018341 | 0.018341 | 0.018341 | 0.97644 | -0.45264 | 0.97665 | -0.44842 | 5.0388
146 | 0.010234 | 0.002565 | -0.010231 | -0.0025637 | 2.4803e-06 | 1.2474e-06 | 0.015596 | 0.015596 | 0.015596 | 0.97636 | -0.45408 | 0.97611 | -0.45917 | 4.2848
147 | 0.0090301 | 0.0022627 | -0.0090293 | -0.0022624 | 7.6807e-07 | 3.5647e-07 | 0.013766 | 0.013766 | 0.013766 | 0.97611 | -0.45917 | 0.97602 | -0.46095 | 3.7818
148 | 0.0074036 | 0.001855 | -0.0074033 | -0.0018548 | 2.9946e-07 | 1.1332e-07 | 0.011287 | 0.011287 | 0.011287 | 0.97602 | -0.46095 | 0.97597 | -0.4618 | 3.1009
149 | 0.028086 | 0.0070536 | -0.028063 | -0.0070392 | 2.3107e-05 | 1.437e-05 | 0.042836 | 0.042836 | 0.042836 | 0.97576 | -0.46589 | 0.97489 | -0.48315 | 11.7682

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61639 | 0.15841

## res_load
| p_mw | q_mvar
0 | 0.0070574 | 0.0017687
1 | 0.0052543 | 0.0013169
2 | 0.004218 | 0.0010571
3 | 0.042385 | 0.010623
4 | 0.035527 | 0.0089039
5 | 0.039384 | 0.0098706
6 | 0.02002 | 0.0050176
7 | 0.0063979 | 0.0016035
8 | 0.0081341 | 0.0020386
9 | 0.0058763 | 0.0014727
10 | 0.0094322 | 0.0023639
11 | 0.013081 | 0.0032784
12 | 0.011994 | 0.0030059
13 | 0.0022881 | 0.00057345
14 | 0.058793 | 0.014735
15 | 0.0056567 | 0.0014177
16 | 0.0055439 | 0.0013894
17 | 0.0021981 | 0.00055091
18 | 0.0018671 | 0.00046794
19 | 0.015492 | 0.0038827
20 | 0.0077846 | 0.001951
21 | 0.0020821 | 0.00052182
22 | 0.020922 | 0.0052437
23 | 0.0059845 | 0.0014998
24 | 0.0035068 | 0.00087889
25 | 0.013089 | 0.0032805
26 | 0.0025087 | 0.00062874
27 | 0.0045516 | 0.0011407
28 | 0.0015931 | 0.00039926
29 | 0.01047 | 0.002624
30 | 0.0094712 | 0.0023737
31 | 0.012723 | 0.0031886
32 | 0.011509 | 0.0028845
33 | 0.0033143 | 0.00083065
34 | 0.002738 | 0.00068621
35 | 0.0027398 | 0.00068667
36 | 0.0027398 | 0.00068667
37 | 0.0031493 | 0.0007893
38 | 0.002943 | 0.00073759
39 | 0.0027409 | 0.00068695
40 | 0.0027399 | 0.00068667
41 | 0.0048441 | 0.0012141
42 | 0.0020494 | 0.00051364
43 | 0.013549 | 0.0033958
44 | 0.0072617 | 0.0018199
45 | 0.010105 | 0.0025325
46 | 0.004125 | 0.0010338
47 | 0.00073559 | 0.00018436
48 | 0.0044692 | 0.0011201
49 | 0.001514 | 0.00037946
50 | 0.0010624 | 0.00026627
51 | 0.00073499 | 0.00018421
52 | 0.00045528 | 0.0001141
53 | 0.0051644 | 0.0012943
54 | 0.0028011 | 0.00070202
55 | 0.00050732 | 0.00012715
56 | 0.0062388 | 0.0015636
57 | 0.0017655 | 0.00044249
58 | 0.0026996 | 0.00067659
59 | 0.0014368 | 0.0003601
60 | 0.001069 | 0.00026792
61 | 0.0016288 | 0.00040821
62 | 0.0011111 | 0.00027846
63 | 0.00091145 | 0.00022843
64 | 0.0010469 | 0.00026238
65 | 0.0017333 | 0.00043442
66 | 0.0015379 | 0.00038544
67 | 0.00091883 | 0.00023028
68 | 0.0014285 | 0.00035802
69 | 0.0015223 | 0.00038153
70 | 0.0019379 | 0.00048569
71 | 0.00091971 | 0.0002305
72 | 0.0017424 | 0.00043669
73 | 0.0018682 | 0.00046823
74 | 0.0011224 | 0.00028131
75 | 0.001741 | 0.00043634
76 | 0.00094233 | 0.00023617
77 | 0.0028892 | 0.0007241
78 | 0.0015671 | 0.00039275
79 | 0.0015379 | 0.00038543
80 | 0.0026015 | 0.000652
81 | 0.0018687 | 0.00046833
82 | 0.0075463 | 0.0018913
83 | 0.0045573 | 0.0011422
84 | 0.0013895 | 0.00034823
85 | 0.0024064 | 0.00060309
86 | 0.0007842 | 0.00019654
87 | 0.0028004 | 0.00070186
88 | 0.0022075 | 0.00055325
89 | 0.0046442 | 0.0011639
90 | 0.00093494 | 0.00023432
91 | 0.0015272 | 0.00038274
92 | 0.0015391 | 0.00038574
93 | 0.0024983 | 0.00062612
94 | 0.0010733 | 0.00026899
95 | 0.0016705 | 0.00041867
96 | 0.00089676 | 0.00022475
97 | 0.0013153 | 0.00032964
98 | 0.0012735 | 0.00031917
99 | 0.0045208 | 0.001133
100 | 0.0017294 | 0.00043342
101 | 0.00056285 | 0.00014106
102 | 0.0012383 | 0.00031034
103 | 0.0024149 | 0.00060522
104 | 0.001201 | 0.000301
105 | 0.0016257 | 0.00040743
106 | 0.00065464 | 0.00016407
107 | 0.0021872 | 0.00054817
108 | 0.0032785 | 0.00082167
109 | 0.0064838 | 0.001625
110 | 0.0033545 | 0.00084071

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1