## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_191-14_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_191-14_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_191-14_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_191-14_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_191-14_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_191-14_0_5_node_80 | 0.4 | n |  | TRUE
6 | bus_LV_191-14_0_5_node_63 | 0.4 | n |  | TRUE
7 | bus_LV_191-14_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_191-14_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_191-14_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_191-14_0_5_node_87 | 0.4 | n |  | TRUE
11 | bus_LV_191-14_0_5_node_78 | 0.4 | n |  | TRUE
12 | bus_LV_191-14_0_5_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_191-14_0_5_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_191-14_0_5_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_191-14_0_5_node_79 | 0.4 | n |  | TRUE
16 | bus_LV_191-14_0_5_node_64 | 0.4 | n |  | TRUE
17 | bus_LV_191-14_0_5_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_191-14_0_5_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_191-14_0_5_node_77 | 0.4 | n |  | TRUE
20 | bus_LV_191-14_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_191-14_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_191-14_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_191-14_0_5_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_191-14_0_5_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_191-14_0_5_node_53 | 0.4 | n |  | TRUE
26 | bus_LV_191-14_0_5_node_126 | 0.4 | n |  | TRUE
27 | bus_LV_191-14_0_5_node_127 | 0.4 | n |  | TRUE
28 | bus_LV_191-14_0_5_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_191-14_0_5_node_71 | 0.4 | n |  | TRUE
30 | bus_LV_191-14_0_5_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_191-14_0_5_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_191-14_0_5_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_191-14_0_5_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_191-14_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_191-14_0_5_node_54 | 0.4 | n |  | TRUE
36 | bus_LV_191-14_0_5_node_57 | 0.4 | n |  | TRUE
37 | bus_LV_191-14_0_5_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_191-14_0_5_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_191-14_0_5_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_191-14_0_5_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_191-14_0_5_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_191-14_0_5_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_191-14_0_5_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_191-14_0_5_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_191-14_0_5_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_191-14_0_5_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_191-14_0_5_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_191-14_0_5_node_72 | 0.4 | n |  | TRUE
49 | bus_LV_191-14_0_5_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_191-14_0_5_node_59 | 0.4 | n |  | TRUE
51 | bus_LV_191-14_0_5_node_73 | 0.4 | n |  | TRUE
52 | bus_LV_191-14_0_5_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_191-14_0_5_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_191-14_0_5_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_191-14_0_5_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_191-14_0_5_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_191-14_0_5_node_82 | 0.4 | n |  | TRUE
58 | bus_LV_191-14_0_5_node_83 | 0.4 | n |  | TRUE
59 | bus_LV_191-14_0_5_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_191-14_0_5_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_191-14_0_5_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_191-14_0_5_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_191-14_0_5_node_84 | 0.4 | n |  | TRUE
64 | bus_LV_191-14_0_5_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_191-14_0_5_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_191-14_0_5_node_85 | 0.4 | n |  | TRUE
67 | bus_LV_191-14_0_5_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_191-14_0_5_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_191-14_0_5_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_191-14_0_5_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_191-14_0_5_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_191-14_0_5_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_191-14_0_5_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_191-14_0_5_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_191-14_0_5_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_191-14_0_5_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_191-14_0_5_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_191-14_0_5_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_191-14_0_5_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_191-14_0_5_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_191-14_0_5_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_191-14_0_5_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_191-14_0_5_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_191-14_0_5_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_191-14_0_5_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_191-14_0_5_node_89 | 0.4 | n |  | TRUE
87 | bus_LV_191-14_0_5_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_191-14_0_5_node_94 | 0.4 | n |  | TRUE
89 | bus_LV_191-14_0_5_node_91 | 0.4 | n |  | TRUE
90 | bus_LV_191-14_0_5_node_98 | 0.4 | n |  | TRUE
91 | bus_LV_191-14_0_5_node_92 | 0.4 | n |  | TRUE
92 | bus_LV_191-14_0_5_node_93 | 0.4 | n |  | TRUE
93 | bus_LV_191-14_0_5_node_121 | 0.4 | n |  | TRUE
94 | bus_LV_191-14_0_5_node_122 | 0.4 | n |  | TRUE
95 | bus_LV_191-14_0_5_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_191-14_0_5_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_191-14_0_5_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_191-14_0_5_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_191-14_0_5_node_99 | 0.4 | n |  | TRUE
100 | bus_LV_191-14_0_5_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_191-14_0_5_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_191-14_0_5_node_115 | 0.4 | n |  | TRUE
103 | bus_LV_191-14_0_5_node_102 | 0.4 | n |  | TRUE
104 | bus_LV_191-14_0_5_node_108 | 0.4 | n |  | TRUE
105 | bus_LV_191-14_0_5_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_191-14_0_5_node_109 | 0.4 | n |  | TRUE
107 | bus_LV_191-14_0_5_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_191-14_0_5_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_191-14_0_5_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_191-14_0_5_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_191-14_0_5_node_110 | 0.4 | n |  | TRUE
112 | bus_LV_191-14_0_5_node_113 | 0.4 | n |  | TRUE
113 | bus_LV_191-14_0_5_node_114 | 0.4 | n |  | TRUE
114 | bus_LV_191-14_0_5_node_117 | 0.4 | n |  | TRUE
115 | bus_LV_191-14_0_5_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_191-14_0_5_node_119 | 0.4 | n |  | TRUE
117 | bus_LV_191-14_0_5_node_120 | 0.4 | n |  | TRUE
118 | bus_LV_191-14_0_5_node_124 | 0.4 | n |  | TRUE
119 | bus_LV_191-14_0_5_node_125 | 0.4 | n |  | TRUE
120 | bus_LV_191-14_0_5_node_123 | 0.4 | n |  | TRUE
121 | bus_LV_191-14_0_5_node_131 | 0.4 | n |  | TRUE
122 | bus_LV_191-14_0_5_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_191-14_0_5_node_132 | 0.4 | n |  | TRUE
124 | bus_LV_191-14_0_5_node_129 | 0.4 | n |  | TRUE
125 | bus_LV_191-14_0_5_node_130 | 0.4 | n |  | TRUE
126 | bus_LV_191-14_0_5_node_133 | 0.4 | n |  | TRUE
127 | bus_MV_499_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_191-14_0_5_load_0 | 0 | 0.019955 | 0.0050011 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_191-14_0_5_load_5 | 3 | 0.033431 | 0.0083786 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_191-14_0_5_load_80 | 5 | 0.0015393 | 0.00038579 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_191-14_0_5_load_63 | 6 | 0.008017 | 0.0020092 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_191-14_0_5_load_8 | 7 | 0.0026031 | 0.00065239 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_191-14_0_5_load_87 | 10 | 0.00074462 | 0.00018662 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_191-14_0_5_load_78 | 11 | 0.0010455 | 0.00026203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_191-14_0_5_load_58 | 13 | 0.015961 | 0.0040003 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_191-14_0_5_load_33 | 14 | 0.014006 | 0.0035102 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_191-14_0_5_load_64 | 16 | 0.018379 | 0.0046062 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_191-14_0_5_load_9 | 18 | 0.025759 | 0.0064559 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_191-14_0_5_load_10 | 20 | 0.01694 | 0.0042454 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_191-14_0_5_load_11 | 21 | 0.00036597 | 9.172e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_191-14_0_5_load_12 | 22 | 0.00033782 | 8.4666e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_191-14_0_5_load_13 | 23 | 0.00037186 | 9.3197e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_191-14_0_5_load_14 | 24 | 0.00049718 | 0.0001246 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_191-14_0_5_load_53 | 25 | 0.00067972 | 0.00017035 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_191-14_0_5_load_126 | 26 | 0.0046452 | 0.0011642 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_191-14_0_5_load_127 | 27 | 0.0004444 | 0.00011138 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_191-14_0_5_load_51 | 28 | 0.0002748 | 6.8872e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_191-14_0_5_load_15 | 30 | 0.00508 | 0.0012732 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_191-14_0_5_load_16 | 31 | 0.00033976 | 8.5152e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_191-14_0_5_load_17 | 32 | 0.00056764 | 0.00014226 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_191-14_0_5_load_18 | 33 | 0.00018668 | 4.6787e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_191-14_0_5_load_19 | 34 | 0.0002927 | 7.3358e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_191-14_0_5_load_54 | 35 | 0.00042516 | 0.00010656 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_191-14_0_5_load_57 | 36 | 0.00044413 | 0.00011131 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_191-14_0_5_load_55 | 37 | 0.00033978 | 8.5157e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_191-14_0_5_load_70 | 38 | 0.00044432 | 0.00011136 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_191-14_0_5_load_20 | 39 | 0.012247 | 0.0030693 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_191-14_0_5_load_21 | 40 | 0.0067953 | 0.0017031 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_191-14_0_5_load_23 | 42 | 0.011567 | 0.0028989 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_191-14_0_5_load_24 | 43 | 0.0095963 | 0.002405 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_191-14_0_5_load_25 | 44 | 0.011648 | 0.0029192 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_191-14_0_5_load_26 | 45 | 0.00896 | 0.0022456 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_191-14_0_5_load_41 | 46 | 0.0086215 | 0.0021607 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_191-14_0_5_load_60 | 47 | 0.011163 | 0.0027977 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_191-14_0_5_load_59 | 50 | 0.004905 | 0.0012293 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_191-14_0_5_load_27 | 52 | 0.0087303 | 0.002188 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_191-14_0_5_load_31 | 56 | 0.0086794 | 0.0021753 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_191-14_0_5_load_82 | 57 | 0.0074048 | 0.0018558 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_191-14_0_5_load_83 | 58 | 0.014074 | 0.0035274 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_191-14_0_5_load_39 | 59 | 0.0059117 | 0.0014816 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_191-14_0_5_load_36 | 61 | 0.0092592 | 0.0023206 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_191-14_0_5_load_35 | 62 | 0.004104 | 0.0010286 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_191-14_0_5_load_84 | 63 | 0.010785 | 0.0027029 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_191-14_0_5_load_38 | 64 | 0.0060986 | 0.0015285 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_191-14_0_5_load_43 | 65 | 0.0085376 | 0.0021397 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_191-14_0_5_load_85 | 66 | 0.0096725 | 0.0024242 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_191-14_0_5_load_40 | 67 | 0.0043358 | 0.0010867 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_191-14_0_5_load_45 | 68 | 0.0013628 | 0.00034156 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_191-14_0_5_load_44 | 69 | 0.0027012 | 0.00067698 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_191-14_0_5_load_46 | 70 | 0.0023086 | 0.00057858 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_191-14_0_5_load_47 | 71 | 0.0026378 | 0.0006611 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_191-14_0_5_load_48 | 72 | 0.0018861 | 0.0004727 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_191-14_0_5_load_52 | 73 | 0.00072538 | 0.0001818 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_191-14_0_5_load_56 | 74 | 0.00070072 | 0.00017562 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_191-14_0_5_load_76 | 75 | 0.0010944 | 0.00027428 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_191-14_0_5_load_74 | 76 | 0.00059289 | 0.00014859 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_191-14_0_5_load_68 | 77 | 0.0081009 | 0.0020303 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_191-14_0_5_load_61 | 78 | 0.00068915 | 0.00017272 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_191-14_0_5_load_75 | 79 | 0.00074453 | 0.0001866 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_191-14_0_5_load_65 | 80 | 0.00037069 | 9.2904e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_191-14_0_5_load_67 | 82 | 0.007209 | 0.0018067 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_191-14_0_5_load_69 | 83 | 0.00044432 | 0.00011136 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_191-14_0_5_load_88 | 85 | 0.0027821 | 0.00069727 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_191-14_0_5_load_89 | 86 | 0.0015128 | 0.00037914 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_191-14_0_5_load_91 | 89 | 0.0025134 | 0.00062992 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_191-14_0_5_load_98 | 90 | 0.0021092 | 0.00052863 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_191-14_0_5_load_92 | 91 | 0.0021776 | 0.00054575 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_191-14_0_5_load_93 | 92 | 0.0015325 | 0.00038409 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_191-14_0_5_load_121 | 93 | 0.007271 | 0.0018223 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_191-14_0_5_load_122 | 94 | 0.0021765 | 0.00054549 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_191-14_0_5_load_116 | 95 | 0.0024296 | 0.00060891 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_191-14_0_5_load_95 | 96 | 0.0015823 | 0.00039657 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_191-14_0_5_load_96 | 97 | 0.0015209 | 0.00038117 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_191-14_0_5_load_97 | 98 | 0.0036388 | 0.00091196 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_191-14_0_5_load_100 | 100 | 0.0024831 | 0.00062233 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_191-14_0_5_load_101 | 101 | 0.00069623 | 0.00017449 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_191-14_0_5_load_102 | 103 | 0.00069682 | 0.00017464 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_191-14_0_5_load_108 | 104 | 0.00069623 | 0.00017449 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_191-14_0_5_load_103 | 105 | 0.00069683 | 0.00017464 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_191-14_0_5_load_109 | 106 | 0.00069623 | 0.00017449 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_191-14_0_5_load_105 | 107 | 0.0006265 | 0.00015701 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_191-14_0_5_load_104 | 108 | 0.001589 | 0.00039824 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_191-14_0_5_load_111 | 109 | 0.00069683 | 0.00017464 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_191-14_0_5_load_110 | 111 | 0.00071035 | 0.00017803 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_191-14_0_5_load_113 | 112 | 0.00069682 | 0.00017464 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_191-14_0_5_load_114 | 113 | 0.00069682 | 0.00017464 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_191-14_0_5_load_117 | 114 | 0.0023137 | 0.00057986 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_191-14_0_5_load_118 | 115 | 0.0015325 | 0.00038409 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_191-14_0_5_load_119 | 116 | 0.0021784 | 0.00054595 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_191-14_0_5_load_123 | 120 | 0.0068863 | 0.0017259 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_191-14_0_5_load_128 | 122 | 0.0032428 | 0.00081273 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_191-14_0_5_load_132 | 123 | 0.0051226 | 0.0012838 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_191-14_0_5_load_129 | 124 | 0.0034648 | 0.00086837 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_191-14_0_5_load_130 | 125 | 0.0080771 | 0.0020243 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_191-14_0_5_load_133 | 126 | 0.0037644 | 0.00094344 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_191-14_0_5_line_0 |  | 0 | 1 | 0.023079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_191-14_0_5_line_1 |  | 1 | 2 | 0.040927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_191-14_0_5_line_2 |  | 1 | 3 | 0.045362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_191-14_0_5_line_3 |  | 2 | 4 | 0.033061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_191-14_0_5_line_4 |  | 2 | 5 | 0.0026984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_191-14_0_5_line_5 |  | 3 | 7 | 0.039805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_191-14_0_5_line_6 |  | 4 | 6 | 0.018783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_191-14_0_5_line_7 |  | 5 | 15 | 0.015063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_191-14_0_5_line_8 |  | 7 | 18 | 0.019938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_191-14_0_5_line_9 |  | 8 | 9 | 0.003864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_191-14_0_5_line_10 |  | 8 | 10 | 0.031808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_191-14_0_5_line_11 |  | 9 | 11 | 0.0028403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_191-14_0_5_line_12 |  | 10 | 19 | 0.00091133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_191-14_0_5_line_13 |  | 11 | 15 | 0.025588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_191-14_0_5_line_14 |  | 12 | 13 | 0.020999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_191-14_0_5_line_15 |  | 12 | 14 | 0.027573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_191-14_0_5_line_16 |  | 13 | 42 | 0.021725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_191-14_0_5_line_17 |  | 15 | 84 | 0.032445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_191-14_0_5_line_18 |  | 16 | 17 | 0.02657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_191-14_0_5_line_19 |  | 17 | 19 | 0.003661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_191-14_0_5_line_20 |  | 17 | 78 | 0.01318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_191-14_0_5_line_21 |  | 19 | 79 | 0.023709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_191-14_0_5_line_22 |  | 20 | 21 | 0.0084491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_191-14_0_5_line_23 |  | 20 | 22 | 0.028315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_191-14_0_5_line_24 |  | 21 | 23 | 0.0019698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_191-14_0_5_line_25 |  | 22 | 24 | 0.012964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_191-14_0_5_line_26 |  | 23 | 25 | 0.023035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_191-14_0_5_line_27 |  | 24 | 26 | 0.014363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_191-14_0_5_line_28 |  | 24 | 27 | 0.014969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_191-14_0_5_line_29 |  | 25 | 28 | 0.0013083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_191-14_0_5_line_30 |  | 27 | 29 | 0.00080627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_191-14_0_5_line_31 |  | 28 | 73 | 0.013211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_191-14_0_5_line_32 |  | 29 | 48 | 0.035246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_191-14_0_5_line_33 |  | 29 | 83 | 0.014623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_191-14_0_5_line_34 |  | 30 | 31 | 0.013467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_191-14_0_5_line_35 |  | 30 | 32 | 0.00037001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_191-14_0_5_line_36 |  | 31 | 33 | 0.0046598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_191-14_0_5_line_37 |  | 32 | 34 | 0.0030661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_191-14_0_5_line_38 |  | 33 | 35 | 0.005925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_191-14_0_5_line_39 |  | 34 | 36 | 0.017328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_191-14_0_5_line_40 |  | 35 | 37 | 0.0052161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_191-14_0_5_line_41 |  | 36 | 38 | 0.015995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_191-14_0_5_line_42 |  | 37 | 74 | 0.007178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_191-14_0_5_line_43 |  | 38 | 77 | 0.0050652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_191-14_0_5_line_44 |  | 39 | 40 | 0.0069877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_191-14_0_5_line_45 |  | 39 | 41 | 0.020072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_191-14_0_5_line_46 |  | 40 | 42 | 0.027477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_191-14_0_5_line_47 |  | 41 | 43 | 0.029153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_191-14_0_5_line_48 |  | 41 | 44 | 0.021315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_191-14_0_5_line_49 |  | 41 | 45 | 0.038751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_191-14_0_5_line_50 |  | 43 | 46 | 0.029616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_191-14_0_5_line_51 |  | 44 | 47 | 0.030073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_191-14_0_5_line_52 |  | 45 | 48 | 0.020701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_191-14_0_5_line_53 |  | 46 | 49 | 0.016065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_191-14_0_5_line_54 |  | 47 | 50 | 0.0031101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_191-14_0_5_line_55 |  | 48 | 51 | 0.01771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_191-14_0_5_line_56 |  | 49 | 65 | 0.016673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_191-14_0_5_line_57 |  | 49 | 55 | 0.045591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_191-14_0_5_line_58 |  | 50 | 78 | 0.027034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_191-14_0_5_line_59 |  | 51 | 82 | 0.017796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_191-14_0_5_line_60 |  | 52 | 53 | 0.018633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_191-14_0_5_line_61 |  | 52 | 54 | 0.020802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_191-14_0_5_line_62 |  | 53 | 55 | 0.014466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_191-14_0_5_line_63 |  | 53 | 56 | 0.014001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_191-14_0_5_line_64 |  | 54 | 57 | 0.02991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_191-14_0_5_line_65 |  | 54 | 58 | 0.021793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_191-14_0_5_line_66 |  | 55 | 59 | 0.018496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_191-14_0_5_line_67 |  | 57 | 63 | 0.039577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_191-14_0_5_line_68 |  | 59 | 64 | 0.029898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_191-14_0_5_line_69 |  | 60 | 61 | 0.014285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_191-14_0_5_line_70 |  | 60 | 62 | 0.036561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_191-14_0_5_line_71 |  | 60 | 63 | 0.015128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_191-14_0_5_line_72 |  | 61 | 66 | 0.020609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_191-14_0_5_line_73 |  | 64 | 67 | 0.012142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_191-14_0_5_line_74 |  | 65 | 68 | 0.014634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_191-14_0_5_line_75 |  | 68 | 69 | 0.0096508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_191-14_0_5_line_76 |  | 69 | 70 | 0.012802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_191-14_0_5_line_77 |  | 70 | 71 | 0.0072788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_191-14_0_5_line_78 |  | 71 | 72 | 0.0067251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_191-14_0_5_line_79 |  | 75 | 76 | 0.010609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_191-14_0_5_line_80 |  | 76 | 79 | 0.021117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_191-14_0_5_line_81 |  | 77 | 83 | 0.011121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_191-14_0_5_line_82 |  | 80 | 81 | 0.013975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_191-14_0_5_line_83 |  | 81 | 82 | 0.022452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_191-14_0_5_line_84 |  | 84 | 85 | 0.025705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_191-14_0_5_line_85 |  | 85 | 86 | 0.012695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_191-14_0_5_line_86 |  | 86 | 87 | 0.015933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_191-14_0_5_line_87 |  | 87 | 88 | 0.004074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_191-14_0_5_line_88 |  | 87 | 89 | 0.038671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_191-14_0_5_line_89 |  | 88 | 90 | 0.028128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_191-14_0_5_line_90 |  | 89 | 91 | 0.005318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_191-14_0_5_line_91 |  | 90 | 95 | 0.00057229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_191-14_0_5_line_92 |  | 91 | 92 | 0.021981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_191-14_0_5_line_93 |  | 92 | 93 | 0.010362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_191-14_0_5_line_94 |  | 93 | 94 | 0.01011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_191-14_0_5_line_95 |  | 95 | 102 | 0.017838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_191-14_0_5_line_96 |  | 96 | 97 | 0.012035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_191-14_0_5_line_97 |  | 97 | 98 | 0.017932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_191-14_0_5_line_98 |  | 98 | 99 | 0.014322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_191-14_0_5_line_99 |  | 99 | 100 | 0.0088753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_191-14_0_5_line_100 |  | 99 | 101 | 0.01112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_191-14_0_5_line_101 |  | 100 | 103 | 0.019946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_191-14_0_5_line_102 |  | 101 | 104 | 0.00083234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_191-14_0_5_line_103 |  | 102 | 114 | 0.035814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_191-14_0_5_line_104 |  | 102 | 113 | 0.032944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_191-14_0_5_line_105 |  | 103 | 105 | 0.018101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_191-14_0_5_line_106 |  | 104 | 106 | 0.033415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_191-14_0_5_line_107 |  | 105 | 107 | 0.015987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_191-14_0_5_line_108 |  | 106 | 111 | 7.651e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_191-14_0_5_line_109 |  | 107 | 108 | 0.017666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_191-14_0_5_line_110 |  | 109 | 110 | 0.027783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_191-14_0_5_line_111 |  | 110 | 112 | 0.029759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_191-14_0_5_line_112 |  | 110 | 111 | 0.015152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_191-14_0_5_line_113 |  | 112 | 113 | 0.020108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_191-14_0_5_line_114 |  | 114 | 115 | 0.019777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_191-14_0_5_line_115 |  | 115 | 116 | 0.022627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_191-14_0_5_line_116 |  | 116 | 117 | 0.0027984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_191-14_0_5_line_117 |  | 117 | 118 | 0.034298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_191-14_0_5_line_118 |  | 118 | 119 | 0.04984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_191-14_0_5_line_119 |  | 118 | 120 | 0.027173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_191-14_0_5_line_120 |  | 119 | 121 | 0.07183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_191-14_0_5_line_121 |  | 119 | 122 | 0.021827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_191-14_0_5_line_122 |  | 121 | 123 | 0.033468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_191-14_0_5_line_123 |  | 122 | 124 | 0.00078247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_191-14_0_5_line_124 |  | 123 | 126 | 0.016673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_191-14_0_5_line_125 |  | 124 | 125 | 0.0083715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_191-14_0_5_trafo_23 | 0.63 MVA 20/0.4 kV | 127 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2689919.0883 | 1250377.7152 | 2689921.3885 | 1250376.8939 | 2689923.0886 | 1250375.8078 | 2689924.4991 | 1250374.4059 | 2689935.0086 | 1250361.5168
1 | 2689919.0883 | 1250377.7152 | 2689916.3779 | 1250377.7074 | 2689913.1249 | 1250376.1458 | 2689907.064 | 1250371.05 | 2689900.7949 | 1250369.2313 | 2689883.6658 | 1250380.0353
2 | 2689919.0883 | 1250377.7152 | 2689918.9686 | 1250380.6267 | 2689950.1976 | 1250409.3777
3 | 2689859.2178 | 1250398.0116 | 2689862.3957 | 1250394.5683 | 2689866.2338 | 1250390.4122 | 2689869.5601 | 1250390.6294 | 2689874.0342 | 1250390.8308 | 2689876.3038 | 1250386.0504 | 2689879.2307 | 1250382.7367 | 2689883.6658 | 1250380.0353
4 | 2689883.6658 | 1250380.0353 | 2689884.8598 | 1250382.4552
5 | 2689950.1976 | 1250409.3777 | 2689979.4815 | 1250436.338
6 | 2689859.2178 | 1250398.0116 | 2689856.2604 | 1250396.8659 | 2689853.0502 | 1250396.4614 | 2689850.2281 | 1250397.3526 | 2689842.1653 | 1250402.2174
7 | 2689876.7134 | 1250394.3852 | 2689879.5977 | 1250386.4118 | 2689884.8598 | 1250382.4552
8 | 2689994.1501 | 1250449.8426 | 2689979.4815 | 1250436.338
9 | 2689890.0843 | 1250419.7739 | 2689892.2171 | 1250416.5483
10 | 2689890.0843 | 1250419.7739 | 2689913.5837 | 1250441.2099
11 | 2689892.2171 | 1250416.5483 | 2689892.6885 | 1250415.8327 | 2689893.0425 | 1250414.8929 | 2689893.0196 | 1250413.914
12 | 2689913.5837 | 1250441.2099 | 2689914.257 | 1250441.824
13 | 2689876.7134 | 1250394.3852 | 2689882.4156 | 1250399.7313 | 2689886.4217 | 1250404.4067 | 2689889.6091 | 1250408.3025 | 2689891.588 | 1250411.2347 | 2689892.6258 | 1250412.9962 | 2689893.0196 | 1250413.914
14 | 2689792.7958 | 1250437.624 | 2689799.6434 | 1250445.1112 | 2689806.8013 | 1250453.2682
15 | 2689792.7958 | 1250437.624 | 2689772.1653 | 1250455.9172
16 | 2689820.674 | 1250469.9404 | 2689818.6802 | 1250466.8051 | 2689806.8013 | 1250453.2682
17 | 2689876.7134 | 1250394.3852 | 2689875.2807 | 1250393.2738 | 2689851.4978 | 1250373.8762
18 | 2689911.8519 | 1250444.5896 | 2689892.1225 | 1250426.7937
19 | 2689914.257 | 1250441.824 | 2689911.8519 | 1250444.5896
20 | 2689911.8519 | 1250444.5896 | 2689910.2382 | 1250446.4444 | 2689903.1964 | 1250454.529
21 | 2689914.257 | 1250441.824 | 2689931.8699 | 1250457.6961
22 | 2689855.6428 | 1250644.3131 | 2689850.2966 | 1250650.8556
23 | 2689855.6428 | 1250644.3131 | 2689866.2706 | 1250631.3072 | 2689873.5598 | 1250622.3875
24 | 2689850.2966 | 1250650.8556 | 2689849.0502 | 1250652.3808
25 | 2689881.7636 | 1250612.3499 | 2689878.1096 | 1250616.8201 | 2689873.5598 | 1250622.3875
26 | 2689834.4744 | 1250670.2181 | 2689843.016 | 1250659.7652 | 2689849.0502 | 1250652.3808
27 | 2689881.7636 | 1250612.3499 | 2689870.5454 | 1250603.3396
28 | 2689881.7636 | 1250612.3499 | 2689891.2382 | 1250600.7607
29 | 2689834.4744 | 1250670.2181 | 2689833.6465 | 1250671.2312
30 | 2689891.7485 | 1250600.1365 | 2689891.2382 | 1250600.7607
31 | 2689833.6465 | 1250671.2312 | 2689825.2869 | 1250681.4614
32 | 2689874.6298 | 1250570.0095 | 2689881.4652 | 1250587.2374 | 2689882.7743 | 1250590.026 | 2689884.1627 | 1250592.5601 | 2689885.7824 | 1250594.7864 | 2689891.7485 | 1250600.1365
33 | 2689891.7485 | 1250600.1365 | 2689900.9142 | 1250588.7419
34 | 2689934.0992 | 1250547.4869 | 2689942.5401 | 1250536.9933
35 | 2689934.0992 | 1250547.4869 | 2689933.8673 | 1250547.7753
36 | 2689942.5401 | 1250536.9933 | 2689945.4608 | 1250533.3624
37 | 2689933.8673 | 1250547.7753 | 2689931.9455 | 1250550.1643
38 | 2689949.1744 | 1250528.7457 | 2689945.4608 | 1250533.3624
39 | 2689921.0849 | 1250563.6661 | 2689931.9455 | 1250550.1643
40 | 2689949.1744 | 1250528.7457 | 2689952.4438 | 1250524.6813
41 | 2689921.0849 | 1250563.6661 | 2689911.0596 | 1250576.1294
42 | 2689956.9428 | 1250519.0881 | 2689952.4438 | 1250524.6813
43 | 2689907.8848 | 1250580.0761 | 2689911.0596 | 1250576.1294
44 | 2689835.4185 | 1250493.1268 | 2689839.1681 | 1250499.0233
45 | 2689849.9388 | 1250515.9607 | 2689839.1681 | 1250499.0233
46 | 2689820.674 | 1250469.9404 | 2689835.4185 | 1250493.1268
47 | 2689828.3573 | 1250535.6263 | 2689849.9388 | 1250515.9607
48 | 2689849.9388 | 1250515.9607 | 2689864.0951 | 1250500.0254
49 | 2689849.9388 | 1250515.9607 | 2689856.9372 | 1250529.4215 | 2689866.5413 | 1250550.957
50 | 2689828.3573 | 1250535.6263 | 2689806.4593 | 1250555.5662
51 | 2689884.0681 | 1250477.5424 | 2689864.0951 | 1250500.0254
52 | 2689874.6298 | 1250570.0095 | 2689870.2478 | 1250559.2682 | 2689866.5413 | 1250550.957
53 | 2689794.581 | 1250566.3824 | 2689806.4593 | 1250555.5662
54 | 2689886.1337 | 1250475.2173 | 2689884.0681 | 1250477.5424
55 | 2689863.5555 | 1250583.8521 | 2689864.5711 | 1250582.5999 | 2689866.5717 | 1250580.1172 | 2689868.3106 | 1250577.9642 | 2689874.6298 | 1250570.0095
56 | 2689794.581 | 1250566.3824 | 2689782.1918 | 1250577.5396
57 | 2689794.581 | 1250566.3824 | 2689779.2786 | 1250549.371 | 2689765.639 | 1250534.2306 | 2689764.0428 | 1250532.4496
58 | 2689886.1337 | 1250475.2173 | 2689886.3627 | 1250474.9595 | 2689894.3203 | 1250466.0067 | 2689894.6476 | 1250464.3437 | 2689903.1964 | 1250454.529
59 | 2689863.5555 | 1250583.8521 | 2689849.6787 | 1250572.7112
60 | 2689757.194 | 1250520.559 | 2689754.255 | 1250517.212 | 2689752.073 | 1250514.7215 | 2689744.9039 | 1250506.5537
61 | 2689731.1806 | 1250490.9204 | 2689732.5313 | 1250492.4642 | 2689734.8322 | 1250495.0788 | 2689744.9039 | 1250506.5537
62 | 2689757.194 | 1250520.559 | 2689756.9755 | 1250521.5231 | 2689756.8701 | 1250523.0004 | 2689757.2788 | 1250524.4299 | 2689758.0362 | 1250525.7646 | 2689758.422 | 1250526.2153 | 2689762.3576 | 1250530.5559 | 2689764.0428 | 1250532.4496
63 | 2689757.194 | 1250520.559 | 2689757.2584 | 1250520.2931 | 2689757.9895 | 1250518.8809 | 2689766.9024 | 1250510.6428
64 | 2689731.1806 | 1250490.9204 | 2689702.3252 | 1250498.7924
65 | 2689731.1806 | 1250490.9204 | 2689737.4446 | 1250470.0471
66 | 2689764.0428 | 1250532.4496 | 2689750.0985 | 1250544.6018
67 | 2689702.3252 | 1250498.7924 | 2689700.4552 | 1250500.2068 | 2689685.8284 | 1250510.3488 | 2689669.2166 | 1250520.4328
68 | 2689727.5587 | 1250564.245 | 2689750.0985 | 1250544.6018
69 | 2689665.9884 | 1250535.212 | 2689653.6557 | 1250542.4203
70 | 2689665.9884 | 1250535.212 | 2689695.8379 | 1250556.3241
71 | 2689665.9884 | 1250535.212 | 2689669.2166 | 1250520.4328
72 | 2689653.6557 | 1250542.4203 | 2689633.0663 | 1250541.5271
73 | 2689718.4052 | 1250572.2222 | 2689727.5587 | 1250564.245
74 | 2689782.1918 | 1250577.5396 | 2689771.3175 | 1250587.3326
75 | 2689764.1461 | 1250593.7909 | 2689771.3175 | 1250587.3326
76 | 2689764.1461 | 1250593.7909 | 2689757.9092 | 1250599.4076 | 2689754.5563 | 1250602.2698
77 | 2689754.5563 | 1250602.2698 | 2689749.0203 | 1250606.9955
78 | 2689743.9054 | 1250611.3618 | 2689749.0203 | 1250606.9955
79 | 2689947.5571 | 1250471.8329 | 2689955.4381 | 1250478.9349
80 | 2689947.5571 | 1250471.8329 | 2689931.8699 | 1250457.6961
81 | 2689907.8848 | 1250580.0761 | 2689900.9142 | 1250588.7419
82 | 2689834.1805 | 1250577.2907 | 2689833.1363 | 1250576.452 | 2689832.3514 | 1250577.4298 | 2689827.8196 | 1250583.032 | 2689831.0754 | 1250585.6472
83 | 2689834.1805 | 1250577.2907 | 2689842.5212 | 1250566.9648 | 2689849.6787 | 1250572.7112
84 | 2689851.4978 | 1250373.8762 | 2689833.9974 | 1250364.3704 | 2689828.8106 | 1250361.7984
85 | 2689828.8106 | 1250361.7984 | 2689822.0149 | 1250358.4287 | 2689817.7003 | 1250355.6921
86 | 2689804.8795 | 1250346.2598 | 2689810.8563 | 1250350.9317 | 2689813.6992 | 1250353.1543 | 2689817.7003 | 1250355.6921
87 | 2689804.8795 | 1250346.2598 | 2689806.7089 | 1250342.6181
88 | 2689804.8795 | 1250346.2598 | 2689801.05 | 1250353.8298 | 2689776.0614 | 1250370.7664
89 | 2689806.7089 | 1250342.6181 | 2689804.3207 | 1250337.3001 | 2689788.5212 | 1250321.5656
90 | 2689776.0614 | 1250370.7664 | 2689771.6592 | 1250373.75
91 | 2689788.1157 | 1250321.1618 | 2689788.5212 | 1250321.5656
92 | 2689752.2983 | 1250384.1357 | 2689770.2233 | 1250374.7232 | 2689771.6592 | 1250373.75
93 | 2689752.2983 | 1250384.1357 | 2689743.1241 | 1250388.9531
94 | 2689734.1734 | 1250393.6531 | 2689743.1241 | 1250388.9531
95 | 2689775.4767 | 1250308.5747 | 2689788.1157 | 1250321.1618
96 | 2689845.3953 | 1250319.5481 | 2689854.668 | 1250311.8766
97 | 2689867.5294 | 1250299.4434 | 2689860.8972 | 1250306.7232 | 2689854.668 | 1250311.8766
98 | 2689877.1747 | 1250288.8564 | 2689867.5294 | 1250299.4434
99 | 2689877.1747 | 1250288.8564 | 2689882.9467 | 1250282.1143
100 | 2689877.1747 | 1250288.8564 | 2689868.9217 | 1250281.4034
101 | 2689882.9467 | 1250282.1143 | 2689890.5568 | 1250273.2252 | 2689896.0271 | 1250267.0576
102 | 2689868.304 | 1250280.8456 | 2689868.9217 | 1250281.4034
103 | 2689775.4767 | 1250308.5747 | 2689752.6591 | 1250325.5754 | 2689746.4052 | 1250329.4557
104 | 2689775.4767 | 1250308.5747 | 2689798.0435 | 1250284.5737
105 | 2689896.0271 | 1250267.0576 | 2689908.0379 | 1250253.5157
106 | 2689868.304 | 1250280.8456 | 2689843.5044 | 1250258.4501
107 | 2689918.646 | 1250241.5553 | 2689908.0379 | 1250253.5157
108 | 2689843.4476 | 1250258.3988 | 2689843.5044 | 1250258.4501
109 | 2689930.3683 | 1250228.3387 | 2689918.646 | 1250241.5553
110 | 2689832.2025 | 1250248.2438 | 2689851.0689 | 1250227.8494
111 | 2689832.2025 | 1250248.2438 | 2689811.8173 | 1250269.9245
112 | 2689832.2025 | 1250248.2438 | 2689843.4476 | 1250258.3988
113 | 2689798.0435 | 1250284.5737 | 2689811.8173 | 1250269.9245
114 | 2689729.6004 | 1250339.8822 | 2689746.4052 | 1250329.4557
115 | 2689729.6004 | 1250339.8822 | 2689710.3735 | 1250351.8116
116 | 2689707.9956 | 1250353.287 | 2689710.3735 | 1250351.8116
117 | 2689707.9956 | 1250353.287 | 2689678.7893 | 1250371.4033
118 | 2689635.583 | 1250396.1575 | 2689660.643 | 1250380.6024 | 2689678.7893 | 1250371.4033
119 | 2689678.7893 | 1250371.4033 | 2689693.2003 | 1250394.4402
120 | 2689635.583 | 1250396.1575 | 2689573.0944 | 1250431.8956
121 | 2689635.583 | 1250396.1575 | 2689646.6119 | 1250414.9929
122 | 2689573.0944 | 1250431.8956 | 2689598.7218 | 1250453.4212
123 | 2689647.0072 | 1250415.6681 | 2689646.6119 | 1250414.9929
124 | 2689611.489 | 1250464.1448 | 2689598.7218 | 1250453.4212
125 | 2689651.2373 | 1250422.8923 | 2689647.0072 | 1250415.6681

## bus_geodata
| x | y | coords
0 | 2689935.0086 | 1250361.5168
1 | 2689919.0883 | 1250377.7152
2 | 2689883.6658 | 1250380.0353
3 | 2689950.1976 | 1250409.3777
4 | 2689859.2178 | 1250398.0116
5 | 2689884.8598 | 1250382.4552
6 | 2689842.1653 | 1250402.2174
7 | 2689979.4815 | 1250436.338
8 | 2689890.0843 | 1250419.7739
9 | 2689892.2171 | 1250416.5483
10 | 2689913.5837 | 1250441.2099
11 | 2689893.0196 | 1250413.914
12 | 2689792.7958 | 1250437.624
13 | 2689806.8013 | 1250453.2682
14 | 2689772.1653 | 1250455.9172
15 | 2689876.7134 | 1250394.3852
16 | 2689892.1225 | 1250426.7937
17 | 2689911.8519 | 1250444.5896
18 | 2689994.1501 | 1250449.8426
19 | 2689914.257 | 1250441.824
20 | 2689855.6428 | 1250644.3131
21 | 2689850.2966 | 1250650.8556
22 | 2689873.5598 | 1250622.3875
23 | 2689849.0502 | 1250652.3808
24 | 2689881.7636 | 1250612.3499
25 | 2689834.4744 | 1250670.2181
26 | 2689870.5454 | 1250603.3396
27 | 2689891.2382 | 1250600.7607
28 | 2689833.6465 | 1250671.2312
29 | 2689891.7485 | 1250600.1365
30 | 2689934.0992 | 1250547.4869
31 | 2689942.5401 | 1250536.9933
32 | 2689933.8673 | 1250547.7753
33 | 2689945.4608 | 1250533.3624
34 | 2689931.9455 | 1250550.1643
35 | 2689949.1744 | 1250528.7457
36 | 2689921.0849 | 1250563.6661
37 | 2689952.4438 | 1250524.6813
38 | 2689911.0596 | 1250576.1294
39 | 2689839.1681 | 1250499.0233
40 | 2689835.4185 | 1250493.1268
41 | 2689849.9388 | 1250515.9607
42 | 2689820.674 | 1250469.9404
43 | 2689828.3573 | 1250535.6263
44 | 2689864.0951 | 1250500.0254
45 | 2689866.5413 | 1250550.957
46 | 2689806.4593 | 1250555.5662
47 | 2689884.0681 | 1250477.5424
48 | 2689874.6298 | 1250570.0095
49 | 2689794.581 | 1250566.3824
50 | 2689886.1337 | 1250475.2173
51 | 2689863.5555 | 1250583.8521
52 | 2689744.9039 | 1250506.5537
53 | 2689757.194 | 1250520.559
54 | 2689731.1806 | 1250490.9204
55 | 2689764.0428 | 1250532.4496
56 | 2689766.9024 | 1250510.6428
57 | 2689702.3252 | 1250498.7924
58 | 2689737.4446 | 1250470.0471
59 | 2689750.0985 | 1250544.6018
60 | 2689665.9884 | 1250535.212
61 | 2689653.6557 | 1250542.4203
62 | 2689695.8379 | 1250556.3241
63 | 2689669.2166 | 1250520.4328
64 | 2689727.5587 | 1250564.245
65 | 2689782.1918 | 1250577.5396
66 | 2689633.0663 | 1250541.5271
67 | 2689718.4052 | 1250572.2222
68 | 2689771.3175 | 1250587.3326
69 | 2689764.1461 | 1250593.7909
70 | 2689754.5563 | 1250602.2698
71 | 2689749.0203 | 1250606.9955
72 | 2689743.9054 | 1250611.3618
73 | 2689825.2869 | 1250681.4614
74 | 2689956.9428 | 1250519.0881
75 | 2689955.4381 | 1250478.9349
76 | 2689947.5571 | 1250471.8329
77 | 2689907.8848 | 1250580.0761
78 | 2689903.1964 | 1250454.529
79 | 2689931.8699 | 1250457.6961
80 | 2689831.0754 | 1250585.6472
81 | 2689834.1805 | 1250577.2907
82 | 2689849.6787 | 1250572.7112
83 | 2689900.9142 | 1250588.7419
84 | 2689851.4978 | 1250373.8762
85 | 2689828.8106 | 1250361.7984
86 | 2689817.7003 | 1250355.6921
87 | 2689804.8795 | 1250346.2598
88 | 2689806.7089 | 1250342.6181
89 | 2689776.0614 | 1250370.7664
90 | 2689788.5212 | 1250321.5656
91 | 2689771.6592 | 1250373.75
92 | 2689752.2983 | 1250384.1357
93 | 2689743.1241 | 1250388.9531
94 | 2689734.1734 | 1250393.6531
95 | 2689788.1157 | 1250321.1618
96 | 2689845.3953 | 1250319.5481
97 | 2689854.668 | 1250311.8766
98 | 2689867.5294 | 1250299.4434
99 | 2689877.1747 | 1250288.8564
100 | 2689882.9467 | 1250282.1143
101 | 2689868.9217 | 1250281.4034
102 | 2689775.4767 | 1250308.5747
103 | 2689896.0271 | 1250267.0576
104 | 2689868.304 | 1250280.8456
105 | 2689908.0379 | 1250253.5157
106 | 2689843.5044 | 1250258.4501
107 | 2689918.646 | 1250241.5553
108 | 2689930.3683 | 1250228.3387
109 | 2689851.0689 | 1250227.8494
110 | 2689832.2025 | 1250248.2438
111 | 2689843.4476 | 1250258.3988
112 | 2689811.8173 | 1250269.9245
113 | 2689798.0435 | 1250284.5737
114 | 2689746.4052 | 1250329.4557
115 | 2689729.6004 | 1250339.8822
116 | 2689710.3735 | 1250351.8116
117 | 2689707.9956 | 1250353.287
118 | 2689678.7893 | 1250371.4033
119 | 2689635.583 | 1250396.1575
120 | 2689693.2003 | 1250394.4402
121 | 2689573.0944 | 1250431.8956
122 | 2689646.6119 | 1250414.9929
123 | 2689598.7218 | 1250453.4212
124 | 2689647.0072 | 1250415.6681
125 | 2689651.2373 | 1250422.8923
126 | 2689611.489 | 1250464.1448
127 | 2689792.7958 | 1250437.624

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98149 | -0.35519 | 0.019955 | 0.0050011
1 | 0.98191 | -0.34686 | 0 | 0
2 | 0.98501 | -0.28656 | 0 | 0
3 | 0.97931 | -0.39767 | 0.033431 | 0.0083786
4 | 0.98477 | -0.29133 | 0 | 0
5 | 0.98523 | -0.28221 | 0.0015393 | 0.00038579
6 | 0.98463 | -0.29403 | 0.008017 | 0.0020092
7 | 0.97827 | -0.41821 | 0.0026031 | 0.00065239
8 | 0.98879 | -0.21352 | 0 | 0
9 | 0.98864 | -0.21647 | 0 | 0
10 | 0.99006 | -0.18929 | 0.00074462 | 0.00018662
11 | 0.98853 | -0.21864 | 0.0010455 | 0.00026203
12 | 0.99914 | -0.016489 | 0 | 0
13 | 0.99941 | -0.011355 | 0.015961 | 0.0040003
14 | 0.99879 | -0.023234 | 0.014006 | 0.0035102
15 | 0.98651 | -0.25755 | 0 | 0
16 | 0.98979 | -0.19444 | 0.018379 | 0.0046062
17 | 0.99024 | -0.18575 | 0 | 0
18 | 0.97779 | -0.42757 | 0.025759 | 0.0064559
19 | 0.99009 | -0.18859 | 0 | 0
20 | 0.98921 | -0.20679 | 0.01694 | 0.0042454
21 | 0.98919 | -0.20715 | 0.00036597 | 9.172e-05
22 | 0.98971 | -0.19703 | 0.00033782 | 8.4666e-05
23 | 0.98918 | -0.20723 | 0.00037186 | 9.3197e-05
24 | 0.98994 | -0.19249 | 0.00049718 | 0.0001246
25 | 0.98915 | -0.20792 | 0.00067972 | 0.00017035
26 | 0.98988 | -0.19367 | 0.0046452 | 0.0011642
27 | 0.99028 | -0.18588 | 0.0004444 | 0.00011138
28 | 0.98915 | -0.20794 | 0.0002748 | 6.8872e-05
29 | 0.9903 | -0.18551 | 0 | 0
30 | 0.98958 | -0.19947 | 0.00508 | 0.0012732
31 | 0.98956 | -0.19994 | 0.00033976 | 8.5152e-05
32 | 0.98959 | -0.19942 | 0.00056764 | 0.00014226
33 | 0.98955 | -0.20008 | 0.00018668 | 4.6787e-05
34 | 0.98961 | -0.199 | 0.0002927 | 7.3358e-05
35 | 0.98954 | -0.20024 | 0.00042516 | 0.00010656
36 | 0.98973 | -0.19656 | 0.00044413 | 0.00011131
37 | 0.98954 | -0.20033 | 0.00033978 | 8.5157e-05
38 | 0.98986 | -0.19417 | 0.00044432 | 0.00011136
39 | 0.99662 | -0.064007 | 0.012247 | 0.0030693
40 | 0.9973 | -0.051161 | 0.0067953 | 0.0017031
41 | 0.99473 | -0.099923 | 0 | 0
42 | 1 | 0 | -0.46436 | -0.11853
43 | 0.99132 | -0.16522 | 0.0095963 | 0.002405
44 | 0.99364 | -0.12071 | 0.011648 | 0.0029192
45 | 0.99263 | -0.14042 | 0.00896 | 0.0022456
46 | 0.98811 | -0.22694 | 0.0086215 | 0.0021607
47 | 0.99218 | -0.14856 | 0.011163 | 0.0027977
48 | 0.99168 | -0.15883 | 0 | 0
49 | 0.9865 | -0.25811 | 0 | 0
50 | 0.99204 | -0.15129 | 0.004905 | 0.0012293
51 | 0.99156 | -0.16121 | 0 | 0
52 | 0.98065 | -0.37172 | 0.0087303 | 0.002188
53 | 0.98176 | -0.35012 | 0 | 0
54 | 0.97959 | -0.39259 | 0 | 0
55 | 0.98274 | -0.33112 | 0 | 0
56 | 0.98165 | -0.35232 | 0.0086794 | 0.0021753
57 | 0.97844 | -0.41502 | 0.0074048 | 0.0018558
58 | 0.9793 | -0.39817 | 0.014074 | 0.0035274
59 | 0.98246 | -0.33657 | 0.0059117 | 0.0014816
60 | 0.97688 | -0.44578 | 0 | 0
61 | 0.97663 | -0.45072 | 0.0092592 | 0.0023206
62 | 0.97674 | -0.44852 | 0.004104 | 0.0010286
63 | 0.9772 | -0.43942 | 0.010785 | 0.0027029
64 | 0.98217 | -0.34221 | 0.0060986 | 0.0015285
65 | 0.9862 | -0.26392 | 0.0085376 | 0.0021397
66 | 0.97644 | -0.45437 | 0.0096725 | 0.0024242
67 | 0.98212 | -0.34316 | 0.0043358 | 0.0010867
68 | 0.98605 | -0.26678 | 0.0013628 | 0.00034156
69 | 0.98597 | -0.26843 | 0.0027012 | 0.00067698
70 | 0.98589 | -0.26999 | 0.0023086 | 0.00057858
71 | 0.98586 | -0.27058 | 0.0026378 | 0.0006611
72 | 0.98585 | -0.27081 | 0.0018861 | 0.0004727
73 | 0.98914 | -0.20811 | 0.00072538 | 0.0001818
74 | 0.98954 | -0.20042 | 0.00070072 | 0.00017562
75 | 0.99 | -0.19046 | 0.0010944 | 0.00027428
76 | 0.99001 | -0.19025 | 0.00059289 | 0.00014859
77 | 0.9899 | -0.19338 | 0.0081009 | 0.0020303
78 | 0.99083 | -0.17447 | 0.00068915 | 0.00017272
79 | 0.99004 | -0.18962 | 0.00074453 | 0.0001866
80 | 0.99142 | -0.16384 | 0.00037069 | 9.2904e-05
81 | 0.99143 | -0.16375 | 0 | 0
82 | 0.99143 | -0.1636 | 0.007209 | 0.0018067
83 | 0.99007 | -0.19003 | 0.00044432 | 0.00011136
84 | 0.98413 | -0.30347 | 0 | 0
85 | 0.98225 | -0.34001 | 0.0027821 | 0.00069727
86 | 0.98135 | -0.35747 | 0.0015128 | 0.00037914
87 | 0.98024 | -0.37898 | 0 | 0
88 | 0.98002 | -0.38334 | 0 | 0
89 | 0.97968 | -0.38999 | 0.0025134 | 0.00062992
90 | 0.97848 | -0.41343 | 0.0021092 | 0.00052863
91 | 0.97962 | -0.39126 | 0.0021776 | 0.00054575
92 | 0.9794 | -0.39564 | 0.0015325 | 0.00038409
93 | 0.9793 | -0.39742 | 0.007271 | 0.0018223
94 | 0.97928 | -0.39782 | 0.0021765 | 0.00054549
95 | 0.97845 | -0.41402 | 0.0024296 | 0.00060891
96 | 0.97527 | -0.47651 | 0.0015823 | 0.00039657
97 | 0.97529 | -0.47616 | 0.0015209 | 0.00038117
98 | 0.97534 | -0.47514 | 0.0036388 | 0.00091196
99 | 0.97543 | -0.47337 | 0 | 0
100 | 0.97538 | -0.47436 | 0.0024831 | 0.00062233
101 | 0.97556 | -0.47075 | 0.00069623 | 0.00017449
102 | 0.97755 | -0.43168 | 0 | 0
103 | 0.97531 | -0.47568 | 0.00069682 | 0.00017464
104 | 0.97557 | -0.47055 | 0.00069623 | 0.00017449
105 | 0.97526 | -0.47664 | 0.00069683 | 0.00017464
106 | 0.97601 | -0.46184 | 0.00069623 | 0.00017449
107 | 0.97523 | -0.47729 | 0.0006265 | 0.00015701
108 | 0.9752 | -0.47781 | 0.001589 | 0.00039824
109 | 0.97622 | -0.45784 | 0.00069683 | 0.00017464
110 | 0.97624 | -0.45749 | 0 | 0
111 | 0.97602 | -0.46182 | 0.00071035 | 0.00017803
112 | 0.97669 | -0.4486 | 0.00069682 | 0.00017464
113 | 0.97701 | -0.44234 | 0.00069682 | 0.00017464
114 | 0.97633 | -0.45561 | 0.0023137 | 0.00057986
115 | 0.9757 | -0.46802 | 0.0015325 | 0.00038409
116 | 0.975 | -0.48159 | 0.0021784 | 0.00054595
117 | 0.97493 | -0.48316 | 0 | 0
118 | 0.97395 | -0.50241 | 0 | 0
119 | 0.97285 | -0.52411 | 0 | 0
120 | 0.97377 | -0.50584 | 0.0068863 | 0.0017259
121 | 0.97225 | -0.53588 | 0 | 0
122 | 0.97255 | -0.53006 | 0.0032428 | 0.00081273
123 | 0.97198 | -0.54137 | 0.0051226 | 0.0012838
124 | 0.97254 | -0.53022 | 0.0034648 | 0.00086837
125 | 0.97248 | -0.53147 | 0.0080771 | 0.0020243
126 | 0.97192 | -0.54252 | 0.0037644 | 0.00094344
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.019955 | -0.0050011 | 0.019963 | 0.0050059 | 7.9211e-06 | 4.7777e-06 | 0.030253 | 0.030253 | 0.030253 | 0.98149 | -0.35519 | 0.98191 | -0.34686 | 8.3112
1 | -0.081946 | -0.020613 | 0.082182 | 0.020764 | 0.00023678 | 0.00015102 | 0.12421 | 0.12421 | 0.12421 | 0.98191 | -0.34686 | 0.98501 | -0.28656 | 34.1235
2 | 0.061983 | 0.015607 | -0.061833 | -0.015511 | 0.00015017 | 9.5537e-05 | 0.093957 | 0.093957 | 0.093957 | 0.98191 | -0.34686 | 0.97931 | -0.39767 | 25.8124
3 | 0.0080199 | 0.0020104 | -0.008018 | -0.0020097 | 1.8198e-06 | 7.4396e-07 | 0.012115 | 0.012116 | 0.012116 | 0.98501 | -0.28656 | 0.98477 | -0.29133 | 3.3285
4 | -0.090202 | -0.022774 | 0.090221 | 0.022786 | 1.8806e-05 | 1.2001e-05 | 0.13632 | 0.13632 | 0.13632 | 0.98501 | -0.28656 | 0.98523 | -0.28221 | 37.4519
5 | 0.028402 | 0.0071327 | -0.028374 | -0.0071154 | 2.7806e-05 | 1.7295e-05 | 0.04316 | 0.04316 | 0.04316 | 0.97931 | -0.39767 | 0.97827 | -0.41821 | 11.8573
6 | 0.008018 | 0.0020097 | -0.008017 | -0.0020092 | 1.0339e-06 | 4.2278e-07 | 0.012116 | 0.012116 | 0.012116 | 0.98477 | -0.29133 | 0.98463 | -0.29403 | 3.3285
7 | -0.09176 | -0.023172 | 0.091869 | 0.023241 | 0.00010859 | 6.9303e-05 | 0.13865 | 0.13865 | 0.13865 | 0.98523 | -0.28221 | 0.98651 | -0.25755 | 38.0906
8 | 0.025771 | 0.006463 | -0.025759 | -0.0064559 | 1.149e-05 | 7.1034e-06 | 0.039201 | 0.039201 | 0.039201 | 0.97827 | -0.41821 | 0.97779 | -0.42757 | 10.7695
9 | 0.17289 | 0.043988 | -0.17286 | -0.043972 | 2.4566e-05 | 1.5524e-05 | 0.26041 | 0.26041 | 0.26041 | 0.98879 | -0.21352 | 0.98864 | -0.21647 | 17.8854
10 | -0.17289 | -0.043988 | 0.17309 | 0.044116 | 0.00020222 | 0.00012779 | 0.26041 | 0.26041 | 0.26041 | 0.98879 | -0.21352 | 0.99006 | -0.18929 | 17.8854
11 | 0.17286 | 0.043972 | -0.17285 | -0.043961 | 1.8058e-05 | 1.1411e-05 | 0.26041 | 0.26041 | 0.26041 | 0.98864 | -0.21647 | 0.98853 | -0.21864 | 17.8854
12 | -0.17384 | -0.044302 | 0.17384 | 0.044306 | 5.8437e-06 | 3.6931e-06 | 0.26153 | 0.26153 | 0.26153 | 0.99006 | -0.18929 | 0.99009 | -0.18859 | 17.9622
13 | 0.1718 | 0.043699 | -0.17148 | -0.043494 | 0.00032143 | 0.00020506 | 0.25884 | 0.25884 | 0.25884 | 0.98853 | -0.21864 | 0.98651 | -0.25755 | 35.5547
14 | -0.01401 | -0.0035127 | 0.014014 | 0.0035147 | 3.4285e-06 | 1.9192e-06 | 0.020866 | 0.020866 | 0.020866 | 0.99914 | -0.016489 | 0.99941 | -0.011355 | 5.7325
15 | 0.01401 | 0.0035127 | -0.014006 | -0.0035102 | 4.502e-06 | 2.5203e-06 | 0.020866 | 0.020866 | 0.020866 | 0.99914 | -0.016489 | 0.99879 | -0.023234 | 5.7325
16 | -0.029975 | -0.007515 | 0.029991 | 0.0075251 | 1.6228e-05 | 1.0101e-05 | 0.044631 | 0.044631 | 0.044631 | 0.99941 | -0.011355 | 1 | 0 | 12.2612
17 | 0.07961 | 0.020252 | -0.079434 | -0.02014 | 0.00017575 | 0.00011207 | 0.12019 | 0.12019 | 0.12019 | 0.98651 | -0.25755 | 0.98413 | -0.30347 | 33.0189
18 | -0.018379 | -0.0046062 | 0.018387 | 0.0046107 | 7.6065e-06 | 4.5265e-06 | 0.02763 | 0.02763 | 0.02763 | 0.98979 | -0.19444 | 0.99024 | -0.18575 | 7.5907
19 | 0.1763 | 0.04493 | -0.17627 | -0.044915 | 2.4136e-05 | 1.5259e-05 | 0.26518 | 0.26519 | 0.26519 | 0.99024 | -0.18575 | 0.99009 | -0.18859 | 18.2133
20 | -0.19468 | -0.049541 | 0.19479 | 0.049608 | 0.00010594 | 6.7124e-05 | 0.29281 | 0.29281 | 0.29281 | 0.99024 | -0.18575 | 0.99083 | -0.17447 | 20.1109
21 | 0.002432 | 0.00060887 | -0.0024319 | -0.0006091 | 1.1877e-07 | -2.2889e-07 | 0.0036548 | 0.0036549 | 0.0036549 | 0.99009 | -0.18859 | 0.99004 | -0.18962 | 1.0041
22 | 0.0024178 | 0.00060539 | -0.0024178 | -0.00060548 | 4.1907e-08 | -8.1643e-08 | 0.0036368 | 0.0036369 | 0.0036369 | 0.98921 | -0.20679 | 0.98919 | -0.20715 | 0.99914
23 | -0.019357 | -0.0048508 | 0.019366 | 0.0048562 | 9.0027e-06 | 5.3981e-06 | 0.029118 | 0.029118 | 0.029118 | 0.98921 | -0.20679 | 0.98971 | -0.19703 | 7.9995
24 | 0.0020518 | 0.00051376 | -0.0020518 | -0.00051378 | 7.0362e-09 | -2.0783e-08 | 0.0030864 | 0.0030864 | 0.0030864 | 0.98919 | -0.20715 | 0.98918 | -0.20723 | 0.8479
25 | -0.019704 | -0.0049409 | 0.019708 | 0.0049435 | 4.2668e-06 | 2.5641e-06 | 0.029626 | 0.029626 | 0.029626 | 0.98971 | -0.19703 | 0.98994 | -0.19249 | 8.139
26 | 0.00168 | 0.00042058 | -0.0016799 | -0.00042084 | 5.5163e-08 | -2.6039e-07 | 0.002527 | 0.0025271 | 0.0025271 | 0.98918 | -0.20723 | 0.98915 | -0.20792 | 0.69425
27 | 0.0046455 | 0.0011642 | -0.0046452 | -0.0011642 | 2.6262e-07 | -1.6573e-08 | 0.0069827 | 0.0069828 | 0.0069828 | 0.98994 | -0.19249 | 0.98988 | -0.19367 | 1.9183
28 | -0.024851 | -0.0062322 | 0.024859 | 0.0062371 | 7.8334e-06 | 4.8208e-06 | 0.037356 | 0.037356 | 0.037356 | 0.98994 | -0.19249 | 0.99028 | -0.18588 | 10.2626
29 | 0.0010002 | 0.00025049 | -0.0010002 | -0.0002505 | 1.1106e-09 | -1.6083e-08 | 0.0015046 | 0.0015046 | 0.0015046 | 0.98915 | -0.20792 | 0.98915 | -0.20794 | 0.41334
30 | -0.025303 | -0.0063484 | 0.025304 | 0.0063487 | 4.3714e-07 | 2.6939e-07 | 0.038024 | 0.038024 | 0.038024 | 0.99028 | -0.18588 | 0.9903 | -0.18551 | 10.446
31 | 0.00072538 | 0.00018163 | -0.00072538 | -0.0001818 | 5.8991e-09 | -1.6581e-07 | 0.0010912 | 0.0010912 | 0.0010912 | 0.98915 | -0.20794 | 0.98914 | -0.20811 | 0.29979
32 | -0.042679 | -0.010705 | 0.042733 | 0.01074 | 5.4361e-05 | 3.4337e-05 | 0.064132 | 0.064132 | 0.064132 | 0.9903 | -0.18551 | 0.99168 | -0.15883 | 17.6186
33 | 0.017375 | 0.0043567 | -0.017371 | -0.0043545 | 3.738e-06 | 2.2042e-06 | 0.026108 | 0.026108 | 0.026108 | 0.9903 | -0.18551 | 0.99007 | -0.19003 | 7.1726
34 | 0.0019922 | 0.00049885 | -0.0019921 | -0.00049899 | 4.5315e-08 | -1.4401e-07 | 0.0029954 | 0.0029955 | 0.0029955 | 0.98958 | -0.19947 | 0.98956 | -0.19994 | 0.82294
35 | -0.0070722 | -0.001772 | 0.0070722 | 0.001772 | 1.5691e-08 | 5.2886e-09 | 0.010634 | 0.010634 | 0.010634 | 0.98958 | -0.19947 | 0.98959 | -0.19942 | 2.9215
36 | 0.0016524 | 0.00041384 | -0.0016524 | -0.00041389 | 1.0787e-08 | -5.2959e-08 | 0.0024846 | 0.0024846 | 0.0024846 | 0.98956 | -0.19994 | 0.98955 | -0.20008 | 0.68259
37 | -0.0076399 | -0.0019143 | 0.00764 | 0.0019143 | 1.5173e-07 | 5.7716e-08 | 0.011488 | 0.011488 | 0.011488 | 0.98959 | -0.19942 | 0.98961 | -0.199 | 3.156
38 | 0.0014657 | 0.00036711 | -0.0014657 | -0.00036718 | 1.0792e-08 | -6.9208e-08 | 0.0022039 | 0.0022039 | 0.0022039 | 0.98955 | -0.20008 | 0.98954 | -0.20024 | 0.60547
39 | -0.0079327 | -0.0019877 | 0.0079336 | 0.0019881 | 9.2446e-07 | 3.69e-07 | 0.011928 | 0.011928 | 0.011928 | 0.98961 | -0.199 | 0.98973 | -0.19656 | 3.2769
40 | 0.0010405 | 0.00026062 | -0.0010405 | -0.00026068 | 4.7884e-09 | -6.3943e-08 | 0.0015646 | 0.0015646 | 0.0015646 | 0.98954 | -0.20024 | 0.98954 | -0.20033 | 0.42984
41 | -0.0083778 | -0.0020994 | 0.0083787 | 0.0020998 | 9.5157e-07 | 4.0342e-07 | 0.012595 | 0.012595 | 0.012595 | 0.98973 | -0.19656 | 0.98986 | -0.19417 | 3.4603
42 | 0.00070072 | 0.00017553 | -0.00070072 | -0.00017562 | 2.9886e-09 | -9.0298e-08 | 0.0010537 | 0.0010537 | 0.0010537 | 0.98954 | -0.20033 | 0.98954 | -0.20042 | 0.28948
43 | -0.008823 | -0.0022111 | 0.0088234 | 0.0022113 | 3.3414e-07 | 1.4874e-07 | 0.013263 | 0.013263 | 0.013263 | 0.98986 | -0.19417 | 0.9899 | -0.19338 | 3.6438
44 | -0.42459 | -0.10845 | 0.42485 | 0.10862 | 0.00026387 | 0.00016851 | 0.63466 | 0.63466 | 0.63466 | 0.99662 | -0.064007 | 0.9973 | -0.051161 | 43.5893
45 | 0.41234 | 0.10538 | -0.41163 | -0.10492 | 0.00071491 | 0.0004565 | 0.61638 | 0.61638 | 0.61638 | 0.99662 | -0.064007 | 0.99473 | -0.099923 | 42.3335
46 | -0.43165 | -0.11032 | 0.43272 | 0.11101 | 0.001071 | 0.00068401 | 0.6448 | 0.6448 | 0.6448 | 0.9973 | -0.051161 | 1 | 0 | 44.2857
47 | 0.12824 | 0.032732 | -0.12784 | -0.032475 | 0.00040321 | 0.00025768 | 0.19205 | 0.19205 | 0.19205 | 0.99473 | -0.099923 | 0.99132 | -0.16522 | 52.7606
48 | 0.22395 | 0.057206 | -0.22373 | -0.057063 | 0.00022478 | 0.00014275 | 0.33539 | 0.33539 | 0.33539 | 0.99473 | -0.099923 | 0.99364 | -0.12071 | 23.035
49 | 0.059434 | 0.014986 | -0.059319 | -0.014913 | 0.00011495 | 7.3065e-05 | 0.088939 | 0.088939 | 0.088939 | 0.99473 | -0.099923 | 0.99263 | -0.14042 | 24.4338
50 | 0.11824 | 0.03007 | -0.11789 | -0.029846 | 0.00035048 | 0.00022393 | 0.17764 | 0.17764 | 0.17764 | 0.99132 | -0.16522 | 0.98811 | -0.22694 | 48.8034
51 | 0.21208 | 0.054144 | -0.21179 | -0.053963 | 0.00028501 | 0.00018085 | 0.31795 | 0.31795 | 0.31795 | 0.99364 | -0.12071 | 0.99218 | -0.14856 | 21.8371
52 | 0.050359 | 0.012668 | -0.050315 | -0.01264 | 4.4259e-05 | 2.8058e-05 | 0.075507 | 0.075507 | 0.075507 | 0.99263 | -0.14042 | 0.99168 | -0.15883 | 20.7438
53 | 0.10927 | 0.027685 | -0.10911 | -0.027581 | 0.00016334 | 0.00010433 | 0.16466 | 0.16466 | 0.16466 | 0.98811 | -0.22694 | 0.9865 | -0.25811 | 45.2366
54 | 0.20063 | 0.051165 | -0.2006 | -0.051149 | 2.6453e-05 | 1.6769e-05 | 0.30121 | 0.30121 | 0.30121 | 0.99218 | -0.14856 | 0.99204 | -0.15129 | 20.6872
55 | 0.0075814 | 0.0018998 | -0.0075805 | -0.0018995 | 8.5944e-07 | 3.2158e-07 | 0.011376 | 0.011376 | 0.011376 | 0.99168 | -0.15883 | 0.99156 | -0.16121 | 3.1252
56 | 0.019442 | 0.0048751 | -0.019437 | -0.0048718 | 5.3775e-06 | 3.2288e-06 | 0.029327 | 0.029327 | 0.029327 | 0.9865 | -0.25811 | 0.9862 | -0.26392 | 8.057
57 | 0.089666 | 0.022706 | -0.089353 | -0.022506 | 0.00031313 | 0.00019982 | 0.13533 | 0.13533 | 0.13533 | 0.9865 | -0.25811 | 0.98274 | -0.33112 | 37.1797
58 | 0.1957 | 0.049919 | -0.19548 | -0.049781 | 0.00021884 | 0.00013866 | 0.29385 | 0.29385 | 0.29385 | 0.99204 | -0.15129 | 0.99083 | -0.17447 | 20.182
59 | 0.0075805 | 0.0018995 | -0.0075797 | -0.0018992 | 8.6361e-07 | 3.232e-07 | 0.011376 | 0.011376 | 0.011376 | 0.99156 | -0.16121 | 0.99143 | -0.1636 | 3.1253
60 | -0.064186 | -0.016145 | 0.064253 | 0.016187 | 6.6309e-05 | 4.2202e-05 | 0.097415 | 0.097415 | 0.097415 | 0.98065 | -0.37172 | 0.98176 | -0.35012 | 26.7625
61 | 0.055456 | 0.013957 | -0.055401 | -0.013922 | 5.5263e-05 | 3.5106e-05 | 0.084168 | 0.084168 | 0.084168 | 0.98065 | -0.37172 | 0.97959 | -0.39259 | 23.1232
62 | -0.072933 | -0.018363 | 0.072999 | 0.018405 | 6.6324e-05 | 4.2264e-05 | 0.11057 | 0.11057 | 0.11057 | 0.98176 | -0.35012 | 0.98274 | -0.33112 | 30.3769
63 | 0.0086803 | 0.0021757 | -0.0086794 | -0.0021753 | 9.088e-07 | 4.0461e-07 | 0.013157 | 0.013157 | 0.013157 | 0.98176 | -0.35012 | 0.98165 | -0.35232 | 3.6144
64 | 0.041323 | 0.010392 | -0.041278 | -0.010364 | 4.4211e-05 | 2.7919e-05 | 0.062783 | 0.062783 | 0.062783 | 0.97959 | -0.39259 | 0.97844 | -0.41502 | 17.2481
65 | 0.014078 | 0.0035295 | -0.014074 | -0.0035274 | 3.7376e-06 | 2.1178e-06 | 0.021386 | 0.021386 | 0.021386 | 0.97959 | -0.39259 | 0.9793 | -0.39817 | 5.8752
66 | 0.016353 | 0.0041006 | -0.016349 | -0.0040981 | 4.2531e-06 | 2.4877e-06 | 0.024762 | 0.024762 | 0.024762 | 0.98274 | -0.33112 | 0.98246 | -0.33657 | 6.8028
67 | 0.033874 | 0.0085086 | -0.033834 | -0.0084839 | 3.9396e-05 | 2.4717e-05 | 0.051522 | 0.051522 | 0.051522 | 0.97844 | -0.41502 | 0.9772 | -0.43942 | 14.1544
68 | 0.010437 | 0.0026165 | -0.010435 | -0.0026151 | 2.802e-06 | 1.4148e-06 | 0.015809 | 0.015809 | 0.015809 | 0.98246 | -0.33657 | 0.98217 | -0.34221 | 4.3431
69 | 0.018938 | 0.0047482 | -0.018933 | -0.0047456 | 4.4578e-06 | 2.6742e-06 | 0.028848 | 0.028848 | 0.028848 | 0.97688 | -0.44578 | 0.97663 | -0.45072 | 7.9252
70 | 0.0041045 | 0.0010284 | -0.004104 | -0.0010286 | 5.3594e-07 | -1.1467e-07 | 0.0062521 | 0.0062522 | 0.0062522 | 0.97688 | -0.44578 | 0.97674 | -0.44852 | 1.7177
71 | -0.023042 | -0.0057767 | 0.023049 | 0.005781 | 6.9888e-06 | 4.2834e-06 | 0.0351 | 0.0351 | 0.0351 | 0.97688 | -0.44578 | 0.9772 | -0.43942 | 9.6428
72 | 0.0096742 | 0.002425 | -0.0096725 | -0.0024242 | 1.6791e-06 | 8.168e-07 | 0.01474 | 0.01474 | 0.01474 | 0.97663 | -0.45072 | 0.97644 | -0.45437 | 4.0495
73 | 0.004336 | 0.0010866 | -0.0043358 | -0.0010867 | 1.9649e-07 | -2.79e-08 | 0.0065692 | 0.0065692 | 0.0065692 | 0.98217 | -0.34221 | 0.98212 | -0.34316 | 1.8047
74 | 0.010899 | 0.0027321 | -0.010898 | -0.0027313 | 1.4842e-06 | 7.6319e-07 | 0.016446 | 0.016446 | 0.016446 | 0.9862 | -0.26392 | 0.98605 | -0.26678 | 4.518
75 | 0.009535 | 0.0023898 | -0.0095343 | -0.0023894 | 7.4931e-07 | 3.5646e-07 | 0.014389 | 0.014389 | 0.014389 | 0.98605 | -0.26678 | 0.98597 | -0.26843 | 3.953
76 | 0.0068331 | 0.0017125 | -0.0068326 | -0.0017123 | 5.1053e-07 | 1.6349e-07 | 0.010312 | 0.010313 | 0.010313 | 0.98597 | -0.26843 | 0.98589 | -0.26999 | 2.8331
77 | 0.0045241 | 0.0011337 | -0.0045239 | -0.0011337 | 1.2726e-07 | -1.1364e-08 | 0.0068282 | 0.0068282 | 0.0068282 | 0.98589 | -0.26999 | 0.98586 | -0.27058 | 1.8759
78 | 0.0018861 | 0.00047262 | -0.0018861 | -0.0004727 | 2.0438e-08 | -7.2669e-08 | 0.0028468 | 0.0028468 | 0.0028468 | 0.98586 | -0.27058 | 0.98585 | -0.27081 | 0.78209
79 | -0.0010944 | -0.00027428 | 0.0010944 | 0.00027415 | 1.0764e-08 | -1.2952e-07 | 0.0016449 | 0.0016449 | 0.0016449 | 0.99 | -0.19046 | 0.99001 | -0.19025 | 0.4519
80 | -0.0016873 | -0.00042274 | 0.0016873 | 0.0004225 | 5.0927e-08 | -2.3895e-07 | 0.002536 | 0.0025359 | 0.002536 | 0.99001 | -0.19025 | 0.99004 | -0.18962 | 0.6967
81 | -0.016924 | -0.0042416 | 0.016927 | 0.0042432 | 2.6993e-06 | 1.5845e-06 | 0.025441 | 0.025441 | 0.025441 | 0.9899 | -0.19338 | 0.99007 | -0.19003 | 6.9892
82 | -0.00037069 | -9.2904e-05 | 0.00037069 | 9.2725e-05 | 1.622e-09 | -1.7917e-07 | 0.00055637 | 0.0005563 | 0.00055637 | 0.99142 | -0.16384 | 0.99143 | -0.16375 | 0.15285
83 | -0.00037069 | -9.2725e-05 | 0.00037069 | 9.2437e-05 | 2.6052e-09 | -2.8787e-07 | 0.0005563 | 0.0005562 | 0.0005563 | 0.99143 | -0.16375 | 0.99143 | -0.1636 | 0.15283
84 | 0.079434 | 0.02014 | -0.079295 | -0.020052 | 0.00013924 | 8.879e-05 | 0.12019 | 0.12019 | 0.12019 | 0.98413 | -0.30347 | 0.98225 | -0.34001 | 33.0189
85 | 0.076513 | 0.019354 | -0.076449 | -0.019314 | 6.4028e-05 | 4.0817e-05 | 0.11597 | 0.11597 | 0.11597 | 0.98225 | -0.34001 | 0.98135 | -0.35747 | 31.8611
86 | 0.074936 | 0.018934 | -0.074859 | -0.018885 | 7.7214e-05 | 4.9216e-05 | 0.11368 | 0.11368 | 0.11368 | 0.98135 | -0.35747 | 0.98024 | -0.37898 | 31.2309
87 | 0.059176 | 0.014951 | -0.059163 | -0.014943 | 1.234e-05 | 7.846e-06 | 0.089872 | 0.089872 | 0.089872 | 0.98024 | -0.37898 | 0.98002 | -0.38334 | 24.6902
88 | 0.015683 | 0.0039342 | -0.015675 | -0.0039294 | 8.2201e-06 | 4.7737e-06 | 0.023808 | 0.023809 | 0.023809 | 0.98024 | -0.37898 | 0.97968 | -0.38999 | 6.5408
89 | 0.059163 | 0.014943 | -0.059078 | -0.014889 | 8.5195e-05 | 5.4171e-05 | 0.089872 | 0.089872 | 0.089872 | 0.98002 | -0.38334 | 0.97848 | -0.41343 | 24.6902
90 | 0.013162 | 0.0032995 | -0.013161 | -0.0032991 | 7.9699e-07 | 4.4311e-07 | 0.019991 | 0.019991 | 0.019991 | 0.97968 | -0.38999 | 0.97962 | -0.39126 | 5.4921
91 | 0.056969 | 0.01436 | -0.056967 | -0.014359 | 1.6119e-06 | 1.0244e-06 | 0.086665 | 0.086665 | 0.086665 | 0.97848 | -0.41343 | 0.97845 | -0.41402 | 23.809
92 | 0.010983 | 0.0027533 | -0.010981 | -0.0027521 | 2.2943e-06 | 1.1917e-06 | 0.016683 | 0.016684 | 0.016684 | 0.97962 | -0.39126 | 0.9794 | -0.39564 | 4.5834
93 | 0.0094483 | 0.002368 | -0.0094475 | -0.0023677 | 8.0074e-07 | 3.8209e-07 | 0.014355 | 0.014355 | 0.014355 | 0.9794 | -0.39564 | 0.9793 | -0.39742 | 3.9437
94 | 0.0021766 | 0.00054539 | -0.0021765 | -0.00054549 | 4.1466e-08 | -1.0066e-07 | 0.0033072 | 0.0033072 | 0.0033072 | 0.9793 | -0.39742 | 0.97928 | -0.39782 | 0.90858
95 | 0.054538 | 0.01375 | -0.054492 | -0.013721 | 4.6048e-05 | 2.9247e-05 | 0.08297 | 0.08297 | 0.08297 | 0.97845 | -0.41402 | 0.97755 | -0.43168 | 22.794
96 | -0.0015823 | -0.00039657 | 0.0015823 | 0.00039643 | 2.6303e-08 | -1.3334e-07 | 0.0024142 | 0.0024142 | 0.0024142 | 0.97527 | -0.47651 | 0.97529 | -0.47616 | 0.66325
97 | -0.0031032 | -0.0007776 | 0.0031034 | 0.00077747 | 1.5074e-07 | -1.2732e-07 | 0.0047346 | 0.0047345 | 0.0047346 | 0.97529 | -0.47616 | 0.97534 | -0.47514 | 1.3007
98 | -0.0067421 | -0.0016894 | 0.0067427 | 0.0016896 | 5.6822e-07 | 1.8491e-07 | 0.010286 | 0.010286 | 0.010286 | 0.97534 | -0.47514 | 0.97543 | -0.47337 | 2.8258
99 | 0.006093 | 0.0015263 | -0.0060927 | -0.0015263 | 2.8753e-07 | 7.3236e-08 | 0.0092946 | 0.0092946 | 0.0092946 | 0.97543 | -0.47337 | 0.97538 | -0.47436 | 2.5535
100 | -0.012836 | -0.003216 | 0.012837 | 0.0032168 | 1.5988e-06 | 8.8439e-07 | 0.01958 | 0.01958 | 0.01958 | 0.97543 | -0.47337 | 0.97556 | -0.47075 | 5.3793
101 | 0.0036096 | 0.00090394 | -0.0036094 | -0.00090404 | 2.268e-07 | -1.0378e-07 | 0.0055065 | 0.0055066 | 0.0055066 | 0.97538 | -0.47436 | 0.97531 | -0.47568 | 1.5128
102 | -0.013534 | -0.0033913 | 0.013534 | 0.0033914 | 1.33e-07 | 7.4727e-08 | 0.020642 | 0.020642 | 0.020642 | 0.97556 | -0.47075 | 0.97557 | -0.47055 | 5.671
103 | 0.036735 | 0.0092614 | -0.036693 | -0.009235 | 4.2023e-05 | 2.6446e-05 | 0.055937 | 0.055937 | 0.055937 | 0.97755 | -0.43168 | 0.97633 | -0.45561 | 15.3673
104 | 0.017757 | 0.0044597 | -0.017748 | -0.0044543 | 9.0283e-06 | 5.3653e-06 | 0.027033 | 0.027033 | 0.027033 | 0.97755 | -0.43168 | 0.97701 | -0.44234 | 7.4267
105 | 0.0029125 | 0.0007294 | -0.0029124 | -0.00072954 | 1.3402e-07 | -1.401e-07 | 0.0044434 | 0.0044435 | 0.0044435 | 0.97531 | -0.47568 | 0.97526 | -0.47664 | 1.2207
106 | -0.01423 | -0.0035659 | 0.014236 | 0.0035693 | 5.9029e-06 | 3.3604e-06 | 0.021704 | 0.021704 | 0.021704 | 0.97557 | -0.47055 | 0.97601 | -0.46184 | 5.9627
107 | 0.0022156 | 0.0005549 | -0.0022155 | -0.00055506 | 6.8505e-08 | -1.5564e-07 | 0.0033803 | 0.0033804 | 0.0033804 | 0.97526 | -0.47664 | 0.97523 | -0.47729 | 0.92868
108 | -0.014932 | -0.0037438 | 0.014932 | 0.0037438 | 1.4869e-08 | 8.5607e-09 | 0.022766 | 0.022766 | 0.022766 | 0.97601 | -0.46184 | 0.97602 | -0.46182 | 6.2543
109 | 0.001589 | 0.00039804 | -0.001589 | -0.00039824 | 3.8942e-08 | -1.955e-07 | 0.0024245 | 0.0024246 | 0.0024246 | 0.97523 | -0.47729 | 0.9752 | -0.47781 | 0.66609
110 | -0.00069683 | -0.00017464 | 0.00069684 | 0.0001743 | 1.1752e-08 | -3.3984e-07 | 0.0010621 | 0.001062 | 0.0010621 | 0.97622 | -0.45784 | 0.97624 | -0.45749 | 0.2918
111 | -0.016342 | -0.004098 | 0.016349 | 0.004102 | 6.925e-06 | 4.0597e-06 | 0.024911 | 0.02491 | 0.024911 | 0.97624 | -0.45749 | 0.97669 | -0.4486 | 6.8436
112 | 0.015646 | 0.0039237 | -0.015642 | -0.0039218 | 3.2316e-06 | 1.8788e-06 | 0.023849 | 0.023849 | 0.023849 | 0.97624 | -0.45749 | 0.97602 | -0.46182 | 6.5518
113 | -0.017046 | -0.0042767 | 0.017051 | 0.0042797 | 5.0863e-06 | 3.0035e-06 | 0.025972 | 0.025972 | 0.025972 | 0.97669 | -0.4486 | 0.97701 | -0.44234 | 7.1352
114 | 0.034379 | 0.0086551 | -0.034359 | -0.0086424 | 2.0372e-05 | 1.2791e-05 | 0.052411 | 0.052411 | 0.052411 | 0.97633 | -0.45561 | 0.9757 | -0.46802 | 14.3986
115 | 0.032826 | 0.0082583 | -0.032805 | -0.0082449 | 2.1275e-05 | 1.3334e-05 | 0.050074 | 0.050074 | 0.050074 | 0.9757 | -0.46802 | 0.975 | -0.48159 | 13.7565
116 | 0.030626 | 0.007699 | -0.030624 | -0.0076975 | 2.2935e-06 | 1.4329e-06 | 0.046749 | 0.046749 | 0.046749 | 0.975 | -0.48159 | 0.97493 | -0.48316 | 12.8432
117 | 0.030624 | 0.0076975 | -0.030596 | -0.00768 | 2.8109e-05 | 1.7563e-05 | 0.046749 | 0.046749 | 0.046749 | 0.97493 | -0.48316 | 0.97395 | -0.50241 | 12.8432
118 | 0.023708 | 0.0059537 | -0.023684 | -0.0059386 | 2.4528e-05 | 1.5078e-05 | 0.036227 | 0.036227 | 0.036227 | 0.97395 | -0.50241 | 0.97285 | -0.52411 | 9.9524
119 | 0.0068875 | 0.0017263 | -0.0068863 | -0.0017259 | 1.1283e-06 | 3.8404e-07 | 0.010523 | 0.010523 | 0.010523 | 0.97395 | -0.50241 | 0.97377 | -0.50584 | 2.8909
120 | 0.0088944 | 0.0022306 | -0.0088894 | -0.0022283 | 4.9859e-06 | 2.2996e-06 | 0.013605 | 0.013605 | 0.013605 | 0.97285 | -0.52411 | 0.97225 | -0.53588 | 3.7377
121 | 0.01479 | 0.0037081 | -0.014785 | -0.0037057 | 4.1887e-06 | 2.4098e-06 | 0.022622 | 0.022622 | 0.022622 | 0.97285 | -0.52411 | 0.97255 | -0.53006 | 6.2148
122 | 0.0088894 | 0.0022283 | -0.0088871 | -0.0022272 | 2.3232e-06 | 1.0719e-06 | 0.013605 | 0.013605 | 0.013605 | 0.97225 | -0.53588 | 0.97198 | -0.54137 | 3.7378
123 | 0.011542 | 0.0028929 | -0.011542 | -0.0028929 | 9.1515e-08 | 4.886e-08 | 0.01766 | 0.01766 | 0.01766 | 0.97255 | -0.53006 | 0.97254 | -0.53022 | 4.8517
124 | 0.0037646 | 0.00094336 | -0.0037644 | -0.00094344 | 2.0767e-07 | -7.3728e-08 | 0.0057632 | 0.0057633 | 0.0057633 | 0.97198 | -0.54137 | 0.97192 | -0.54252 | 1.5833
125 | 0.0080776 | 0.0020245 | -0.0080771 | -0.0020243 | 4.7952e-07 | 2.0302e-07 | 0.012359 | 0.012359 | 0.012359 | 0.97254 | -0.53022 | 0.97248 | -0.53147 | 3.3953

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47593 | 0.12143

## res_load
| p_mw | q_mvar
0 | 0.019955 | 0.0050011
1 | 0.033431 | 0.0083786
2 | 0.0015393 | 0.00038579
3 | 0.008017 | 0.0020092
4 | 0.0026031 | 0.00065239
5 | 0.00074462 | 0.00018662
6 | 0.0010455 | 0.00026203
7 | 0.015961 | 0.0040003
8 | 0.014006 | 0.0035102
9 | 0.018379 | 0.0046062
10 | 0.025759 | 0.0064559
11 | 0.01694 | 0.0042454
12 | 0.00036597 | 9.172e-05
13 | 0.00033782 | 8.4666e-05
14 | 0.00037186 | 9.3197e-05
15 | 0.00049718 | 0.0001246
16 | 0.00067972 | 0.00017035
17 | 0.0046452 | 0.0011642
18 | 0.0004444 | 0.00011138
19 | 0.0002748 | 6.8872e-05
20 | 0.00508 | 0.0012732
21 | 0.00033976 | 8.5152e-05
22 | 0.00056764 | 0.00014226
23 | 0.00018668 | 4.6787e-05
24 | 0.0002927 | 7.3358e-05
25 | 0.00042516 | 0.00010656
26 | 0.00044413 | 0.00011131
27 | 0.00033978 | 8.5157e-05
28 | 0.00044432 | 0.00011136
29 | 0.012247 | 0.0030693
30 | 0.0067953 | 0.0017031
31 | 0.011567 | 0.0028989
32 | 0.0095963 | 0.002405
33 | 0.011648 | 0.0029192
34 | 0.00896 | 0.0022456
35 | 0.0086215 | 0.0021607
36 | 0.011163 | 0.0027977
37 | 0.004905 | 0.0012293
38 | 0.0087303 | 0.002188
39 | 0.0086794 | 0.0021753
40 | 0.0074048 | 0.0018558
41 | 0.014074 | 0.0035274
42 | 0.0059117 | 0.0014816
43 | 0.0092592 | 0.0023206
44 | 0.004104 | 0.0010286
45 | 0.010785 | 0.0027029
46 | 0.0060986 | 0.0015285
47 | 0.0085376 | 0.0021397
48 | 0.0096725 | 0.0024242
49 | 0.0043358 | 0.0010867
50 | 0.0013628 | 0.00034156
51 | 0.0027012 | 0.00067698
52 | 0.0023086 | 0.00057858
53 | 0.0026378 | 0.0006611
54 | 0.0018861 | 0.0004727
55 | 0.00072538 | 0.0001818
56 | 0.00070072 | 0.00017562
57 | 0.0010944 | 0.00027428
58 | 0.00059289 | 0.00014859
59 | 0.0081009 | 0.0020303
60 | 0.00068915 | 0.00017272
61 | 0.00074453 | 0.0001866
62 | 0.00037069 | 9.2904e-05
63 | 0.007209 | 0.0018067
64 | 0.00044432 | 0.00011136
65 | 0.0027821 | 0.00069727
66 | 0.0015128 | 0.00037914
67 | 0.0025134 | 0.00062992
68 | 0.0021092 | 0.00052863
69 | 0.0021776 | 0.00054575
70 | 0.0015325 | 0.00038409
71 | 0.007271 | 0.0018223
72 | 0.0021765 | 0.00054549
73 | 0.0024296 | 0.00060891
74 | 0.0015823 | 0.00039657
75 | 0.0015209 | 0.00038117
76 | 0.0036388 | 0.00091196
77 | 0.0024831 | 0.00062233
78 | 0.00069623 | 0.00017449
79 | 0.00069682 | 0.00017464
80 | 0.00069623 | 0.00017449
81 | 0.00069683 | 0.00017464
82 | 0.00069623 | 0.00017449
83 | 0.0006265 | 0.00015701
84 | 0.001589 | 0.00039824
85 | 0.00069683 | 0.00017464
86 | 0.00071035 | 0.00017803
87 | 0.00069682 | 0.00017464
88 | 0.00069682 | 0.00017464
89 | 0.0023137 | 0.00057986
90 | 0.0015325 | 0.00038409
91 | 0.0021784 | 0.00054595
92 | 0.0068863 | 0.0017259
93 | 0.0032428 | 0.00081273
94 | 0.0051226 | 0.0012838
95 | 0.0034648 | 0.00086837
96 | 0.0080771 | 0.0020243
97 | 0.0037644 | 0.00094344

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1