## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_191-19_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_191-19_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_191-19_0_6_node_13 | 0.4 | n |  | TRUE
3 | bus_LV_191-19_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_191-19_0_6_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_191-19_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_191-19_0_6_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_191-19_0_6_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_191-19_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_191-19_0_6_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_191-19_0_6_node_64 | 0.4 | n |  | TRUE
11 | bus_LV_191-19_0_6_node_128 | 0.4 | n |  | TRUE
12 | bus_LV_191-19_0_6_node_125 | 0.4 | n |  | TRUE
13 | bus_LV_191-19_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_191-19_0_6_node_130 | 0.4 | n |  | TRUE
15 | bus_LV_191-19_0_6_node_110 | 0.4 | n |  | TRUE
16 | bus_LV_191-19_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_191-19_0_6_node_60 | 0.4 | n |  | TRUE
18 | bus_LV_191-19_0_6_node_115 | 0.4 | n |  | TRUE
19 | bus_LV_191-19_0_6_node_126 | 0.4 | n |  | TRUE
20 | bus_LV_191-19_0_6_node_76 | 0.4 | n |  | TRUE
21 | bus_LV_191-19_0_6_node_88 | 0.4 | n |  | TRUE
22 | bus_LV_191-19_0_6_node_75 | 0.4 | n |  | TRUE
23 | bus_LV_191-19_0_6_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_191-19_0_6_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_191-19_0_6_node_104 | 0.4 | n |  | TRUE
26 | bus_LV_191-19_0_6_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_191-19_0_6_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_191-19_0_6_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_191-19_0_6_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_191-19_0_6_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_191-19_0_6_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_191-19_0_6_node_106 | 0.4 | n |  | TRUE
33 | bus_LV_191-19_0_6_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_191-19_0_6_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_191-19_0_6_node_123 | 0.4 | n |  | TRUE
36 | bus_LV_191-19_0_6_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_191-19_0_6_node_122 | 0.4 | n |  | TRUE
38 | bus_LV_191-19_0_6_node_127 | 0.4 | n |  | TRUE
39 | bus_LV_191-19_0_6_node_105 | 0.4 | n |  | TRUE
40 | bus_LV_191-19_0_6_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_191-19_0_6_node_62 | 0.4 | n |  | TRUE
42 | bus_LV_191-19_0_6_node_124 | 0.4 | n |  | TRUE
43 | bus_LV_191-19_0_6_node_97 | 0.4 | n |  | TRUE
44 | bus_LV_191-19_0_6_node_96 | 0.4 | n |  | TRUE
45 | bus_LV_191-19_0_6_node_99 | 0.4 | n |  | TRUE
46 | bus_LV_191-19_0_6_node_109 | 0.4 | n |  | TRUE
47 | bus_LV_191-19_0_6_node_132 | 0.4 | n |  | TRUE
48 | bus_LV_191-19_0_6_node_100 | 0.4 | n |  | TRUE
49 | bus_LV_191-19_0_6_node_133 | 0.4 | n |  | TRUE
50 | bus_LV_191-19_0_6_node_113 | 0.4 | n |  | TRUE
51 | bus_LV_191-19_0_6_node_66 | 0.4 | n |  | TRUE
52 | bus_LV_191-19_0_6_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_191-19_0_6_node_65 | 0.4 | n |  | TRUE
54 | bus_LV_191-19_0_6_node_63 | 0.4 | n |  | TRUE
55 | bus_LV_191-19_0_6_node_94 | 0.4 | n |  | TRUE
56 | bus_LV_191-19_0_6_node_95 | 0.4 | n |  | TRUE
57 | bus_LV_191-19_0_6_node_93 | 0.4 | n |  | TRUE
58 | bus_LV_191-19_0_6_node_108 | 0.4 | n |  | TRUE
59 | bus_LV_191-19_0_6_node_107 | 0.4 | n |  | TRUE
60 | bus_LV_191-19_0_6_node_14 | 0.4 | n |  | TRUE
61 | bus_LV_191-19_0_6_node_16 | 0.4 | n |  | TRUE
62 | bus_LV_191-19_0_6_node_15 | 0.4 | n |  | TRUE
63 | bus_LV_191-19_0_6_node_17 | 0.4 | n |  | TRUE
64 | bus_LV_191-19_0_6_node_18 | 0.4 | n |  | TRUE
65 | bus_LV_191-19_0_6_node_19 | 0.4 | n |  | TRUE
66 | bus_LV_191-19_0_6_node_90 | 0.4 | n |  | TRUE
67 | bus_LV_191-19_0_6_node_85 | 0.4 | n |  | TRUE
68 | bus_LV_191-19_0_6_node_20 | 0.4 | n |  | TRUE
69 | bus_LV_191-19_0_6_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_191-19_0_6_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_191-19_0_6_node_22 | 0.4 | n |  | TRUE
72 | bus_LV_191-19_0_6_node_92 | 0.4 | n |  | TRUE
73 | bus_LV_191-19_0_6_node_71 | 0.4 | n |  | TRUE
74 | bus_LV_191-19_0_6_node_28 | 0.4 | n |  | TRUE
75 | bus_LV_191-19_0_6_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_191-19_0_6_node_42 | 0.4 | n |  | TRUE
77 | bus_LV_191-19_0_6_node_89 | 0.4 | n |  | TRUE
78 | bus_LV_191-19_0_6_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_191-19_0_6_node_46 | 0.4 | n |  | TRUE
80 | bus_LV_191-19_0_6_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_191-19_0_6_node_33 | 0.4 | n |  | TRUE
82 | bus_LV_191-19_0_6_node_34 | 0.4 | n |  | TRUE
83 | bus_LV_191-19_0_6_node_68 | 0.4 | n |  | TRUE
84 | bus_LV_191-19_0_6_node_29 | 0.4 | n |  | TRUE
85 | bus_LV_191-19_0_6_node_129 | 0.4 | n |  | TRUE
86 | bus_LV_191-19_0_6_node_37 | 0.4 | n |  | TRUE
87 | bus_LV_191-19_0_6_node_30 | 0.4 | n |  | TRUE
88 | bus_LV_191-19_0_6_node_47 | 0.4 | n |  | TRUE
89 | bus_LV_191-19_0_6_node_48 | 0.4 | n |  | TRUE
90 | bus_LV_191-19_0_6_node_36 | 0.4 | n |  | TRUE
91 | bus_LV_191-19_0_6_node_35 | 0.4 | n |  | TRUE
92 | bus_LV_191-19_0_6_node_50 | 0.4 | n |  | TRUE
93 | bus_LV_191-19_0_6_node_116 | 0.4 | n |  | TRUE
94 | bus_LV_191-19_0_6_node_49 | 0.4 | n |  | TRUE
95 | bus_LV_191-19_0_6_node_118 | 0.4 | n |  | TRUE
96 | bus_LV_191-19_0_6_node_120 | 0.4 | n |  | TRUE
97 | bus_LV_191-19_0_6_node_121 | 0.4 | n |  | TRUE
98 | bus_LV_191-19_0_6_node_45 | 0.4 | n |  | TRUE
99 | bus_LV_191-19_0_6_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_191-19_0_6_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_191-19_0_6_node_117 | 0.4 | n |  | TRUE
102 | bus_LV_191-19_0_6_node_53 | 0.4 | n |  | TRUE
103 | bus_LV_191-19_0_6_node_54 | 0.4 | n |  | TRUE
104 | bus_LV_191-19_0_6_node_55 | 0.4 | n |  | TRUE
105 | bus_LV_191-19_0_6_node_56 | 0.4 | n |  | TRUE
106 | bus_LV_191-19_0_6_node_83 | 0.4 | n |  | TRUE
107 | bus_LV_191-19_0_6_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_191-19_0_6_node_138 | 0.4 | n |  | TRUE
109 | bus_LV_191-19_0_6_node_137 | 0.4 | n |  | TRUE
110 | bus_LV_191-19_0_6_node_81 | 0.4 | n |  | TRUE
111 | bus_LV_191-19_0_6_node_57 | 0.4 | n |  | TRUE
112 | bus_LV_191-19_0_6_node_59 | 0.4 | n |  | TRUE
113 | bus_LV_191-19_0_6_node_61 | 0.4 | n |  | TRUE
114 | bus_LV_191-19_0_6_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_191-19_0_6_node_135 | 0.4 | n |  | TRUE
116 | bus_LV_191-19_0_6_node_136 | 0.4 | n |  | TRUE
117 | bus_LV_191-19_0_6_node_82 | 0.4 | n |  | TRUE
118 | bus_LV_191-19_0_6_node_67 | 0.4 | n |  | TRUE
119 | bus_LV_191-19_0_6_node_69 | 0.4 | n |  | TRUE
120 | bus_LV_191-19_0_6_node_72 | 0.4 | n |  | TRUE
121 | bus_LV_191-19_0_6_node_73 | 0.4 | n |  | TRUE
122 | bus_LV_191-19_0_6_node_101 | 0.4 | n |  | TRUE
123 | bus_LV_191-19_0_6_node_86 | 0.4 | n |  | TRUE
124 | bus_LV_191-19_0_6_node_87 | 0.4 | n |  | TRUE
125 | bus_LV_191-19_0_6_node_111 | 0.4 | n |  | TRUE
126 | bus_LV_191-19_0_6_node_134 | 0.4 | n |  | TRUE
127 | bus_LV_191-19_0_6_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_191-19_0_6_node_112 | 0.4 | n |  | TRUE
129 | bus_LV_191-19_0_6_node_131 | 0.4 | n |  | TRUE
130 | bus_LV_191-19_0_6_node_119 | 0.4 | n |  | TRUE
131 | bus_MV_499_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_191-19_0_6_load_0 | 0 | 0.010367 | 0.0025983 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_191-19_0_6_load_13 | 2 | 0.002458 | 0.00061603 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_191-19_0_6_load_74 | 7 | 0.0094105 | 0.0023585 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_191-19_0_6_load_64 | 10 | 0.0041688 | 0.0010448 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_191-19_0_6_load_128 | 11 | 0.0052265 | 0.0013099 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_191-19_0_6_load_125 | 12 | 0.0059705 | 0.0014964 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_191-19_0_6_load_130 | 14 | 0.0088953 | 0.0022294 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_191-19_0_6_load_115 | 18 | 0.020683 | 0.0051837 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_191-19_0_6_load_126 | 19 | 0.0058981 | 0.0014782 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_191-19_0_6_load_76 | 20 | 0.0048869 | 0.0012248 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_191-19_0_6_load_88 | 21 | 0.004812 | 0.001206 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_191-19_0_6_load_104 | 25 | 0.0043557 | 0.0010916 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_191-19_0_6_load_51 | 27 | 0.010118 | 0.0025359 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_191-19_0_6_load_31 | 28 | 0.0019718 | 0.00049419 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_191-19_0_6_load_52 | 30 | 0.0030265 | 0.00075852 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_191-19_0_6_load_106 | 32 | 0.0012931 | 0.00032409 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_191-19_0_6_load_123 | 35 | 0.0012761 | 0.00031983 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_191-19_0_6_load_122 | 37 | 0.0075182 | 0.0018842 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_191-19_0_6_load_127 | 38 | 0.0020429 | 0.000512 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_191-19_0_6_load_105 | 39 | 0.0041793 | 0.0010474 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_191-19_0_6_load_62 | 41 | 0.0042787 | 0.0010724 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_191-19_0_6_load_124 | 42 | 0.0035233 | 0.00088301 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_191-19_0_6_load_109 | 46 | 0.016878 | 0.00423 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_191-19_0_6_load_132 | 47 | 0.013115 | 0.0032869 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_191-19_0_6_load_133 | 49 | 0.013027 | 0.0032648 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_191-19_0_6_load_58 | 52 | 0.0027241 | 0.00068273 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_191-19_0_6_load_65 | 53 | 0.0013681 | 0.00034287 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_191-19_0_6_load_63 | 54 | 0.015152 | 0.0037974 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_191-19_0_6_load_95 | 56 | 0.0018943 | 0.00047475 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_191-19_0_6_load_93 | 57 | 0.0040363 | 0.0010116 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_191-19_0_6_load_108 | 58 | 0.0025351 | 0.00063536 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_191-19_0_6_load_107 | 59 | 0.0031098 | 0.00077938 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_191-19_0_6_load_14 | 60 | 0.0091185 | 0.0022853 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_191-19_0_6_load_17 | 63 | 0.0054734 | 0.0013718 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_191-19_0_6_load_90 | 66 | 0.0014465 | 0.00036253 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_191-19_0_6_load_85 | 67 | 0.0014874 | 0.00037278 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_191-19_0_6_load_78 | 70 | 0.0044588 | 0.0011175 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_191-19_0_6_load_92 | 72 | 0.0049927 | 0.0012513 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_191-19_0_6_load_71 | 73 | 0.0028091 | 0.00070402 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_191-19_0_6_load_44 | 75 | 0.0055109 | 0.0013812 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_191-19_0_6_load_42 | 76 | 0.0030537 | 0.00076532 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_191-19_0_6_load_89 | 77 | 0.0035104 | 0.00087978 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_191-19_0_6_load_70 | 78 | 0.002768 | 0.00069373 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_191-19_0_6_load_46 | 79 | 0.0088589 | 0.0022203 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_191-19_0_6_load_79 | 80 | 0.0021433 | 0.00053717 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_191-19_0_6_load_33 | 81 | 0.001539 | 0.00038572 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_191-19_0_6_load_29 | 84 | 0.0031529 | 0.00079019 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_191-19_0_6_load_129 | 85 | 0.0039084 | 0.00097954 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_191-19_0_6_load_30 | 87 | 0.0019699 | 0.00049371 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_191-19_0_6_load_48 | 89 | 0.0058437 | 0.0014646 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_191-19_0_6_load_36 | 90 | 0.0025038 | 0.00062751 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_191-19_0_6_load_35 | 91 | 0.0029502 | 0.00073938 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_191-19_0_6_load_116 | 93 | 0.0084205 | 0.0021104 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_191-19_0_6_load_120 | 96 | 0.0014732 | 0.00036922 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_191-19_0_6_load_121 | 97 | 0.0029218 | 0.00073228 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_191-19_0_6_load_45 | 98 | 0.0049907 | 0.0012508 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_191-19_0_6_load_77 | 99 | 0.0046373 | 0.0011622 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_191-19_0_6_load_91 | 100 | 0.0045842 | 0.0011489 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_191-19_0_6_load_53 | 102 | 0.0023455 | 0.00058784 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_191-19_0_6_load_54 | 103 | 0.0036899 | 0.00092478 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_191-19_0_6_load_55 | 104 | 0.0017692 | 0.00044341 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_191-19_0_6_load_80 | 107 | 0.0010331 | 0.00025893 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_191-19_0_6_load_138 | 108 | 0.0039381 | 0.00098697 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_191-19_0_6_load_137 | 109 | 0.0055349 | 0.0013872 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_191-19_0_6_load_57 | 111 | 0.0012763 | 0.00031987 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_191-19_0_6_load_61 | 113 | 0.0013048 | 0.000327 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_191-19_0_6_load_103 | 114 | 0.0020852 | 0.0005226 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_191-19_0_6_load_135 | 115 | 0.0041092 | 0.0010299 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_191-19_0_6_load_136 | 116 | 0.0027828 | 0.00069743 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_191-19_0_6_load_82 | 117 | 0.0012315 | 0.00030864 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_191-19_0_6_load_67 | 118 | 0.0042191 | 0.0010574 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_191-19_0_6_load_72 | 120 | 0.0028876 | 0.0007237 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_191-19_0_6_load_73 | 121 | 0.0026987 | 0.00067636 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_191-19_0_6_load_101 | 122 | 0.0015786 | 0.00039563 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_191-19_0_6_load_86 | 123 | 0.0026723 | 0.00066974 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_191-19_0_6_load_87 | 124 | 0.0037171 | 0.0009316 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_191-19_0_6_load_134 | 126 | 0.01295 | 0.0032456 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_191-19_0_6_load_112 | 128 | 0.0064963 | 0.0016281 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_191-19_0_6_load_131 | 129 | 0.0062046 | 0.001555 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_191-19_0_6_load_119 | 130 | 0.0033954 | 0.00085096 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_191-19_0_6_line_0 |  | 0 | 1 | 0.047332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_191-19_0_6_line_1 |  | 1 | 2 | 0.022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_191-19_0_6_line_2 |  | 2 | 3 | 0.011633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_191-19_0_6_line_3 |  | 3 | 4 | 0.036164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_191-19_0_6_line_4 |  | 4 | 19 | 0.023879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_191-19_0_6_line_5 |  | 5 | 6 | 0.028934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_191-19_0_6_line_6 |  | 5 | 7 | 0.018765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_191-19_0_6_line_7 |  | 6 | 11 | 0.012227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_191-19_0_6_line_8 |  | 6 | 12 | 0.0062988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_191-19_0_6_line_9 |  | 7 | 22 | 0.011468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_191-19_0_6_line_10 |  | 8 | 9 | 0.021468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_191-19_0_6_line_11 |  | 8 | 10 | 0.017342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_191-19_0_6_line_12 |  | 9 | 18 | 0.027192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_191-19_0_6_line_13 |  | 9 | 16 | 0.031042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_191-19_0_6_line_14 |  | 10 | 41 | 0.024028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_191-19_0_6_line_15 |  | 12 | 42 | 0.023685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_191-19_0_6_line_16 |  | 13 | 14 | 0.025737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_191-19_0_6_line_17 |  | 13 | 15 | 0.040046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_191-19_0_6_line_18 |  | 15 | 45 | 0.036243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_191-19_0_6_line_19 |  | 15 | 46 | 0.017676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_191-19_0_6_line_20 |  | 16 | 17 | 0.030991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_191-19_0_6_line_21 |  | 17 | 51 | 0.018021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_191-19_0_6_line_22 |  | 17 | 52 | 0.0037031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_191-19_0_6_line_23 |  | 18 | 43 | 0.035383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_191-19_0_6_line_24 |  | 19 | 33 | 0.022961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_191-19_0_6_line_25 |  | 20 | 21 | 0.012882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_191-19_0_6_line_26 |  | 20 | 22 | 0.026553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_191-19_0_6_line_27 |  | 21 | 123 | 0.0131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_191-19_0_6_line_28 |  | 22 | 99 | 0.02162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_191-19_0_6_line_29 |  | 23 | 24 | 0.00379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_191-19_0_6_line_30 |  | 23 | 25 | 0.0268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_191-19_0_6_line_31 |  | 24 | 28 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_191-19_0_6_line_32 |  | 24 | 26 | 0.045094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_191-19_0_6_line_33 |  | 26 | 27 | 0.0059219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_191-19_0_6_line_34 |  | 27 | 29 | 0.023578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_191-19_0_6_line_35 |  | 28 | 84 | 0.01862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_191-19_0_6_line_36 |  | 29 | 30 | 0.032163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_191-19_0_6_line_37 |  | 31 | 32 | 0.01183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_191-19_0_6_line_38 |  | 31 | 33 | 0.0043605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_191-19_0_6_line_39 |  | 32 | 85 | 0.012491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_191-19_0_6_line_40 |  | 33 | 38 | 0.017828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_191-19_0_6_line_41 |  | 34 | 35 | 0.014327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_191-19_0_6_line_42 |  | 34 | 36 | 0.010673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_191-19_0_6_line_43 |  | 34 | 37 | 0.016882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_191-19_0_6_line_44 |  | 35 | 38 | 0.0072826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_191-19_0_6_line_45 |  | 36 | 39 | 0.016062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_191-19_0_6_line_46 |  | 36 | 40 | 0.00481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_191-19_0_6_line_47 |  | 37 | 97 | 0.015318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_191-19_0_6_line_48 |  | 40 | 88 | 0.019497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_191-19_0_6_line_49 |  | 40 | 87 | 0.0072054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_191-19_0_6_line_50 |  | 41 | 54 | 0.021837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_191-19_0_6_line_51 |  | 42 | 95 | 0.010237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_191-19_0_6_line_52 |  | 43 | 44 | 0.026364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_191-19_0_6_line_53 |  | 44 | 58 | 0.015448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_191-19_0_6_line_54 |  | 44 | 59 | 0.044934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_191-19_0_6_line_55 |  | 44 | 55 | 0.023742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_191-19_0_6_line_56 |  | 45 | 47 | 0.019512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_191-19_0_6_line_57 |  | 45 | 48 | 0.055861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_191-19_0_6_line_58 |  | 48 | 49 | 0.012573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_191-19_0_6_line_59 |  | 48 | 50 | 0.012946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_191-19_0_6_line_60 |  | 50 | 126 | 0.00722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_191-19_0_6_line_61 |  | 50 | 127 | 0.035772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_191-19_0_6_line_62 |  | 51 | 115 | 0.003388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_191-19_0_6_line_63 |  | 51 | 116 | 0.020504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_191-19_0_6_line_64 |  | 52 | 111 | 0.014931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_191-19_0_6_line_65 |  | 53 | 54 | 0.009656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_191-19_0_6_line_66 |  | 55 | 56 | 0.02723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_191-19_0_6_line_67 |  | 55 | 57 | 0.043792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_191-19_0_6_line_68 |  | 58 | 125 | 0.028737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_191-19_0_6_line_69 |  | 60 | 61 | 0.021815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_191-19_0_6_line_70 |  | 61 | 65 | 0.037291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_191-19_0_6_line_71 |  | 62 | 63 | 0.018423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_191-19_0_6_line_72 |  | 62 | 64 | 0.024428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_191-19_0_6_line_73 |  | 63 | 65 | 0.022357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_191-19_0_6_line_74 |  | 64 | 66 | 0.0169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_191-19_0_6_line_75 |  | 64 | 67 | 0.011335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_191-19_0_6_line_76 |  | 66 | 77 | 0.0040144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_191-19_0_6_line_77 |  | 67 | 78 | 0.025092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_191-19_0_6_line_78 |  | 68 | 69 | 0.032123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_191-19_0_6_line_79 |  | 68 | 70 | 0.023435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_191-19_0_6_line_80 |  | 69 | 79 | 0.027473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_191-19_0_6_line_81 |  | 69 | 76 | 0.016989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_191-19_0_6_line_82 |  | 70 | 80 | 0.013791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_191-19_0_6_line_83 |  | 71 | 72 | 0.01705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_191-19_0_6_line_84 |  | 71 | 73 | 0.050066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_191-19_0_6_line_85 |  | 73 | 83 | 0.011112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_191-19_0_6_line_86 |  | 74 | 75 | 0.03017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_191-19_0_6_line_87 |  | 74 | 76 | 0.028395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_191-19_0_6_line_88 |  | 75 | 86 | 0.027641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_191-19_0_6_line_89 |  | 77 | 124 | 0.027811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_191-19_0_6_line_90 |  | 78 | 83 | 0.018446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_191-19_0_6_line_91 |  | 79 | 100 | 0.014439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_191-19_0_6_line_92 |  | 81 | 82 | 0.013791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_191-19_0_6_line_93 |  | 82 | 91 | 0.053371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_191-19_0_6_line_94 |  | 82 | 90 | 0.014323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_191-19_0_6_line_95 |  | 82 | 86 | 0.004192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_191-19_0_6_line_96 |  | 83 | 118 | 0.032624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_191-19_0_6_line_97 |  | 84 | 87 | 0.024872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_191-19_0_6_line_98 |  | 86 | 92 | 0.018729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_191-19_0_6_line_99 |  | 88 | 89 | 0.010777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_191-19_0_6_line_100 |  | 88 | 90 | 0.037785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_191-19_0_6_line_101 |  | 92 | 93 | 0.026176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_191-19_0_6_line_102 |  | 93 | 101 | 0.010292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_191-19_0_6_line_103 |  | 94 | 95 | 0.016264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_191-19_0_6_line_104 |  | 94 | 96 | 0.020822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_191-19_0_6_line_105 |  | 95 | 101 | 0.008306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_191-19_0_6_line_106 |  | 97 | 130 | 0.024466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_191-19_0_6_line_107 |  | 98 | 99 | 0.016809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_191-19_0_6_line_108 |  | 102 | 103 | 0.021204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_191-19_0_6_line_109 |  | 102 | 104 | 0.0084993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_191-19_0_6_line_110 |  | 103 | 105 | 0.016222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_191-19_0_6_line_111 |  | 105 | 106 | 0.020503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_191-19_0_6_line_112 |  | 105 | 107 | 0.01423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_191-19_0_6_line_113 |  | 106 | 108 | 0.00261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_191-19_0_6_line_114 |  | 106 | 109 | 0.034763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_191-19_0_6_line_115 |  | 107 | 110 | 0.015409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_191-19_0_6_line_116 |  | 110 | 117 | 0.0057953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_191-19_0_6_line_117 |  | 110 | 120 | 0.017821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_191-19_0_6_line_118 |  | 111 | 112 | 0.014069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_191-19_0_6_line_119 |  | 112 | 113 | 0.0044044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_191-19_0_6_line_120 |  | 113 | 114 | 0.011712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_191-19_0_6_line_121 |  | 114 | 117 | 0.0083698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_191-19_0_6_line_122 |  | 118 | 119 | 0.0085019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_191-19_0_6_line_123 |  | 119 | 120 | 0.020938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_191-19_0_6_line_124 |  | 119 | 121 | 0.014735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_191-19_0_6_line_125 |  | 121 | 122 | 0.0029304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_191-19_0_6_line_126 |  | 123 | 124 | 0.019234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_191-19_0_6_line_127 |  | 125 | 128 | 0.014413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_191-19_0_6_line_128 |  | 125 | 127 | 0.037126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
129 | LV_191-19_0_6_line_129 |  | 127 | 129 | 0.006612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_191-19_0_6_trafo_88 | 0.63 MVA 20/0.4 kV | 131 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2689455.2858 | 1249962.3489 | 2689462.2479 | 1249915.5321
1 | 2689455.2858 | 1249962.3489 | 2689453.0109 | 1249976.9923 | 2689447.9481 | 1249982.0855
2 | 2689438.5987 | 1249988.8728 | 2689445.0832 | 1249984.9676 | 2689447.9481 | 1249982.0855
3 | 2689438.5987 | 1249988.8728 | 2689435.2154 | 1249990.9122 | 2689440.3205 | 1250002.8538 | 2689443.7315 | 1250012.4792 | 2689446.0993 | 1250021.1771
4 | 2689446.0993 | 1250021.1771 | 2689432.7045 | 1250025.1892 | 2689425.6526 | 1250027.6735 | 2689423.3465 | 1250028.4053
5 | 2689388.9173 | 1249899.2221 | 2689386.4656 | 1249908.5811 | 2689387.8056 | 1249914.8505 | 2689384.9729 | 1249918.4327 | 2689381.1322 | 1249925.7693
6 | 2689388.9173 | 1249899.2221 | 2689372.5303 | 1249890.0785
7 | 2689370.6804 | 1249919.3735 | 2689381.1322 | 1249925.7693
8 | 2689381.1322 | 1249925.7693 | 2689378.2115 | 1249931.35
9 | 2689362.5159 | 1249884.4906 | 2689372.5303 | 1249890.0785
10 | 2689399.1804 | 1249807.5518 | 2689399.4505 | 1249794.6572 | 2689399.5472 | 1249790.2553 | 2689403.7138 | 1249790.3516
11 | 2689399.1804 | 1249807.5518 | 2689381.8383 | 1249807.5785
12 | 2689403.7138 | 1249790.3516 | 2689403.9798 | 1249763.1612
13 | 2689403.7138 | 1249790.3516 | 2689399.5472 | 1249790.2553 | 2689400.2245 | 1249763.3896
14 | 2689359.3068 | 1249804.2149 | 2689362.4072 | 1249807.6085 | 2689381.8383 | 1249807.5785
15 | 2689367.2261 | 1249952.3331 | 2689371.1493 | 1249944.8443 | 2689378.2115 | 1249931.35
16 | 2689451.802 | 1249833.5431 | 2689425.9929 | 1249833.0867
17 | 2689451.802 | 1249833.5431 | 2689468.0055 | 1249809.0802 | 2689474.223 | 1249800.3674
18 | 2689474.223 | 1249800.3674 | 2689494.4052 | 1249772.9513 | 2689492.5814 | 1249771.7228
19 | 2689474.223 | 1249800.3674 | 2689470.8961 | 1249797.6707 | 2689471.8845 | 1249784.314
20 | 2689377.1153 | 1249743.1036 | 2689387.074 | 1249754.6736 | 2689400.2245 | 1249763.3896
21 | 2689377.1153 | 1249743.1036 | 2689363.8228 | 1249755.3124
22 | 2689377.1153 | 1249743.1036 | 2689374.6077 | 1249740.3788
23 | 2689404.3259 | 1249727.7801 | 2689403.9798 | 1249763.1612
24 | 2689402.4977 | 1250037.0091 | 2689405.2136 | 1250034.1591 | 2689423.3465 | 1250028.4053
25 | 2689374.0669 | 1249860.5689 | 2689371.0884 | 1249858.3 | 2689364.9492 | 1249851.5318
26 | 2689362.5159 | 1249884.4906 | 2689374.0669 | 1249860.5689
27 | 2689356.1478 | 1249841.8285 | 2689364.9492 | 1249851.5318
28 | 2689362.5159 | 1249884.4906 | 2689356.232 | 1249891.6124 | 2689350.3109 | 1249888.6987 | 2689344.8581 | 1249889.5795
29 | 2689339.4767 | 1250088.3757 | 2689335.9021 | 1250087.0876
30 | 2689339.4767 | 1250088.3757 | 2689351.1467 | 1250064.2502
31 | 2689335.9021 | 1250087.0876 | 2689343.805 | 1250070.6064
32 | 2689304.6989 | 1250101.9286 | 2689315.0613 | 1250108.2229 | 2689320.3932 | 1250108.6369 | 2689325.0355 | 1250106.7165 | 2689328.044 | 1250103.4816 | 2689335.9021 | 1250087.0876
33 | 2689304.6989 | 1250101.9286 | 2689299.6374 | 1250098.8545
34 | 2689279.4848 | 1250086.615 | 2689299.6374 | 1250098.8545
35 | 2689343.805 | 1250070.6064 | 2689351.8559 | 1250053.8168
36 | 2689279.4848 | 1250086.615 | 2689297.9729 | 1250060.2624
37 | 2689399.8335 | 1250040.4382 | 2689405.7355 | 1250045.6089 | 2689408.358 | 1250048.6077
38 | 2689399.8335 | 1250040.4382 | 2689401.1321 | 1250038.4452 | 2689402.4977 | 1250037.0091
39 | 2689414.8239 | 1250059.1642 | 2689411.5398 | 1250052.246 | 2689408.358 | 1250048.6077
40 | 2689402.4977 | 1250037.0091 | 2689387.6627 | 1250027.1214
41 | 2689368.9038 | 1250016.6093 | 2689376.4836 | 1250019.6704 | 2689381.6027 | 1250023.0823
42 | 2689368.9038 | 1250016.6093 | 2689372.4277 | 1250020.2541 | 2689369.9883 | 1250025.2989
43 | 2689368.9038 | 1250016.6093 | 2689373.9338 | 1250015.0173 | 2689382.0585 | 1250006.729
44 | 2689387.6627 | 1250027.1214 | 2689381.6027 | 1250023.0823
45 | 2689369.9883 | 1250025.2989 | 2689374.4946 | 1250026.8903 | 2689379.1447 | 1250026.9605 | 2689384.7022 | 1250030.581
46 | 2689369.9883 | 1250025.2989 | 2689365.2029 | 1250024.693
47 | 2689382.0585 | 1250006.729 | 2689386.748 | 1250001.945 | 2689389.5461 | 1250000.1525 | 2689394.8311 | 1249999.8133
48 | 2689365.2029 | 1250024.693 | 2689365.426 | 1250023.918 | 2689364.6667 | 1250020.1926 | 2689361.1869 | 1250015.6256 | 2689354.8844 | 1250008.97
49 | 2689365.2029 | 1250024.693 | 2689364.2551 | 1250027.959 | 2689362.6101 | 1250031.3896
50 | 2689359.3068 | 1249804.2149 | 2689357.9057 | 1249802.6814 | 2689352.4236 | 1249796.6942 | 2689352.5291 | 1249785.0532
51 | 2689362.4806 | 1249961.404 | 2689366.3291 | 1249954.0453 | 2689367.2261 | 1249952.3331
52 | 2689403.3493 | 1249701.4343 | 2689403.4707 | 1249704.8943 | 2689403.8341 | 1249715.341 | 2689404.3259 | 1249727.7801
53 | 2689403.3493 | 1249701.4343 | 2689418.7141 | 1249699.8352
54 | 2689403.3493 | 1249701.4343 | 2689397.6992 | 1249656.8574
55 | 2689403.3493 | 1249701.4343 | 2689399.288 | 1249701.8622 | 2689396.2814 | 1249682.4355
56 | 2689492.0077 | 1249752.2216 | 2689492.4305 | 1249766.7168 | 2689492.5814 | 1249771.7228
57 | 2689470.7972 | 1249727.7273 | 2689471.63 | 1249752.581 | 2689470.8666 | 1249757.6288 | 2689490.1811 | 1249770.1632 | 2689492.5814 | 1249771.7228
58 | 2689470.7972 | 1249727.7273 | 2689458.1953 | 1249728.1931
59 | 2689470.177 | 1249714.7971 | 2689470.7972 | 1249727.7273
60 | 2689470.177 | 1249714.7971 | 2689477.3966 | 1249714.2389
61 | 2689468.5043 | 1249679.067 | 2689469.0139 | 1249694.3195 | 2689470.177 | 1249714.7971
62 | 2689363.8228 | 1249755.3124 | 2689361.5579 | 1249752.7875
63 | 2689347.2305 | 1249756.0184 | 2689351.9066 | 1249760.8815 | 2689358.6777 | 1249760.0162 | 2689363.8228 | 1249755.3124
64 | 2689364.4963 | 1249729.3922 | 2689374.6077 | 1249740.3788
65 | 2689352.5291 | 1249785.0532 | 2689352.6166 | 1249775.3976
66 | 2689396.2814 | 1249682.4355 | 2689375.973 | 1249664.2958
67 | 2689396.2814 | 1249682.4355 | 2689393.6222 | 1249662.0022 | 2689390.505 | 1249639.0261
68 | 2689447.2968 | 1249696.8604 | 2689418.7141 | 1249699.8352
69 | 2689235.2513 | 1249803.6345 | 2689250.9883 | 1249788.5267
70 | 2689261.3368 | 1249830.3586 | 2689235.2513 | 1249803.6345
71 | 2689290.8543 | 1249803.2048 | 2689289.3794 | 1249802.8712 | 2689277.3027 | 1249814.7088
72 | 2689290.8543 | 1249803.2048 | 2689297.3182 | 1249803.6803 | 2689308.4199 | 1249793.5287 | 2689310.4893 | 1249791.4917
73 | 2689261.3368 | 1249830.3586 | 2689277.3027 | 1249814.7088
74 | 2689310.4893 | 1249791.4917 | 2689321.8437 | 1249804.0094
75 | 2689310.4893 | 1249791.4917 | 2689303.3401 | 1249782.696
76 | 2689321.8437 | 1249804.0094 | 2689324.5407 | 1249806.9828
77 | 2689286.666 | 1249763.9486 | 2689301.7416 | 1249780.7295 | 2689303.3401 | 1249782.696
78 | 2689303.6308 | 1249902.8394 | 2689301.6658 | 1249898.9513 | 2689298.784 | 1249895.2717 | 2689290.6463 | 1249887.6323 | 2689286.9897 | 1249876.2463
79 | 2689286.9897 | 1249876.2463 | 2689292.9074 | 1249853.571
80 | 2689303.6308 | 1249902.8394 | 2689312.5317 | 1249891.9096 | 2689315.9946 | 1249878.9886
81 | 2689303.6308 | 1249902.8394 | 2689292.0584 | 1249915.277
82 | 2689296.3897 | 1249840.2273 | 2689292.9074 | 1249853.571
83 | 2689229.1102 | 1249709.0482 | 2689241.7805 | 1249697.6398
84 | 2689229.1102 | 1249709.0482 | 2689250.8412 | 1249729.6354 | 2689258.0023 | 1249735.9591 | 2689265.9694 | 1249742.9174
85 | 2689274.3388 | 1249750.227 | 2689265.9694 | 1249742.9174
86 | 2689272.7159 | 1249936.0656 | 2689296.3243 | 1249954.851
87 | 2689272.7159 | 1249936.0656 | 2689292.0584 | 1249915.277
88 | 2689317.9525 | 1249972.0632 | 2689310.1781 | 1249965.8747 | 2689296.3243 | 1249954.851
89 | 2689343.2254 | 1249827.5821 | 2689324.5407 | 1249806.9828
90 | 2689274.3388 | 1249750.227 | 2689286.666 | 1249763.9486
91 | 2689319.7324 | 1249865.0422 | 2689315.9946 | 1249878.9886
92 | 2689315.2315 | 1249975.2579 | 2689304.4655 | 1249966.6389
93 | 2689306.7975 | 1250013.8157 | 2689292.6836 | 1250002.4277 | 2689315.2315 | 1249975.2579
94 | 2689315.2315 | 1249975.2579 | 2689326.3419 | 1249984.2971
95 | 2689317.9525 | 1249972.0632 | 2689315.2315 | 1249975.2579
96 | 2689274.3388 | 1249750.227 | 2689274.6602 | 1249749.9427 | 2689298.7211 | 1249728.5515
97 | 2689351.8559 | 1250053.8168 | 2689362.6101 | 1250031.3896
98 | 2689317.9525 | 1249972.0632 | 2689332.9901 | 1249983.2872
99 | 2689354.8844 | 1250008.97 | 2689348.1778 | 1250017.406
100 | 2689354.8844 | 1250008.97 | 2689348.9314 | 1250002.6755 | 2689326.3419 | 1249984.2971
101 | 2689332.9901 | 1249983.2872 | 2689349.4329 | 1249962.9195
102 | 2689356.3052 | 1249955.8289 | 2689351.9289 | 1249962.1344 | 2689349.4329 | 1249962.9195
103 | 2689354.939 | 1249975.8234 | 2689362.4806 | 1249961.404
104 | 2689354.939 | 1249975.8234 | 2689364.9612 | 1249981.1563 | 2689372.8476 | 1249975.9157
105 | 2689356.3052 | 1249955.8289 | 2689362.4806 | 1249961.404
106 | 2689407.425 | 1249986.2905 | 2689410.2303 | 1249993.4372 | 2689396.8394 | 1249999.6844 | 2689394.8311 | 1249999.8133
107 | 2689338.7013 | 1249903.6778 | 2689342.1892 | 1249890.0107 | 2689344.8581 | 1249889.5795
108 | 2689338.8775 | 1249647.7327 | 2689324.666 | 1249663.4696
109 | 2689334.981 | 1249641.9919 | 2689340.0564 | 1249646.4273 | 2689338.8775 | 1249647.7327
110 | 2689313.7935 | 1249675.5092 | 2689324.666 | 1249663.4696
111 | 2689313.7935 | 1249675.5092 | 2689312.9612 | 1249674.6182 | 2689310.6501 | 1249672.1481 | 2689309.5279 | 1249670.9526 | 2689308.6566 | 1249670.1499 | 2689299.5 | 1249679.4857
112 | 2689313.7935 | 1249675.5092 | 2689323.5158 | 1249685.9006
113 | 2689297.5709 | 1249677.722 | 2689299.5 | 1249679.4857
114 | 2689278.9602 | 1249699.1023 | 2689281.8241 | 1249701.9698 | 2689292.5606 | 1249690.0114 | 2689290.9108 | 1249688.2519 | 2689299.5 | 1249679.4857
115 | 2689334.0435 | 1249697.1529 | 2689323.5158 | 1249685.9006
116 | 2689334.0435 | 1249697.1529 | 2689338.0483 | 1249701.3418
117 | 2689334.0435 | 1249697.1529 | 2689320.7241 | 1249708.9923
118 | 2689354.9692 | 1249719.0404 | 2689364.4963 | 1249729.3922
119 | 2689354.9692 | 1249719.0404 | 2689351.9255 | 1249715.8569
120 | 2689343.8322 | 1249707.3915 | 2689351.9255 | 1249715.8569
121 | 2689343.8322 | 1249707.3915 | 2689338.0483 | 1249701.3418
122 | 2689305.075 | 1249722.9026 | 2689298.7211 | 1249728.5515
123 | 2689305.075 | 1249722.9026 | 2689320.7241 | 1249708.9923
124 | 2689305.075 | 1249722.9026 | 2689315.1533 | 1249733.6524
125 | 2689317.1575 | 1249735.7902 | 2689315.1533 | 1249733.6524
126 | 2689356.1478 | 1249841.8285 | 2689343.2254 | 1249827.5821
127 | 2689447.2968 | 1249696.8604 | 2689446.7394 | 1249687.267 | 2689448.6484 | 1249682.8591
128 | 2689468.5043 | 1249679.067 | 2689469.0139 | 1249694.3195 | 2689447.2968 | 1249696.8604
129 | 2689475.1248 | 1249678.6777 | 2689468.5043 | 1249679.067

## bus_geodata
| x | y | coords
0 | 2689462.2479 | 1249915.5321
1 | 2689455.2858 | 1249962.3489
2 | 2689447.9481 | 1249982.0855
3 | 2689438.5987 | 1249988.8728
4 | 2689446.0993 | 1250021.1771
5 | 2689388.9173 | 1249899.2221
6 | 2689381.1322 | 1249925.7693
7 | 2689372.5303 | 1249890.0785
8 | 2689399.1804 | 1249807.5518
9 | 2689403.7138 | 1249790.3516
10 | 2689381.8383 | 1249807.5785
11 | 2689370.6804 | 1249919.3735
12 | 2689378.2115 | 1249931.35
13 | 2689451.802 | 1249833.5431
14 | 2689425.9929 | 1249833.0867
15 | 2689474.223 | 1249800.3674
16 | 2689400.2245 | 1249763.3896
17 | 2689377.1153 | 1249743.1036
18 | 2689403.9798 | 1249763.1612
19 | 2689423.3465 | 1250028.4053
20 | 2689374.0669 | 1249860.5689
21 | 2689364.9492 | 1249851.5318
22 | 2689362.5159 | 1249884.4906
23 | 2689339.4767 | 1250088.3757
24 | 2689335.9021 | 1250087.0876
25 | 2689351.1467 | 1250064.2502
26 | 2689304.6989 | 1250101.9286
27 | 2689299.6374 | 1250098.8545
28 | 2689343.805 | 1250070.6064
29 | 2689279.4848 | 1250086.615
30 | 2689297.9729 | 1250060.2624
31 | 2689399.8335 | 1250040.4382
32 | 2689408.358 | 1250048.6077
33 | 2689402.4977 | 1250037.0091
34 | 2689368.9038 | 1250016.6093
35 | 2689381.6027 | 1250023.0823
36 | 2689369.9883 | 1250025.2989
37 | 2689382.0585 | 1250006.729
38 | 2689387.6627 | 1250027.1214
39 | 2689384.7022 | 1250030.581
40 | 2689365.2029 | 1250024.693
41 | 2689359.3068 | 1249804.2149
42 | 2689367.2261 | 1249952.3331
43 | 2689404.3259 | 1249727.7801
44 | 2689403.3493 | 1249701.4343
45 | 2689492.5814 | 1249771.7228
46 | 2689471.8845 | 1249784.314
47 | 2689492.0077 | 1249752.2216
48 | 2689470.7972 | 1249727.7273
49 | 2689458.1953 | 1249728.1931
50 | 2689470.177 | 1249714.7971
51 | 2689363.8228 | 1249755.3124
52 | 2689374.6077 | 1249740.3788
53 | 2689352.6166 | 1249775.3976
54 | 2689352.5291 | 1249785.0532
55 | 2689396.2814 | 1249682.4355
56 | 2689375.973 | 1249664.2958
57 | 2689390.505 | 1249639.0261
58 | 2689418.7141 | 1249699.8352
59 | 2689397.6992 | 1249656.8574
60 | 2689250.9883 | 1249788.5267
61 | 2689235.2513 | 1249803.6345
62 | 2689290.8543 | 1249803.2048
63 | 2689277.3027 | 1249814.7088
64 | 2689310.4893 | 1249791.4917
65 | 2689261.3368 | 1249830.3586
66 | 2689321.8437 | 1249804.0094
67 | 2689303.3401 | 1249782.696
68 | 2689286.9897 | 1249876.2463
69 | 2689303.6308 | 1249902.8394
70 | 2689292.9074 | 1249853.571
71 | 2689229.1102 | 1249709.0482
72 | 2689241.7805 | 1249697.6398
73 | 2689265.9694 | 1249742.9174
74 | 2689272.7159 | 1249936.0656
75 | 2689296.3243 | 1249954.851
76 | 2689292.0584 | 1249915.277
77 | 2689324.5407 | 1249806.9828
78 | 2689286.666 | 1249763.9486
79 | 2689315.9946 | 1249878.9886
80 | 2689296.3897 | 1249840.2273
81 | 2689304.4655 | 1249966.6389
82 | 2689315.2315 | 1249975.2579
83 | 2689274.3388 | 1249750.227
84 | 2689351.8559 | 1250053.8168
85 | 2689414.8239 | 1250059.1642
86 | 2689317.9525 | 1249972.0632
87 | 2689362.6101 | 1250031.3896
88 | 2689354.8844 | 1250008.97
89 | 2689348.1778 | 1250017.406
90 | 2689326.3419 | 1249984.2971
91 | 2689306.7975 | 1250013.8157
92 | 2689332.9901 | 1249983.2872
93 | 2689349.4329 | 1249962.9196
94 | 2689354.939 | 1249975.8234
95 | 2689362.4806 | 1249961.404
96 | 2689372.8476 | 1249975.9157
97 | 2689394.8311 | 1249999.8133
98 | 2689338.7013 | 1249903.6778
99 | 2689344.8581 | 1249889.5795
100 | 2689319.7324 | 1249865.0422
101 | 2689356.3052 | 1249955.8289
102 | 2689338.8775 | 1249647.7327
103 | 2689324.666 | 1249663.4696
104 | 2689334.981 | 1249641.9919
105 | 2689313.7935 | 1249675.5092
106 | 2689299.5 | 1249679.4857
107 | 2689323.5158 | 1249685.9006
108 | 2689297.5709 | 1249677.722
109 | 2689278.9602 | 1249699.1023
110 | 2689334.0435 | 1249697.1529
111 | 2689364.4963 | 1249729.3922
112 | 2689354.9692 | 1249719.0404
113 | 2689351.9255 | 1249715.8569
114 | 2689343.8322 | 1249707.3915
115 | 2689361.5579 | 1249752.7875
116 | 2689347.2305 | 1249756.0184
117 | 2689338.0483 | 1249701.3418
118 | 2689298.7211 | 1249728.5515
119 | 2689305.075 | 1249722.9026
120 | 2689320.7241 | 1249708.9923
121 | 2689315.1533 | 1249733.6524
122 | 2689317.1575 | 1249735.7902
123 | 2689356.1478 | 1249841.8285
124 | 2689343.2254 | 1249827.5821
125 | 2689447.2968 | 1249696.8604
126 | 2689477.3966 | 1249714.2389
127 | 2689468.5043 | 1249679.067
128 | 2689448.6484 | 1249682.8591
129 | 2689475.1248 | 1249678.6777
130 | 2689407.425 | 1249986.2905
131 | 2689364.9492 | 1249851.5318

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97112 | -0.55714 | 0.010367 | 0.0025983
1 | 0.97158 | -0.54808 | 0 | 0
2 | 0.97179 | -0.54387 | 0.002458 | 0.00061603
3 | 0.97193 | -0.54111 | 0 | 0
4 | 0.97236 | -0.53256 | 0 | 0
5 | 0.99495 | -0.095349 | 0 | 0
6 | 0.99129 | -0.16486 | 0 | 0
7 | 0.99732 | -0.050539 | 0.0094105 | 0.0023585
8 | 0.98121 | -0.35997 | 0 | 0
9 | 0.98171 | -0.35027 | 0 | 0
10 | 0.98081 | -0.36782 | 0.0041688 | 0.0010448
11 | 0.99123 | -0.166 | 0.0052265 | 0.0013099
12 | 0.99053 | -0.17948 | 0.0059705 | 0.0014964
13 | 0.97074 | -0.56539 | 0 | 0
14 | 0.97053 | -0.56962 | 0.0088953 | 0.0022294
15 | 0.97107 | -0.5588 | 0 | 0
16 | 0.983 | -0.32508 | 0 | 0
17 | 0.9843 | -0.29999 | 0 | 0
18 | 0.98078 | -0.3683 | 0.020683 | 0.0051837
19 | 0.97265 | -0.52691 | 0.0058981 | 0.0014782
20 | 0.99936 | -0.011973 | 0.0048869 | 0.0012248
21 | 1 | 0 | -0.38623 | -0.098968
22 | 0.99809 | -0.035944 | 0 | 0
23 | 0.97326 | -0.51488 | 0 | 0
24 | 0.97327 | -0.51458 | 0 | 0
25 | 0.97315 | -0.51703 | 0.0043557 | 0.0010916
26 | 0.97272 | -0.52549 | 0 | 0
27 | 0.97265 | -0.52693 | 0.010118 | 0.0025359
28 | 0.97357 | -0.50869 | 0.0019718 | 0.00049419
29 | 0.97258 | -0.52824 | 0 | 0
30 | 0.97249 | -0.53004 | 0.0030265 | 0.00075852
31 | 0.97303 | -0.51941 | 0 | 0
32 | 0.97297 | -0.52054 | 0.0012931 | 0.00032409
33 | 0.97305 | -0.51899 | 0 | 0
34 | 0.97399 | -0.50049 | 0 | 0
35 | 0.97362 | -0.50766 | 0.0012761 | 0.00031983
36 | 0.97439 | -0.49243 | 0 | 0
37 | 0.97377 | -0.50478 | 0.0075182 | 0.0018842
38 | 0.97345 | -0.51114 | 0.0020429 | 0.000512
39 | 0.97433 | -0.49366 | 0.0041793 | 0.0010474
40 | 0.9746 | -0.48844 | 0 | 0
41 | 0.98035 | -0.37687 | 0.0042787 | 0.0010724
42 | 0.98778 | -0.23211 | 0.0035233 | 0.00088301
43 | 0.9798 | -0.38737 | 0 | 0
44 | 0.97907 | -0.40161 | 0 | 0
45 | 0.97195 | -0.54155 | 0 | 0
46 | 0.97079 | -0.56432 | 0.016878 | 0.00423
47 | 0.97171 | -0.54627 | 0.013115 | 0.0032869
48 | 0.97397 | -0.50155 | 0 | 0
49 | 0.97382 | -0.50456 | 0.013027 | 0.0032648
50 | 0.9746 | -0.48921 | 0 | 0
51 | 0.98418 | -0.30222 | 0 | 0
52 | 0.98446 | -0.29684 | 0.0027241 | 0.00068273
53 | 0.98 | -0.38366 | 0.0013681 | 0.00034287
54 | 0.98001 | -0.38342 | 0.015152 | 0.0037974
55 | 0.97894 | -0.40417 | 0 | 0
56 | 0.97889 | -0.40511 | 0.0018943 | 0.00047475
57 | 0.97878 | -0.40739 | 0.0040363 | 0.0010116
58 | 0.97869 | -0.40911 | 0.0025351 | 0.00063536
59 | 0.97894 | -0.40415 | 0.0031098 | 0.00077938
60 | 0.99344 | -0.12469 | 0.0091185 | 0.0022853
61 | 0.99362 | -0.12118 | 0 | 0
62 | 0.99436 | -0.10684 | 0 | 0
63 | 0.99412 | -0.11158 | 0.0054734 | 0.0013718
64 | 0.99469 | -0.10056 | 0 | 0
65 | 0.99393 | -0.11518 | 0 | 0
66 | 0.99577 | -0.080064 | 0.0014465 | 0.00036253
67 | 0.99402 | -0.11335 | 0.0014874 | 0.00037278
68 | 0.9774 | -0.43366 | 0 | 0
69 | 0.9776 | -0.42979 | 0 | 0
70 | 0.97725 | -0.43649 | 0.0044588 | 0.0011175
71 | 0.99116 | -0.16795 | 0 | 0
72 | 0.99108 | -0.16946 | 0.0049927 | 0.0012513
73 | 0.99139 | -0.16352 | 0.0028091 | 0.00070402
74 | 0.97852 | -0.41163 | 0 | 0
75 | 0.97917 | -0.39895 | 0.0055109 | 0.0013812
76 | 0.97791 | -0.42358 | 0.0030537 | 0.00076532
77 | 0.99602 | -0.075169 | 0.0035104 | 0.00087978
78 | 0.99254 | -0.14152 | 0.002768 | 0.00069373
79 | 0.97725 | -0.43653 | 0.0088589 | 0.0022203
80 | 0.97723 | -0.43703 | 0.0021433 | 0.00053717
81 | 0.97956 | -0.39127 | 0.001539 | 0.00038572
82 | 0.97958 | -0.39088 | 0 | 0
83 | 0.99147 | -0.16198 | 0 | 0
84 | 0.97391 | -0.50203 | 0.0031529 | 0.00079019
85 | 0.97292 | -0.52144 | 0.0039084 | 0.00097954
86 | 0.9799 | -0.38458 | 0 | 0
87 | 0.97443 | -0.49169 | 0.0019699 | 0.00049371
88 | 0.97587 | -0.46347 | 0 | 0
89 | 0.97581 | -0.46462 | 0.0058437 | 0.0014646
90 | 0.97853 | -0.41125 | 0.0025038 | 0.00062751
91 | 0.97943 | -0.39374 | 0.0029502 | 0.00073938
92 | 0.98184 | -0.34681 | 0 | 0
93 | 0.98455 | -0.29427 | 0.0084205 | 0.0021104
94 | 0.9866 | -0.25474 | 0 | 0
95 | 0.98662 | -0.25431 | 0 | 0
96 | 0.98657 | -0.25528 | 0.0014732 | 0.00036922
97 | 0.97368 | -0.50656 | 0.0029218 | 0.00073228
98 | 0.99783 | -0.041056 | 0.0049907 | 0.0012508
99 | 0.9979 | -0.039587 | 0.0046373 | 0.0011622
100 | 0.97719 | -0.43774 | 0.0045842 | 0.0011489
101 | 0.9857 | -0.27213 | 0 | 0
102 | 0.98647 | -0.25817 | 0.0023455 | 0.00058784
103 | 0.98655 | -0.25661 | 0.0036899 | 0.00092478
104 | 0.98645 | -0.25844 | 0.0017692 | 0.00044341
105 | 0.98667 | -0.25434 | 0 | 0
106 | 0.98649 | -0.25782 | 0 | 0
107 | 0.98689 | -0.24994 | 0.0010331 | 0.00025893
108 | 0.98648 | -0.258 | 0.0039381 | 0.00098697
109 | 0.98631 | -0.26126 | 0.0055349 | 0.0013872
110 | 0.98715 | -0.24489 | 0 | 0
111 | 0.98513 | -0.28392 | 0.0012763 | 0.00031987
112 | 0.98576 | -0.27165 | 0 | 0
113 | 0.98596 | -0.26782 | 0.0013048 | 0.000327
114 | 0.98649 | -0.25753 | 0.0020852 | 0.0005226
115 | 0.98417 | -0.30247 | 0.0041092 | 0.0010299
116 | 0.98413 | -0.30325 | 0.0027828 | 0.00069743
117 | 0.98688 | -0.25008 | 0.0012315 | 0.00030864
118 | 0.98965 | -0.19676 | 0.0042191 | 0.0010574
119 | 0.98919 | -0.20563 | 0 | 0
120 | 0.98808 | -0.22698 | 0.0028876 | 0.0007237
121 | 0.98913 | -0.20676 | 0.0026987 | 0.00067636
122 | 0.98913 | -0.20684 | 0.0015786 | 0.00039563
123 | 0.99912 | -0.016612 | 0.0026723 | 0.00066974
124 | 0.99784 | -0.040756 | 0.0037171 | 0.0009316
125 | 0.978 | -0.42264 | 0 | 0
126 | 0.97451 | -0.49092 | 0.01295 | 0.0032456
127 | 0.97676 | -0.44672 | 0 | 0
128 | 0.97791 | -0.42435 | 0.0064963 | 0.0016281
129 | 0.97673 | -0.44747 | 0.0062046 | 0.001555
130 | 0.9736 | -0.50809 | 0.0033954 | 0.00085096
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010367 | -0.0025983 | 0.010372 | 0.0026006 | 4.479e-06 | 2.2807e-06 | 0.015886 | 0.015885 | 0.015886 | 0.97112 | -0.55714 | 0.97158 | -0.54808 | 4.3642
1 | -0.010372 | -0.0026006 | 0.010374 | 0.0026016 | 2.0819e-06 | 1.0599e-06 | 0.015885 | 0.015885 | 0.015885 | 0.97158 | -0.54808 | 0.97179 | -0.54387 | 4.3641
2 | -0.012832 | -0.0032177 | 0.012834 | 0.0032186 | 1.6843e-06 | 9.3379e-07 | 0.019649 | 0.019649 | 0.019649 | 0.97179 | -0.54387 | 0.97193 | -0.54111 | 5.3981
3 | -0.012834 | -0.0032186 | 0.012839 | 0.0032215 | 5.2358e-06 | 2.9025e-06 | 0.019649 | 0.019649 | 0.019649 | 0.97193 | -0.54111 | 0.97236 | -0.53256 | 5.3981
4 | -0.012839 | -0.0032215 | 0.012842 | 0.0032234 | 3.4571e-06 | 1.9163e-06 | 0.019649 | 0.019649 | 0.019649 | 0.97236 | -0.53256 | 0.97265 | -0.52691 | 5.398
5 | 0.13819 | 0.035506 | -0.13773 | -0.035209 | 0.00046485 | 0.00029713 | 0.20699 | 0.20699 | 0.20699 | 0.99495 | -0.095349 | 0.99129 | -0.16486 | 56.8641
6 | -0.13819 | -0.035506 | 0.13849 | 0.035699 | 0.00030149 | 0.00019271 | 0.20699 | 0.20698 | 0.20699 | 0.99495 | -0.095349 | 0.99732 | -0.050539 | 56.864
7 | 0.0052268 | 0.0013099 | -0.0052265 | -0.0013099 | 2.8225e-07 | 2.3021e-08 | 0.0078458 | 0.0078459 | 0.0078459 | 0.99129 | -0.16486 | 0.99123 | -0.166 | 2.1555
8 | 0.1325 | 0.033899 | -0.1324 | -0.033839 | 9.367e-05 | 5.9868e-05 | 0.19914 | 0.19914 | 0.19914 | 0.99129 | -0.16486 | 0.99053 | -0.17948 | 54.7086
9 | -0.1479 | -0.038058 | 0.14801 | 0.038125 | 0.00010504 | 6.6928e-05 | 0.22103 | 0.22103 | 0.22103 | 0.99732 | -0.050539 | 0.99809 | -0.035944 | 30.3606
10 | -0.024991 | -0.0062715 | 0.025002 | 0.0062786 | 1.1565e-05 | 7.1302e-06 | 0.037902 | 0.037902 | 0.037902 | 0.98121 | -0.35997 | 0.98171 | -0.35027 | 10.4126
11 | 0.024991 | 0.0062715 | -0.024981 | -0.0062658 | 9.3423e-06 | 5.7601e-06 | 0.037902 | 0.037902 | 0.037902 | 0.98121 | -0.35997 | 0.98081 | -0.36782 | 10.4126
12 | 0.1105 | 0.027946 | -0.11041 | -0.027886 | 9.5455e-05 | 6.0061e-05 | 0.16758 | 0.16758 | 0.16758 | 0.98171 | -0.35027 | 0.98078 | -0.3683 | 15.3463
13 | -0.1355 | -0.034225 | 0.13567 | 0.034328 | 0.00016384 | 0.00010368 | 0.20548 | 0.20548 | 0.20548 | 0.98171 | -0.35027 | 0.983 | -0.32508 | 18.8171
14 | 0.020813 | 0.005221 | -0.020804 | -0.0052155 | 8.9845e-06 | 5.447e-06 | 0.031577 | 0.031577 | 0.031577 | 0.98081 | -0.36782 | 0.98035 | -0.37687 | 8.6751
15 | 0.12643 | 0.032343 | -0.12611 | -0.032138 | 0.00032121 | 0.00020527 | 0.19017 | 0.19017 | 0.19017 | 0.99053 | -0.17948 | 0.98778 | -0.23211 | 52.2446
16 | 0.0088971 | 0.0022302 | -0.0088953 | -0.0022294 | 1.7952e-06 | 8.3079e-07 | 0.013638 | 0.013638 | 0.013638 | 0.97074 | -0.56539 | 0.97053 | -0.56962 | 3.7468
17 | -0.0088971 | -0.0022302 | 0.0088998 | 0.0022315 | 2.7932e-06 | 1.2924e-06 | 0.013638 | 0.013638 | 0.013638 | 0.97074 | -0.56539 | 0.97107 | -0.5588 | 3.7467
18 | -0.025782 | -0.0064641 | 0.025803 | 0.0064772 | 2.1214e-05 | 1.3128e-05 | 0.039508 | 0.039508 | 0.039508 | 0.97107 | -0.5588 | 0.97195 | -0.54155 | 10.8538
19 | 0.016882 | 0.0042326 | -0.016878 | -0.00423 | 4.4361e-06 | 2.6205e-06 | 0.02587 | 0.02587 | 0.02587 | 0.97107 | -0.5588 | 0.97079 | -0.56432 | 7.1071
20 | -0.13567 | -0.034328 | 0.13583 | 0.034432 | 0.00016357 | 0.0001035 | 0.20548 | 0.20548 | 0.20548 | 0.983 | -0.32508 | 0.9843 | -0.29999 | 18.8171
21 | 0.0068929 | 0.0017273 | -0.0068921 | -0.0017271 | 7.3379e-07 | 2.406e-07 | 0.01042 | 0.01042 | 0.01042 | 0.9843 | -0.29999 | 0.98418 | -0.30222 | 2.8627
22 | -0.14272 | -0.036159 | 0.14274 | 0.036173 | 2.1577e-05 | 1.3668e-05 | 0.2159 | 0.2159 | 0.2159 | 0.9843 | -0.29999 | 0.98446 | -0.29684 | 19.7712
23 | 0.089722 | 0.022702 | -0.08964 | -0.022651 | 8.2048e-05 | 5.1172e-05 | 0.1362 | 0.1362 | 0.1362 | 0.98078 | -0.3683 | 0.9798 | -0.38737 | 12.4727
24 | -0.01874 | -0.0047016 | 0.018747 | 0.0047059 | 7.0784e-06 | 4.2451e-06 | 0.028672 | 0.028672 | 0.028672 | 0.97265 | -0.52691 | 0.97305 | -0.51899 | 7.8769
25 | -0.16271 | -0.04188 | 0.1628 | 0.04194 | 9.4816e-05 | 6.0175e-05 | 0.24266 | 0.24266 | 0.24266 | 0.99936 | -0.011973 | 1 | 0 | 22.2214
26 | 0.15782 | 0.040655 | -0.15764 | -0.040538 | 0.00018389 | 0.00011665 | 0.23538 | 0.23538 | 0.23538 | 0.99936 | -0.011973 | 0.99809 | -0.035944 | 21.5551
27 | 0.22178 | 0.057028 | -0.2216 | -0.056914 | 0.0001789 | 0.00011398 | 0.33053 | 0.33053 | 0.33053 | 1 | 0 | 0.99912 | -0.016612 | 30.2682
28 | 0.00963 | 0.0024138 | -0.0096283 | -0.002413 | 1.6712e-06 | 7.8705e-07 | 0.014357 | 0.014357 | 0.014357 | 0.99809 | -0.035944 | 0.9979 | -0.039587 | 3.9443
29 | -0.0043561 | -0.0010916 | 0.0043562 | 0.0010916 | 6.304e-08 | -6.7532e-09 | 0.00666 | 0.00666 | 0.00666 | 0.97326 | -0.51488 | 0.97327 | -0.51458 | 1.8297
30 | 0.0043561 | 0.0010916 | -0.0043557 | -0.0010916 | 4.4578e-07 | -4.7705e-08 | 0.00666 | 0.0066601 | 0.0066601 | 0.97326 | -0.51488 | 0.97315 | -0.51703 | 1.8297
31 | -0.017509 | -0.0043899 | 0.017514 | 0.0043928 | 4.9119e-06 | 2.9164e-06 | 0.02677 | 0.02677 | 0.02677 | 0.97327 | -0.51458 | 0.97357 | -0.50869 | 7.3544
32 | 0.013153 | 0.0032983 | -0.013146 | -0.0032945 | 6.8387e-06 | 3.8167e-06 | 0.02011 | 0.02011 | 0.02011 | 0.97327 | -0.51458 | 0.97272 | -0.52549 | 5.5248
33 | 0.013146 | 0.0032945 | -0.013145 | -0.003294 | 8.981e-07 | 5.0128e-07 | 0.02011 | 0.02011 | 0.02011 | 0.97272 | -0.52549 | 0.97265 | -0.52693 | 5.5248
34 | 0.003027 | 0.00075811 | -0.0030268 | -0.00075829 | 1.896e-07 | -1.7127e-07 | 0.0046307 | 0.0046308 | 0.0046308 | 0.97265 | -0.52693 | 0.97258 | -0.52824 | 1.2722
35 | -0.019486 | -0.004887 | 0.019492 | 0.0048907 | 6.1939e-06 | 3.7325e-06 | 0.029784 | 0.029784 | 0.029784 | 0.97357 | -0.50869 | 0.97391 | -0.50203 | 8.1823
36 | 0.0030268 | 0.00075829 | -0.0030265 | -0.00075852 | 2.5865e-07 | -2.3356e-07 | 0.0046308 | 0.0046309 | 0.0046309 | 0.97258 | -0.52824 | 0.97249 | -0.53004 | 1.2722
37 | 0.005202 | 0.0013036 | -0.0052017 | -0.0013036 | 2.8076e-07 | 3.2748e-08 | 0.0079552 | 0.0079552 | 0.0079552 | 0.97303 | -0.51941 | 0.97297 | -0.52054 | 2.1855
38 | -0.005202 | -0.0013036 | 0.0052021 | 0.0013036 | 1.0348e-07 | 1.2066e-08 | 0.0079552 | 0.0079552 | 0.0079552 | 0.97303 | -0.51941 | 0.97305 | -0.51899 | 2.1855
39 | 0.0039086 | 0.00097949 | -0.0039084 | -0.00097954 | 1.6738e-07 | -4.801e-08 | 0.0059776 | 0.0059776 | 0.0059776 | 0.97297 | -0.52054 | 0.97292 | -0.52144 | 1.6422
40 | -0.02395 | -0.0060095 | 0.023959 | 0.006015 | 8.969e-06 | 5.5186e-06 | 0.036627 | 0.036627 | 0.036627 | 0.97305 | -0.51899 | 0.97345 | -0.51114 | 10.0624
41 | 0.027291 | 0.0068553 | -0.027282 | -0.0068495 | 9.3422e-06 | 5.8007e-06 | 0.0417 | 0.0417 | 0.0417 | 0.97399 | -0.50049 | 0.97362 | -0.50766 | 11.4561
42 | -0.04113 | -0.010324 | 0.041146 | 0.010334 | 1.5807e-05 | 9.9836e-06 | 0.062843 | 0.062843 | 0.062843 | 0.97399 | -0.50049 | 0.97439 | -0.49243 | 17.2645
43 | 0.013839 | 0.0034691 | -0.013836 | -0.0034675 | 2.83e-06 | 1.6012e-06 | 0.021143 | 0.021143 | 0.021143 | 0.97399 | -0.50049 | 0.97377 | -0.50478 | 5.8085
44 | 0.026006 | 0.0065297 | -0.026001 | -0.006527 | 4.3151e-06 | 2.6711e-06 | 0.03975 | 0.03975 | 0.03975 | 0.97362 | -0.50766 | 0.97345 | -0.51114 | 10.9203
45 | 0.0041795 | 0.0010474 | -0.0041793 | -0.0010474 | 2.4538e-07 | -4.3017e-08 | 0.0063826 | 0.0063827 | 0.0063827 | 0.97439 | -0.49243 | 0.97433 | -0.49366 | 1.7535
46 | -0.045326 | -0.011382 | 0.045334 | 0.011387 | 8.6439e-06 | 5.4722e-06 | 0.069226 | 0.069225 | 0.069226 | 0.97439 | -0.49243 | 0.9746 | -0.48844 | 19.018
47 | 0.006318 | 0.0015832 | -0.0063175 | -0.0015831 | 5.3542e-07 | 1.5213e-07 | 0.0096545 | 0.0096545 | 0.0096545 | 0.97377 | -0.50478 | 0.97368 | -0.50656 | 2.6523
48 | -0.069964 | -0.017571 | 0.070048 | 0.017624 | 8.3449e-05 | 5.3164e-05 | 0.10683 | 0.10683 | 0.10683 | 0.9746 | -0.48844 | 0.97587 | -0.46347 | 29.3501
49 | 0.02463 | 0.0061838 | -0.024626 | -0.0061815 | 3.8218e-06 | 2.3562e-06 | 0.037609 | 0.037609 | 0.037609 | 0.9746 | -0.48844 | 0.97443 | -0.49169 | 10.3321
50 | 0.016525 | 0.0041432 | -0.01652 | -0.0041401 | 5.1519e-06 | 3.022e-06 | 0.025083 | 0.025083 | 0.025083 | 0.98035 | -0.37687 | 0.98001 | -0.38342 | 6.8909
51 | 0.12259 | 0.031255 | -0.12246 | -0.031171 | 0.00013119 | 8.3833e-05 | 0.18486 | 0.18486 | 0.18486 | 0.98778 | -0.23211 | 0.98662 | -0.25431 | 50.7865
52 | 0.08964 | 0.022651 | -0.089579 | -0.022613 | 6.1135e-05 | 3.8131e-05 | 0.1362 | 0.1362 | 0.1362 | 0.9798 | -0.38737 | 0.97907 | -0.40161 | 12.4727
53 | 0.080536 | 0.020348 | -0.080507 | -0.02033 | 2.8958e-05 | 1.795e-05 | 0.12246 | 0.12246 | 0.12246 | 0.97907 | -0.40161 | 0.97869 | -0.40911 | 11.2143
54 | 0.0031101 | 0.00077906 | -0.0031098 | -0.00077938 | 3.7648e-07 | -3.2406e-07 | 0.0047267 | 0.0047269 | 0.0047269 | 0.97907 | -0.40161 | 0.97894 | -0.40415 | 1.2986
55 | 0.005932 | 0.0014861 | -0.0059313 | -0.0014859 | 7.2364e-07 | 1.6459e-07 | 0.0090154 | 0.0090155 | 0.0090155 | 0.97907 | -0.40161 | 0.97894 | -0.40417 | 2.4768
56 | 0.013118 | 0.0032885 | -0.013115 | -0.0032869 | 2.9512e-06 | 1.647e-06 | 0.020083 | 0.020083 | 0.020083 | 0.97195 | -0.54155 | 0.97171 | -0.54627 | 5.5174
57 | -0.038921 | -0.0097657 | 0.038995 | 0.0098126 | 7.4386e-05 | 4.6914e-05 | 0.059591 | 0.059591 | 0.059591 | 0.97195 | -0.54155 | 0.97397 | -0.50155 | 16.3711
58 | 0.013028 | 0.0032658 | -0.013027 | -0.0032648 | 1.8681e-06 | 1.0391e-06 | 0.019905 | 0.019905 | 0.019905 | 0.97397 | -0.50155 | 0.97382 | -0.50456 | 5.4684
59 | -0.052024 | -0.013078 | 0.052055 | 0.013098 | 3.068e-05 | 1.9474e-05 | 0.079495 | 0.079495 | 0.079495 | 0.97397 | -0.50155 | 0.9746 | -0.48921 | 21.8394
60 | 0.012951 | 0.0032462 | -0.01295 | -0.0032456 | 1.0586e-06 | 5.8757e-07 | 0.019774 | 0.019774 | 0.019774 | 0.9746 | -0.48921 | 0.97451 | -0.49092 | 5.4324
61 | -0.065006 | -0.016344 | 0.065138 | 0.016428 | 0.00013219 | 8.4155e-05 | 0.099269 | 0.099269 | 0.099269 | 0.9746 | -0.48921 | 0.97676 | -0.44672 | 27.2717
62 | 0.0041092 | 0.0010298 | -0.0041092 | -0.0010299 | 4.904e-08 | -1.1667e-08 | 0.0062128 | 0.0062128 | 0.0062128 | 0.98418 | -0.30222 | 0.98417 | -0.30247 | 1.7068
63 | 0.0027829 | 0.00069726 | -0.0027828 | -0.00069743 | 1.3612e-07 | -1.7342e-07 | 0.0042075 | 0.0042076 | 0.0042076 | 0.98418 | -0.30222 | 0.98413 | -0.30325 | 1.1559
64 | -0.14547 | -0.036856 | 0.14556 | 0.036913 | 9.0351e-05 | 5.7254e-05 | 0.22002 | 0.22002 | 0.22002 | 0.98446 | -0.29684 | 0.98513 | -0.28392 | 20.1483
65 | -0.0013681 | -0.00034287 | 0.0013681 | 0.00034276 | 1.5624e-08 | -1.1167e-07 | 0.0020772 | 0.0020772 | 0.0020772 | 0.98 | -0.38366 | 0.98001 | -0.38342 | 0.57067
66 | 0.0018944 | 0.00047446 | -0.0018943 | -0.00047475 | 8.4663e-08 | -2.8815e-07 | 0.0028794 | 0.0028795 | 0.0028795 | 0.97894 | -0.40417 | 0.97889 | -0.40511 | 0.79107
67 | 0.0040369 | 0.0010114 | -0.0040363 | -0.0010116 | 6.1835e-07 | -1.5475e-07 | 0.0061361 | 0.0061363 | 0.0061363 | 0.97894 | -0.40417 | 0.97878 | -0.40739 | 1.6858
68 | 0.077972 | 0.019695 | -0.077922 | -0.019663 | 5.0532e-05 | 3.1258e-05 | 0.11861 | 0.11861 | 0.11861 | 0.97869 | -0.40911 | 0.978 | -0.42264 | 10.8614
69 | -0.0091185 | -0.0022853 | 0.00912 | 0.002286 | 1.526e-06 | 6.9414e-07 | 0.013658 | 0.013658 | 0.013658 | 0.99344 | -0.12469 | 0.99362 | -0.12118 | 3.7522
70 | -0.00912 | -0.002286 | 0.0091226 | 0.0022872 | 2.6085e-06 | 1.1863e-06 | 0.013658 | 0.013658 | 0.013658 | 0.99362 | -0.12118 | 0.99393 | -0.11518 | 3.7522
71 | 0.014601 | 0.0036615 | -0.014598 | -0.0036597 | 3.2984e-06 | 1.8721e-06 | 0.02185 | 0.02185 | 0.02185 | 0.99436 | -0.10684 | 0.99412 | -0.11158 | 6.0028
72 | -0.014601 | -0.0036615 | 0.014605 | 0.003664 | 4.3736e-06 | 2.4821e-06 | 0.02185 | 0.02185 | 0.02185 | 0.99436 | -0.10684 | 0.99469 | -0.10056 | 6.0028
73 | 0.0091242 | 0.0022879 | -0.0091226 | -0.0022872 | 1.5638e-06 | 7.1105e-07 | 0.013658 | 0.013658 | 0.013658 | 0.99412 | -0.11158 | 0.99393 | -0.11518 | 3.7521
74 | -0.20938 | -0.053514 | 0.20959 | 0.053647 | 0.00020776 | 0.00013231 | 0.3136 | 0.3136 | 0.3136 | 0.99469 | -0.10056 | 0.99577 | -0.080064 | 28.718
75 | 0.19478 | 0.04985 | -0.19466 | -0.049774 | 0.0001206 | 7.6742e-05 | 0.29175 | 0.29175 | 0.29175 | 0.99469 | -0.10056 | 0.99402 | -0.11335 | 26.7171
76 | -0.21104 | -0.054009 | 0.21109 | 0.054041 | 5.0032e-05 | 3.1864e-05 | 0.31576 | 0.31576 | 0.31576 | 0.99577 | -0.080064 | 0.99602 | -0.075169 | 28.9159
77 | 0.19317 | 0.049401 | -0.19291 | -0.049233 | 0.00026292 | 0.00016729 | 0.28952 | 0.28952 | 0.28952 | 0.99402 | -0.11335 | 0.99254 | -0.14152 | 26.5132
78 | -0.0066031 | -0.0016548 | 0.0066043 | 0.0016552 | 1.2173e-06 | 3.7641e-07 | 0.010053 | 0.010053 | 0.010053 | 0.9774 | -0.43366 | 0.9776 | -0.42979 | 2.7617
79 | 0.0066031 | 0.0016548 | -0.0066022 | -0.0016545 | 8.8811e-07 | 2.7472e-07 | 0.010053 | 0.010053 | 0.010053 | 0.9774 | -0.43366 | 0.97725 | -0.43649 | 2.7618
80 | 0.013448 | 0.0033716 | -0.013443 | -0.0033692 | 4.3167e-06 | 2.4183e-06 | 0.02047 | 0.02047 | 0.02047 | 0.9776 | -0.42979 | 0.97725 | -0.43653 | 5.6235
81 | -0.020052 | -0.0050268 | 0.020058 | 0.0050303 | 5.935e-06 | 3.5853e-06 | 0.030522 | 0.030522 | 0.030522 | 0.9776 | -0.42979 | 0.97791 | -0.42358 | 8.3852
82 | 0.0021434 | 0.00053703 | -0.0021433 | -0.00053717 | 5.5082e-08 | -1.3753e-07 | 0.0032636 | 0.0032636 | 0.0032636 | 0.97725 | -0.43649 | 0.97723 | -0.43703 | 0.89661
83 | 0.0049931 | 0.0012513 | -0.0049927 | -0.0012513 | 3.5926e-07 | 1.0201e-08 | 0.007496 | 0.0074961 | 0.0074961 | 0.99116 | -0.16795 | 0.99108 | -0.16946 | 2.0594
84 | -0.0049931 | -0.0012513 | 0.0049941 | 0.0012513 | 1.0549e-06 | 2.9729e-08 | 0.007496 | 0.0074958 | 0.007496 | 0.99116 | -0.16795 | 0.99139 | -0.16352 | 2.0593
85 | -0.0078032 | -0.0019554 | 0.0078038 | 0.0019556 | 5.7159e-07 | 2.2253e-07 | 0.011712 | 0.011712 | 0.011712 | 0.99139 | -0.16352 | 0.99147 | -0.16198 | 3.2176
86 | -0.023125 | -0.0058037 | 0.023139 | 0.0058123 | 1.3993e-05 | 8.5764e-06 | 0.035168 | 0.035168 | 0.035168 | 0.97852 | -0.41163 | 0.97917 | -0.39895 | 9.6617
87 | 0.023125 | 0.0058037 | -0.023112 | -0.0057957 | 1.317e-05 | 8.0723e-06 | 0.035168 | 0.035169 | 0.035169 | 0.97852 | -0.41163 | 0.97791 | -0.42358 | 9.6617
88 | -0.02865 | -0.0071935 | 0.028669 | 0.0072057 | 1.9653e-05 | 1.223e-05 | 0.043543 | 0.043543 | 0.043543 | 0.97917 | -0.39895 | 0.9799 | -0.38458 | 11.9624
89 | -0.2146 | -0.054921 | 0.21496 | 0.055149 | 0.00035822 | 0.00022817 | 0.32101 | 0.32101 | 0.32101 | 0.99602 | -0.075169 | 0.99784 | -0.040756 | 29.3962
90 | 0.19014 | 0.04854 | -0.18995 | -0.04842 | 0.00018777 | 0.00011946 | 0.28537 | 0.28538 | 0.28538 | 0.99254 | -0.14152 | 0.99147 | -0.16198 | 26.1333
91 | 0.0045845 | 0.0011489 | -0.0045842 | -0.0011489 | 2.6384e-07 | -1.2037e-08 | 0.0069805 | 0.0069806 | 0.0069806 | 0.97725 | -0.43653 | 0.97719 | -0.43774 | 1.9177
92 | -0.001539 | -0.00038572 | 0.0015391 | 0.00038556 | 2.8266e-08 | -1.5552e-07 | 0.0023379 | 0.0023378 | 0.0023379 | 0.97956 | -0.39127 | 0.97958 | -0.39088 | 0.64228
93 | 0.0029506 | 0.00073897 | -0.0029502 | -0.00073938 | 4.0204e-07 | -4.1447e-07 | 0.0044818 | 0.0044821 | 0.0044821 | 0.97958 | -0.39088 | 0.97943 | -0.39374 | 1.2313
94 | 0.078662 | 0.019886 | -0.078585 | -0.019837 | 7.6769e-05 | 4.8952e-05 | 0.11955 | 0.11955 | 0.11955 | 0.97958 | -0.39088 | 0.97853 | -0.41125 | 32.8441
95 | -0.083152 | -0.021011 | 0.083177 | 0.021027 | 2.5105e-05 | 1.6014e-05 | 0.12637 | 0.12637 | 0.12637 | 0.97958 | -0.39088 | 0.9799 | -0.38458 | 34.7176
96 | 0.18215 | 0.046465 | -0.18184 | -0.046271 | 0.00030541 | 0.0001942 | 0.27366 | 0.27366 | 0.27366 | 0.99147 | -0.16198 | 0.98965 | -0.19676 | 25.0608
97 | -0.022645 | -0.0056809 | 0.022656 | 0.0056877 | 1.1167e-05 | 6.8369e-06 | 0.034601 | 0.034601 | 0.034601 | 0.97391 | -0.50203 | 0.97443 | -0.49169 | 9.5057
98 | -0.11185 | -0.028233 | 0.11205 | 0.028362 | 0.00020277 | 0.00012954 | 0.16992 | 0.16991 | 0.16992 | 0.9799 | -0.38458 | 0.98184 | -0.34681 | 46.68
99 | 0.0058441 | 0.0014646 | -0.0058437 | -0.0014646 | 3.2092e-07 | 7.0751e-08 | 0.0089111 | 0.0089111 | 0.0089111 | 0.97587 | -0.46347 | 0.97581 | -0.46462 | 2.4481
100 | -0.075892 | -0.019089 | 0.076081 | 0.01921 | 0.00018983 | 0.00012102 | 0.11575 | 0.11575 | 0.11575 | 0.97587 | -0.46347 | 0.97853 | -0.41125 | 31.7982
101 | -0.11205 | -0.028362 | 0.11233 | 0.028543 | 0.0002834 | 0.00018105 | 0.16991 | 0.16991 | 0.16991 | 0.98184 | -0.34681 | 0.98455 | -0.29427 | 46.6799
102 | -0.12075 | -0.030654 | 0.12088 | 0.030736 | 0.00012874 | 8.2265e-05 | 0.18264 | 0.18264 | 0.18264 | 0.98455 | -0.29427 | 0.9857 | -0.27213 | 50.1762
103 | -0.0014732 | -0.00036898 | 0.0014733 | 0.00036879 | 3.0109e-08 | -1.8843e-07 | 0.0022219 | 0.0022218 | 0.0022219 | 0.9866 | -0.25474 | 0.98662 | -0.25431 | 0.61041
104 | 0.0014732 | 0.00036898 | -0.0014732 | -0.00036922 | 3.8549e-08 | -2.4121e-07 | 0.0022219 | 0.002222 | 0.002222 | 0.9866 | -0.25474 | 0.98657 | -0.25528 | 0.61044
105 | 0.12099 | 0.030802 | -0.12088 | -0.030736 | 0.0001039 | 6.6391e-05 | 0.18264 | 0.18264 | 0.18264 | 0.98662 | -0.25431 | 0.9857 | -0.27213 | 50.1762
106 | 0.0033956 | 0.00085082 | -0.0033954 | -0.00085096 | 2.4707e-07 | -1.4616e-07 | 0.0051893 | 0.0051894 | 0.0051894 | 0.97368 | -0.50656 | 0.9736 | -0.50809 | 1.4257
107 | -0.0049907 | -0.0012508 | 0.004991 | 0.0012508 | 3.4912e-07 | 3.8628e-09 | 0.0074424 | 0.0074423 | 0.0074424 | 0.99783 | -0.041056 | 0.9979 | -0.039587 | 2.0446
108 | -0.0041148 | -0.0010312 | 0.0041151 | 0.0010311 | 3.0632e-07 | -7.4682e-08 | 0.0062068 | 0.0062067 | 0.0062068 | 0.98647 | -0.25817 | 0.98655 | -0.25661 | 1.7052
109 | 0.0017693 | 0.00044332 | -0.0017692 | -0.00044341 | 2.2701e-08 | -9.3977e-08 | 0.0026688 | 0.0026688 | 0.0026688 | 0.98647 | -0.25817 | 0.98645 | -0.25844 | 0.73319
110 | -0.007805 | -0.0019559 | 0.0078058 | 0.0019562 | 8.4305e-07 | 3.3239e-07 | 0.011772 | 0.011772 | 0.011772 | 0.98655 | -0.25661 | 0.98667 | -0.25434 | 3.2341
111 | 0.0094755 | 0.002375 | -0.0094739 | -0.0023743 | 1.5701e-06 | 7.4307e-07 | 0.01429 | 0.01429 | 0.01429 | 0.98667 | -0.25434 | 0.98649 | -0.25782 | 3.9259
112 | -0.017281 | -0.0043312 | 0.017285 | 0.0043333 | 3.6247e-06 | 2.138e-06 | 0.026062 | 0.026062 | 0.026062 | 0.98667 | -0.25434 | 0.98689 | -0.24994 | 7.16
113 | 0.0039381 | 0.00098696 | -0.0039381 | -0.00098697 | 3.4536e-08 | -1.1219e-08 | 0.0059402 | 0.0059402 | 0.0059402 | 0.98649 | -0.25782 | 0.98648 | -0.258 | 1.6319
114 | 0.0055358 | 0.0013873 | -0.0055349 | -0.0013872 | 9.0897e-07 | 1.3799e-07 | 0.0083502 | 0.0083503 | 0.0083503 | 0.98649 | -0.25782 | 0.98631 | -0.26126 | 2.294
115 | -0.018318 | -0.0045923 | 0.018322 | 0.0045949 | 4.4082e-06 | 2.6243e-06 | 0.02762 | 0.02762 | 0.02762 | 0.98689 | -0.24994 | 0.98715 | -0.24489 | 7.5879
116 | 0.15174 | 0.038568 | -0.1517 | -0.038544 | 3.7961e-05 | 2.4073e-05 | 0.22892 | 0.22892 | 0.22892 | 0.98715 | -0.24489 | 0.98688 | -0.25008 | 20.9632
117 | -0.17006 | -0.043163 | 0.17021 | 0.043256 | 0.0001466 | 9.314e-05 | 0.25654 | 0.25654 | 0.25654 | 0.98715 | -0.24489 | 0.98808 | -0.22698 | 23.4925
118 | -0.14684 | -0.037233 | 0.14692 | 0.037288 | 8.6628e-05 | 5.4904e-05 | 0.22195 | 0.22195 | 0.22195 | 0.98513 | -0.28392 | 0.98576 | -0.27165 | 20.3248
119 | -0.14692 | -0.037288 | 0.14695 | 0.037305 | 2.712e-05 | 1.7188e-05 | 0.22195 | 0.22195 | 0.22195 | 0.98576 | -0.27165 | 0.98596 | -0.26782 | 20.3248
120 | -0.14825 | -0.037632 | 0.14833 | 0.037678 | 7.3401e-05 | 4.6528e-05 | 0.22392 | 0.22392 | 0.22392 | 0.98596 | -0.26782 | 0.98649 | -0.25753 | 20.5051
121 | -0.15041 | -0.038201 | 0.15047 | 0.038235 | 5.394e-05 | 3.4201e-05 | 0.22706 | 0.22706 | 0.22706 | 0.98649 | -0.25753 | 0.98688 | -0.25008 | 20.7931
122 | 0.17762 | 0.045213 | -0.17755 | -0.045165 | 7.5943e-05 | 4.8276e-05 | 0.26732 | 0.26732 | 0.26732 | 0.98965 | -0.19676 | 0.98919 | -0.20563 | 24.4799
123 | 0.17327 | 0.044093 | -0.17309 | -0.04398 | 0.00017813 | 0.0001132 | 0.26089 | 0.26089 | 0.26089 | 0.98919 | -0.20563 | 0.98808 | -0.22698 | 23.8907
124 | 0.0042775 | 0.0010719 | -0.0042773 | -0.001072 | 2.2879e-07 | -4.2726e-08 | 0.0064345 | 0.0064346 | 0.0064346 | 0.98919 | -0.20563 | 0.98913 | -0.20676 | 1.7677
125 | 0.0015786 | 0.00039559 | -0.0015786 | -0.00039563 | 6.1972e-09 | -3.3647e-08 | 0.0023747 | 0.0023748 | 0.0023748 | 0.98913 | -0.20676 | 0.98913 | -0.20684 | 0.65241
126 | 0.21893 | 0.056244 | -0.21867 | -0.056081 | 0.00025638 | 0.00016333 | 0.32655 | 0.32655 | 0.32655 | 0.99912 | -0.016612 | 0.99784 | -0.040756 | 29.9037
127 | 0.0064969 | 0.0016283 | -0.0064963 | -0.0016281 | 5.2813e-07 | 1.5716e-07 | 0.009885 | 0.009885 | 0.009885 | 0.978 | -0.42264 | 0.97791 | -0.42435 | 2.7157
128 | 0.071425 | 0.018035 | -0.071343 | -0.017983 | 8.2283e-05 | 5.1731e-05 | 0.10872 | 0.10872 | 0.10872 | 0.978 | -0.42264 | 0.97676 | -0.44672 | 14.9343
129 | 0.0062048 | 0.0015551 | -0.0062046 | -0.001555 | 2.2154e-07 | 5.9029e-08 | 0.0094525 | 0.0094525 | 0.0094525 | 0.97676 | -0.44672 | 0.97673 | -0.44747 | 2.5968

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39105 | 0.10017

## res_load
| p_mw | q_mvar
0 | 0.010367 | 0.0025983
1 | 0.002458 | 0.00061603
2 | 0.0094105 | 0.0023585
3 | 0.0041688 | 0.0010448
4 | 0.0052265 | 0.0013099
5 | 0.0059705 | 0.0014964
6 | 0.0088953 | 0.0022294
7 | 0.020683 | 0.0051837
8 | 0.0058981 | 0.0014782
9 | 0.0048869 | 0.0012248
10 | 0.004812 | 0.001206
11 | 0.0043557 | 0.0010916
12 | 0.010118 | 0.0025359
13 | 0.0019718 | 0.00049419
14 | 0.0030265 | 0.00075852
15 | 0.0012931 | 0.00032409
16 | 0.0012761 | 0.00031983
17 | 0.0075182 | 0.0018842
18 | 0.0020429 | 0.000512
19 | 0.0041793 | 0.0010474
20 | 0.0042787 | 0.0010724
21 | 0.0035233 | 0.00088301
22 | 0.016878 | 0.00423
23 | 0.013115 | 0.0032869
24 | 0.013027 | 0.0032648
25 | 0.0027241 | 0.00068273
26 | 0.0013681 | 0.00034287
27 | 0.015152 | 0.0037974
28 | 0.0018943 | 0.00047475
29 | 0.0040363 | 0.0010116
30 | 0.0025351 | 0.00063536
31 | 0.0031098 | 0.00077938
32 | 0.0091185 | 0.0022853
33 | 0.0054734 | 0.0013718
34 | 0.0014465 | 0.00036253
35 | 0.0014874 | 0.00037278
36 | 0.0044588 | 0.0011175
37 | 0.0049927 | 0.0012513
38 | 0.0028091 | 0.00070402
39 | 0.0055109 | 0.0013812
40 | 0.0030537 | 0.00076532
41 | 0.0035104 | 0.00087978
42 | 0.002768 | 0.00069373
43 | 0.0088589 | 0.0022203
44 | 0.0021433 | 0.00053717
45 | 0.001539 | 0.00038572
46 | 0.0031529 | 0.00079019
47 | 0.0039084 | 0.00097954
48 | 0.0019699 | 0.00049371
49 | 0.0058437 | 0.0014646
50 | 0.0025038 | 0.00062751
51 | 0.0029502 | 0.00073938
52 | 0.0084205 | 0.0021104
53 | 0.0014732 | 0.00036922
54 | 0.0029218 | 0.00073228
55 | 0.0049907 | 0.0012508
56 | 0.0046373 | 0.0011622
57 | 0.0045842 | 0.0011489
58 | 0.0023455 | 0.00058784
59 | 0.0036899 | 0.00092478
60 | 0.0017692 | 0.00044341
61 | 0.0010331 | 0.00025893
62 | 0.0039381 | 0.00098697
63 | 0.0055349 | 0.0013872
64 | 0.0012763 | 0.00031987
65 | 0.0013048 | 0.000327
66 | 0.0020852 | 0.0005226
67 | 0.0041092 | 0.0010299
68 | 0.0027828 | 0.00069743
69 | 0.0012315 | 0.00030864
70 | 0.0042191 | 0.0010574
71 | 0.0028876 | 0.0007237
72 | 0.0026987 | 0.00067636
73 | 0.0015786 | 0.00039563
74 | 0.0026723 | 0.00066974
75 | 0.0037171 | 0.0009316
76 | 0.01295 | 0.0032456
77 | 0.0064963 | 0.0016281
78 | 0.0062046 | 0.001555
79 | 0.0033954 | 0.00085096

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1