## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_191-44_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_191-44_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_191-44_0_5_node_17 | 0.4 | n |  | TRUE
3 | bus_LV_191-44_0_5_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_191-44_0_5_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_191-44_0_5_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_191-44_0_5_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_191-44_0_5_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_191-44_0_5_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_191-44_0_5_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_191-44_0_5_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_191-44_0_5_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_191-44_0_5_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_191-44_0_5_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_191-44_0_5_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_191-44_0_5_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_191-44_0_5_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_191-44_0_5_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_191-44_0_5_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_191-44_0_5_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_191-44_0_5_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_191-44_0_5_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_191-44_0_5_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_191-44_0_5_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_191-44_0_5_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_191-44_0_5_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_191-44_0_5_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_191-44_0_5_node_56 | 0.4 | n |  | TRUE
28 | bus_LV_191-44_0_5_node_36 | 0.4 | n |  | TRUE
29 | bus_MV_500_0_node_21 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_191-44_0_5_load_0 | 0 | 0.038487 | 0.0096459 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_191-44_0_5_load_25 | 5 | 0.048117 | 0.012059 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_191-44_0_5_load_24 | 8 | 0.031729 | 0.0079521 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_191-44_0_5_load_33 | 11 | 0.046205 | 0.01158 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_191-44_0_5_load_38 | 15 | 0.075561 | 0.018937 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_191-44_0_5_load_31 | 16 | 0.035936 | 0.0090065 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_191-44_0_5_load_54 | 19 | 0.0047903 | 0.0012006 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_191-44_0_5_load_35 | 20 | 0.0314 | 0.0078696 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_191-44_0_5_load_32 | 21 | 0.048305 | 0.012106 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_191-44_0_5_load_30 | 22 | 0.072573 | 0.018188 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_191-44_0_5_load_21 | 23 | 0.048027 | 0.012037 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_191-44_0_5_load_37 | 24 | 0.032551 | 0.008158 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_191-44_0_5_load_55 | 25 | 0.0052736 | 0.0013217 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_191-44_0_5_load_34 | 26 | 0.014336 | 0.0035929 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_191-44_0_5_load_56 | 27 | 0.0048927 | 0.0012262 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_191-44_0_5_load_36 | 28 | 0.032467 | 0.0081371 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_191-44_0_5_line_0 |  | 0 | 1 | 0.068329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_191-44_0_5_line_1 |  | 1 | 2 | 0.0096687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_191-44_0_5_line_2 |  | 2 | 12 | 0.077139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_191-44_0_5_line_3 |  | 2 | 10 | 0.021718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_191-44_0_5_line_4 |  | 3 | 4 | 0.03289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_191-44_0_5_line_5 |  | 3 | 5 | 0.011736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_191-44_0_5_line_6 |  | 4 | 20 | 0.02265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_191-44_0_5_line_7 |  | 4 | 18 | 0.034822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_191-44_0_5_line_8 |  | 5 | 17 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_191-44_0_5_line_9 |  | 6 | 7 | 0.023255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_191-44_0_5_line_10 |  | 6 | 8 | 0.054851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_191-44_0_5_line_11 |  | 7 | 15 | 0.043468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_191-44_0_5_line_12 |  | 8 | 10 | 0.066878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_191-44_0_5_line_13 |  | 9 | 10 | 0.063328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_191-44_0_5_line_14 |  | 9 | 11 | 0.041004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_191-44_0_5_line_15 |  | 12 | 13 | 0.083867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_191-44_0_5_line_16 |  | 12 | 14 | 0.046627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_191-44_0_5_line_17 |  | 13 | 23 | 0.052672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_191-44_0_5_line_18 |  | 14 | 21 | 0.02606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_191-44_0_5_line_19 |  | 14 | 22 | 0.038068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_191-44_0_5_line_20 |  | 15 | 24 | 0.022096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_191-44_0_5_line_21 |  | 16 | 17 | 0.019308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_191-44_0_5_line_22 |  | 18 | 19 | 0.0092065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_191-44_0_5_line_23 |  | 19 | 25 | 0.00018155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_191-44_0_5_line_24 |  | 20 | 26 | 0.026905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_191-44_0_5_line_25 |  | 24 | 28 | 0.012426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_191-44_0_5_line_26 |  | 25 | 27 | 0.00024966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_191-44_0_5_line_27 |  | 26 | 28 | 0.011167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_191-44_0_5_trafo_33 | 0.63 MVA 20/0.4 kV | 29 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2687982.5865 | 1250716.5225 | 2688007.821 | 1250702.0417 | 2688027.4218 | 1250690.7242 | 2688041.8344 | 1250682.4851
1 | 2687976.0649 | 1250714.4018 | 2687980.0171 | 1250712.1143 | 2687982.5865 | 1250716.5225
2 | 2687911.1998 | 1250746.8973 | 2687913.3821 | 1250750.9328 | 2687976.0649 | 1250714.4018
3 | 2687976.0649 | 1250714.4018 | 2687980.0171 | 1250712.1143 | 2687973.6762 | 1250702.4129 | 2687978.6359 | 1250699.8957
4 | 2687784.7112 | 1250659.5343 | 2687783.3657 | 1250656.0784 | 2687779.4891 | 1250646.1357 | 2687782.5846 | 1250644.0911 | 2687784.9222 | 1250641.2236 | 2687786.2943 | 1250637.7858 | 2687786.583 | 1250634.0984 | 2687785.7456 | 1250630.4943
5 | 2687784.7112 | 1250659.5343 | 2687793.142 | 1250666.2976 | 2687793.4766 | 1250667.1623
6 | 2687785.7456 | 1250630.4943 | 2687794.6294 | 1250626.0559 | 2687806.0578 | 1250620.4721
7 | 2687785.7456 | 1250630.4943 | 2687784.2012 | 1250627.7249 | 2687781.9925 | 1250625.4572 | 2687779.2763 | 1250623.8157 | 2687776.2319 | 1250622.9255 | 2687773.0622 | 1250622.8452 | 2687769.9712 | 1250623.5666 | 2687768.2884 | 1250619.4386 | 2687763.9972 | 1250608.9449
8 | 2687802.3326 | 1250690.0517 | 2687793.4766 | 1250667.1623
9 | 2687915.2645 | 1250581.388 | 2687916.7958 | 1250585.5471 | 2687919.3505 | 1250585.8631 | 2687921.4881 | 1250586.8066 | 2687923.2265 | 1250588.2001 | 2687924.7097 | 1250590.5127 | 2687929.2577 | 1250588.7789 | 2687933.0616 | 1250587.3342
10 | 2687933.0616 | 1250587.3342 | 2687933.6717 | 1250588.9556 | 2687952.9523 | 1250638.4516
11 | 2687915.2645 | 1250581.388 | 2687874.1763 | 1250595.5742
12 | 2687978.6359 | 1250699.8957 | 2687976.1368 | 1250697.3678 | 2687974.2926 | 1250693.4374 | 2687957.8164 | 1250650.9385 | 2687952.9523 | 1250638.4516
13 | 2687952.1784 | 1250648.7977 | 2687958.555 | 1250664.2373 | 2687973.6762 | 1250702.4129 | 2687978.6359 | 1250699.8957
14 | 2687952.1784 | 1250648.7977 | 2687914.2765 | 1250664.4437
15 | 2687911.1998 | 1250746.8973 | 2687913.3821 | 1250750.9328 | 2687900.3626 | 1250759.346 | 2687893.4186 | 1250762.8012 | 2687897.2475 | 1250770.853 | 2687921.4705 | 1250811.2539
16 | 2687870.7009 | 1250751.1778 | 2687882.5621 | 1250747.0505 | 2687888.9605 | 1250747.8015 | 2687896.9332 | 1250755.4033 | 2687911.1998 | 1250746.8973
17 | 2687921.4705 | 1250811.2539 | 2687937.0781 | 1250808.0164 | 2687959.55 | 1250796.0074 | 2687967.8943 | 1250788.4583
18 | 2687870.7009 | 1250751.1778 | 2687862.4166 | 1250751.344 | 2687859.3261 | 1250748.4738 | 2687853.9853 | 1250735.9741
19 | 2687870.7009 | 1250751.1778 | 2687856.8884 | 1250715.7037
20 | 2687874.1763 | 1250595.5742 | 2687853.2903 | 1250602.7854
21 | 2687802.3326 | 1250690.0517 | 2687809.3721 | 1250708.0312
22 | 2687763.9972 | 1250608.9449 | 2687761.5203 | 1250602.8703 | 2687760.5516 | 1250600.4076
23 | 2687760.5516 | 1250600.4076 | 2687760.4851 | 1250600.2386
24 | 2687830.9888 | 1250610.4853 | 2687815.6794 | 1250615.7711 | 2687806.0578 | 1250620.4721
25 | 2687841.5448 | 1250606.8407 | 2687853.2903 | 1250602.7854
26 | 2687760.4851 | 1250600.2386 | 2687760.3938 | 1250600.0063
27 | 2687841.5448 | 1250606.8407 | 2687830.9888 | 1250610.4853

## bus_geodata
| x | y | coords
0 | 2688041.8344 | 1250682.4851
1 | 2687982.5865 | 1250716.5225
2 | 2687976.0649 | 1250714.4018
3 | 2687784.7112 | 1250659.5343
4 | 2687785.7456 | 1250630.4943
5 | 2687793.4766 | 1250667.1623
6 | 2687933.0616 | 1250587.3342
7 | 2687915.2645 | 1250581.388
8 | 2687952.9523 | 1250638.4516
9 | 2687952.1784 | 1250648.7977
10 | 2687978.6359 | 1250699.8957
11 | 2687914.2765 | 1250664.4437
12 | 2687911.1998 | 1250746.8973
13 | 2687921.4705 | 1250811.2539
14 | 2687870.7009 | 1250751.1778
15 | 2687874.1763 | 1250595.5742
16 | 2687809.3721 | 1250708.0312
17 | 2687802.3326 | 1250690.0517
18 | 2687763.9972 | 1250608.9449
19 | 2687760.5516 | 1250600.4076
20 | 2687806.0578 | 1250620.4721
21 | 2687853.9853 | 1250735.9741
22 | 2687856.8884 | 1250715.7037
23 | 2687967.8943 | 1250788.4583
24 | 2687853.2903 | 1250602.7854
25 | 2687760.4851 | 1250600.2386
26 | 2687830.9888 | 1250610.4853
27 | 2687760.3938 | 1250600.0063
28 | 2687841.5448 | 1250606.8407
29 | 2687910.344 | 1250666.0671

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98627 | -0.2624 | 0.038487 | 0.0096459
1 | 0.98869 | -0.2154 | 0 | 0
2 | 0.98903 | -0.20876 | 0 | 0
3 | 0.9724 | -0.53232 | 0 | 0
4 | 0.97498 | -0.4815 | 0 | 0
5 | 0.97148 | -0.55052 | 0.048117 | 0.012059
6 | 0.98301 | -0.32477 | 0 | 0
7 | 0.98178 | -0.34874 | 0 | 0
8 | 0.98592 | -0.26847 | 0.031729 | 0.0079521
9 | 0.99601 | -0.075276 | 0 | 0
10 | 0.98986 | -0.19272 | 0 | 0
11 | 1 | 0 | -0.53597 | -0.13772
12 | 0.98663 | -0.25532 | 0 | 0
13 | 0.9829 | -0.32771 | 0 | 0
14 | 0.98559 | -0.27552 | 0 | 0
15 | 0.97947 | -0.3937 | 0.075561 | 0.018937
16 | 0.97001 | -0.57967 | 0.035936 | 0.0090065
17 | 0.97066 | -0.56683 | 0 | 0
18 | 0.9745 | -0.49105 | 0 | 0
19 | 0.97437 | -0.49358 | 0.0047903 | 0.0012006
20 | 0.97708 | -0.44047 | 0.0314 | 0.0078696
21 | 0.98501 | -0.28682 | 0.048305 | 0.012106
22 | 0.98474 | -0.29206 | 0.072573 | 0.018188
23 | 0.98056 | -0.37346 | 0.048027 | 0.012037
24 | 0.97861 | -0.41056 | 0.032551 | 0.008158
25 | 0.97437 | -0.49362 | 0.0052736 | 0.0013217
26 | 0.9779 | -0.42447 | 0.014336 | 0.0035929
27 | 0.97437 | -0.49364 | 0.0048927 | 0.0012262
28 | 0.9782 | -0.41857 | 0.032467 | 0.0081371
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.038487 | -0.0096459 | 0.038574 | 0.0097003 | 8.6397e-05 | 5.442e-05 | 0.058067 | 0.058067 | 0.058067 | 0.98627 | -0.2624 | 0.98869 | -0.2154 | 15.9526
1 | -0.038574 | -0.0097003 | 0.038586 | 0.009708 | 1.2225e-05 | 7.7002e-06 | 0.058067 | 0.058067 | 0.058067 | 0.98869 | -0.2154 | 0.98903 | -0.20876 | 15.9525
2 | 0.16975 | 0.042864 | -0.16938 | -0.042627 | 0.00037772 | 0.0002368 | 0.25551 | 0.25552 | 0.25552 | 0.98903 | -0.20876 | 0.98663 | -0.25532 | 14.0393
3 | -0.20834 | -0.052572 | 0.2085 | 0.052673 | 0.00016017 | 0.00010112 | 0.31358 | 0.31358 | 0.31358 | 0.98903 | -0.20876 | 0.98986 | -0.19272 | 17.2297
4 | -0.084176 | -0.021144 | 0.084381 | 0.021274 | 0.0002047 | 0.0001306 | 0.12883 | 0.12883 | 0.12883 | 0.9724 | -0.53232 | 0.97498 | -0.4815 | 35.3921
5 | 0.084176 | 0.021144 | -0.084103 | -0.021097 | 7.3038e-05 | 4.6599e-05 | 0.12883 | 0.12883 | 0.12883 | 0.9724 | -0.53232 | 0.97148 | -0.55052 | 35.3921
6 | -0.099346 | -0.025028 | 0.099541 | 0.025153 | 0.00019539 | 0.00012476 | 0.15167 | 0.15167 | 0.15167 | 0.97498 | -0.4815 | 0.97708 | -0.44047 | 41.667
7 | 0.014965 | 0.0037534 | -0.014958 | -0.0037495 | 6.8126e-06 | 3.926e-06 | 0.022841 | 0.022841 | 0.022841 | 0.97498 | -0.4815 | 0.9745 | -0.49105 | 6.275
8 | 0.035986 | 0.0090379 | -0.035958 | -0.0090203 | 2.7969e-05 | 1.7597e-05 | 0.055127 | 0.055127 | 0.055127 | 0.97148 | -0.55052 | 0.97066 | -0.56683 | 15.1448
9 | 0.28718 | 0.072688 | -0.28685 | -0.072478 | 0.00032999 | 0.00020972 | 0.43497 | 0.43498 | 0.43498 | 0.98301 | -0.32477 | 0.98178 | -0.34874 | 23.8998
10 | -0.28718 | -0.072688 | 0.28796 | 0.073183 | 0.00077835 | 0.00049466 | 0.43497 | 0.43497 | 0.43497 | 0.98301 | -0.32477 | 0.98592 | -0.26847 | 23.8997
11 | 0.28685 | 0.072478 | -0.28624 | -0.072086 | 0.00061683 | 0.00039203 | 0.43498 | 0.43498 | 0.43498 | 0.98178 | -0.34874 | 0.97947 | -0.3937 | 23.8998
12 | -0.31969 | -0.081135 | 0.32086 | 0.081879 | 0.0011695 | 0.00074418 | 0.48286 | 0.48286 | 0.48286 | 0.98592 | -0.26847 | 0.98986 | -0.19272 | 26.5308
13 | 0.53237 | 0.13648 | -0.52936 | -0.13455 | 0.0030127 | 0.001924 | 0.79644 | 0.79644 | 0.79644 | 0.99601 | -0.075276 | 0.98986 | -0.19272 | 43.7604
14 | -0.53237 | -0.13648 | 0.53432 | 0.13772 | 0.0019507 | 0.0012458 | 0.79644 | 0.79644 | 0.79644 | 0.99601 | -0.075276 | 1 | 0 | 43.7603
15 | 0.048299 | 0.012209 | -0.048132 | -0.012103 | 0.00016705 | 0.00010585 | 0.072881 | 0.072882 | 0.072882 | 0.98663 | -0.25532 | 0.9829 | -0.32771 | 20.0224
16 | 0.12108 | 0.030418 | -0.12096 | -0.030346 | 0.00011664 | 7.1678e-05 | 0.18263 | 0.18264 | 0.18264 | 0.98663 | -0.25532 | 0.98559 | -0.27552 | 10.0349
17 | 0.048132 | 0.012103 | -0.048027 | -0.012037 | 0.00010492 | 6.6481e-05 | 0.072882 | 0.072882 | 0.072882 | 0.9829 | -0.32771 | 0.98056 | -0.37346 | 20.0225
18 | 0.048331 | 0.012122 | -0.048305 | -0.012106 | 2.602e-05 | 1.5989e-05 | 0.072973 | 0.072973 | 0.072973 | 0.98559 | -0.27552 | 0.98501 | -0.28682 | 10.0238
19 | 0.07263 | 0.018224 | -0.072573 | -0.018188 | 5.7226e-05 | 3.517e-05 | 0.10966 | 0.10966 | 0.10966 | 0.98559 | -0.27552 | 0.98474 | -0.29206 | 10.0424
20 | 0.21067 | 0.053149 | -0.2105 | -0.053041 | 0.00016989 | 0.00010734 | 0.32018 | 0.32018 | 0.32018 | 0.97947 | -0.3937 | 0.97861 | -0.41056 | 17.5925
21 | -0.035936 | -0.0090065 | 0.035958 | 0.0090203 | 2.2004e-05 | 1.3844e-05 | 0.055127 | 0.055127 | 0.055127 | 0.97001 | -0.57967 | 0.97066 | -0.56683 | 15.1448
22 | 0.014958 | 0.0037495 | -0.014957 | -0.0037485 | 1.8012e-06 | 1.0381e-06 | 0.022841 | 0.022841 | 0.022841 | 0.9745 | -0.49105 | 0.97437 | -0.49358 | 6.275
23 | 0.010166 | 0.0025479 | -0.010166 | -0.0025479 | 1.641e-08 | 8.2414e-09 | 0.015526 | 0.015526 | 0.015526 | 0.97437 | -0.49358 | 0.97437 | -0.49362 | 4.2653
24 | -0.13094 | -0.033022 | 0.13104 | 0.033085 | 0.00010038 | 6.2892e-05 | 0.19949 | 0.19949 | 0.19949 | 0.97708 | -0.44047 | 0.9779 | -0.42447 | 13.7011
25 | 0.17795 | 0.044883 | -0.17789 | -0.04484 | 6.8286e-05 | 4.2923e-05 | 0.27069 | 0.27069 | 0.27069 | 0.97861 | -0.41056 | 0.9782 | -0.41857 | 14.873
26 | 0.0048927 | 0.0012262 | -0.0048927 | -0.0012262 | 5.2267e-09 | 2.3547e-10 | 0.0074719 | 0.0074719 | 0.0074719 | 0.97437 | -0.49362 | 0.97437 | -0.49364 | 2.0527
27 | -0.14538 | -0.036678 | 0.14542 | 0.036703 | 4.1019e-05 | 2.5551e-05 | 0.2213 | 0.2213 | 0.2213 | 0.9779 | -0.42447 | 0.9782 | -0.41857 | 12.1594

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58218 | 0.1493

## res_load
| p_mw | q_mvar
0 | 0.038487 | 0.0096459
1 | 0.048117 | 0.012059
2 | 0.031729 | 0.0079521
3 | 0.046205 | 0.01158
4 | 0.075561 | 0.018937
5 | 0.035936 | 0.0090065
6 | 0.0047903 | 0.0012006
7 | 0.0314 | 0.0078696
8 | 0.048305 | 0.012106
9 | 0.072573 | 0.018188
10 | 0.048027 | 0.012037
11 | 0.032551 | 0.008158
12 | 0.0052736 | 0.0013217
13 | 0.014336 | 0.0035929
14 | 0.0048927 | 0.0012262
15 | 0.032467 | 0.0081371

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1