## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_194-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_194-3_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_194-3_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_194-3_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_194-3_0_6_node_23 | 0.4 | n |  | TRUE
5 | bus_LV_194-3_0_6_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_194-3_0_6_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_194-3_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_194-3_0_6_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_194-3_0_6_node_91 | 0.4 | n |  | TRUE
10 | bus_LV_194-3_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_194-3_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_194-3_0_6_node_116 | 0.4 | n |  | TRUE
13 | bus_LV_194-3_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_194-3_0_6_node_67 | 0.4 | n |  | TRUE
15 | bus_LV_194-3_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_194-3_0_6_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_194-3_0_6_node_90 | 0.4 | n |  | TRUE
18 | bus_LV_194-3_0_6_node_133 | 0.4 | n |  | TRUE
19 | bus_LV_194-3_0_6_node_131 | 0.4 | n |  | TRUE
20 | bus_LV_194-3_0_6_node_132 | 0.4 | n |  | TRUE
21 | bus_LV_194-3_0_6_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_194-3_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_194-3_0_6_node_104 | 0.4 | n |  | TRUE
24 | bus_LV_194-3_0_6_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_194-3_0_6_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_194-3_0_6_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_194-3_0_6_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_194-3_0_6_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_194-3_0_6_node_83 | 0.4 | n |  | TRUE
30 | bus_LV_194-3_0_6_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_194-3_0_6_node_99 | 0.4 | n |  | TRUE
32 | bus_LV_194-3_0_6_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_194-3_0_6_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_194-3_0_6_node_106 | 0.4 | n |  | TRUE
35 | bus_LV_194-3_0_6_node_98 | 0.4 | n |  | TRUE
36 | bus_LV_194-3_0_6_node_97 | 0.4 | n |  | TRUE
37 | bus_LV_194-3_0_6_node_94 | 0.4 | n |  | TRUE
38 | bus_LV_194-3_0_6_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_194-3_0_6_node_72 | 0.4 | n |  | TRUE
40 | bus_LV_194-3_0_6_node_69 | 0.4 | n |  | TRUE
41 | bus_LV_194-3_0_6_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_194-3_0_6_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_194-3_0_6_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_194-3_0_6_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_194-3_0_6_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_194-3_0_6_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_194-3_0_6_node_51 | 0.4 | n |  | TRUE
48 | bus_LV_194-3_0_6_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_194-3_0_6_node_117 | 0.4 | n |  | TRUE
50 | bus_LV_194-3_0_6_node_125 | 0.4 | n |  | TRUE
51 | bus_LV_194-3_0_6_node_123 | 0.4 | n |  | TRUE
52 | bus_LV_194-3_0_6_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_194-3_0_6_node_134 | 0.4 | n |  | TRUE
54 | bus_LV_194-3_0_6_node_135 | 0.4 | n |  | TRUE
55 | bus_LV_194-3_0_6_node_103 | 0.4 | n |  | TRUE
56 | bus_LV_194-3_0_6_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_194-3_0_6_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_194-3_0_6_node_26 | 0.4 | n |  | TRUE
59 | bus_LV_194-3_0_6_node_100 | 0.4 | n |  | TRUE
60 | bus_LV_194-3_0_6_node_105 | 0.4 | n |  | TRUE
61 | bus_LV_194-3_0_6_node_96 | 0.4 | n |  | TRUE
62 | bus_LV_194-3_0_6_node_95 | 0.4 | n |  | TRUE
63 | bus_LV_194-3_0_6_node_102 | 0.4 | n |  | TRUE
64 | bus_LV_194-3_0_6_node_101 | 0.4 | n |  | TRUE
65 | bus_LV_194-3_0_6_node_85 | 0.4 | n |  | TRUE
66 | bus_LV_194-3_0_6_node_87 | 0.4 | n |  | TRUE
67 | bus_LV_194-3_0_6_node_88 | 0.4 | n |  | TRUE
68 | bus_LV_194-3_0_6_node_84 | 0.4 | n |  | TRUE
69 | bus_LV_194-3_0_6_node_107 | 0.4 | n |  | TRUE
70 | bus_LV_194-3_0_6_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_194-3_0_6_node_27 | 0.4 | n |  | TRUE
72 | bus_LV_194-3_0_6_node_29 | 0.4 | n |  | TRUE
73 | bus_LV_194-3_0_6_node_30 | 0.4 | n |  | TRUE
74 | bus_LV_194-3_0_6_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_194-3_0_6_node_112 | 0.4 | n |  | TRUE
76 | bus_LV_194-3_0_6_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_194-3_0_6_node_115 | 0.4 | n |  | TRUE
78 | bus_LV_194-3_0_6_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_194-3_0_6_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_194-3_0_6_node_109 | 0.4 | n |  | TRUE
81 | bus_LV_194-3_0_6_node_114 | 0.4 | n |  | TRUE
82 | bus_LV_194-3_0_6_node_35 | 0.4 | n |  | TRUE
83 | bus_LV_194-3_0_6_node_36 | 0.4 | n |  | TRUE
84 | bus_LV_194-3_0_6_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_194-3_0_6_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_194-3_0_6_node_44 | 0.4 | n |  | TRUE
87 | bus_LV_194-3_0_6_node_45 | 0.4 | n |  | TRUE
88 | bus_LV_194-3_0_6_node_46 | 0.4 | n |  | TRUE
89 | bus_LV_194-3_0_6_node_48 | 0.4 | n |  | TRUE
90 | bus_LV_194-3_0_6_node_49 | 0.4 | n |  | TRUE
91 | bus_LV_194-3_0_6_node_56 | 0.4 | n |  | TRUE
92 | bus_LV_194-3_0_6_node_65 | 0.4 | n |  | TRUE
93 | bus_LV_194-3_0_6_node_55 | 0.4 | n |  | TRUE
94 | bus_LV_194-3_0_6_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_194-3_0_6_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_194-3_0_6_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_194-3_0_6_node_62 | 0.4 | n |  | TRUE
98 | bus_LV_194-3_0_6_node_63 | 0.4 | n |  | TRUE
99 | bus_LV_194-3_0_6_node_64 | 0.4 | n |  | TRUE
100 | bus_LV_194-3_0_6_node_92 | 0.4 | n |  | TRUE
101 | bus_LV_194-3_0_6_node_126 | 0.4 | n |  | TRUE
102 | bus_LV_194-3_0_6_node_68 | 0.4 | n |  | TRUE
103 | bus_LV_194-3_0_6_node_122 | 0.4 | n |  | TRUE
104 | bus_LV_194-3_0_6_node_124 | 0.4 | n |  | TRUE
105 | bus_LV_194-3_0_6_node_71 | 0.4 | n |  | TRUE
106 | bus_LV_194-3_0_6_node_108 | 0.4 | n |  | TRUE
107 | bus_LV_194-3_0_6_node_73 | 0.4 | n |  | TRUE
108 | bus_LV_194-3_0_6_node_74 | 0.4 | n |  | TRUE
109 | bus_LV_194-3_0_6_node_75 | 0.4 | n |  | TRUE
110 | bus_LV_194-3_0_6_node_76 | 0.4 | n |  | TRUE
111 | bus_LV_194-3_0_6_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_194-3_0_6_node_78 | 0.4 | n |  | TRUE
113 | bus_LV_194-3_0_6_node_79 | 0.4 | n |  | TRUE
114 | bus_LV_194-3_0_6_node_80 | 0.4 | n |  | TRUE
115 | bus_LV_194-3_0_6_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_194-3_0_6_node_118 | 0.4 | n |  | TRUE
117 | bus_LV_194-3_0_6_node_119 | 0.4 | n |  | TRUE
118 | bus_LV_194-3_0_6_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_194-3_0_6_node_120 | 0.4 | n |  | TRUE
120 | bus_LV_194-3_0_6_node_121 | 0.4 | n |  | TRUE
121 | bus_LV_194-3_0_6_node_127 | 0.4 | n |  | TRUE
122 | bus_LV_194-3_0_6_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_194-3_0_6_node_129 | 0.4 | n |  | TRUE
124 | bus_LV_194-3_0_6_node_130 | 0.4 | n |  | TRUE
125 | bus_LV_194-3_0_6_node_137 | 0.4 | n |  | TRUE
126 | bus_LV_194-3_0_6_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_194-3_0_6_node_136 | 0.4 | n |  | TRUE
128 | bus_MV_365_0_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_194-3_0_6_load_0 | 0 | 0.016926 | 0.004242 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_194-3_0_6_load_33 | 5 | 0.014533 | 0.0036423 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_194-3_0_6_load_32 | 6 | 0.018104 | 0.0045373 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_194-3_0_6_load_91 | 9 | 0.003113 | 0.0007802 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_194-3_0_6_load_116 | 12 | 0.0052046 | 0.0013044 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_194-3_0_6_load_43 | 16 | 0.0051545 | 0.0012918 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_194-3_0_6_load_90 | 17 | 0.0063678 | 0.0015959 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_194-3_0_6_load_133 | 18 | 0.002317 | 0.00058068 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_194-3_0_6_load_131 | 19 | 0.0036129 | 0.00090549 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_194-3_0_6_load_104 | 23 | 0.0037375 | 0.0009367 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_194-3_0_6_load_57 | 26 | 0.0079573 | 0.0019943 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_194-3_0_6_load_83 | 29 | 0.0065178 | 0.0016335 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_194-3_0_6_load_99 | 31 | 0.010004 | 0.0025072 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_194-3_0_6_load_106 | 34 | 0.010501 | 0.0026318 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_194-3_0_6_load_98 | 35 | 0.0094184 | 0.0023605 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_194-3_0_6_load_97 | 36 | 0.0077656 | 0.0019463 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_194-3_0_6_load_94 | 37 | 0.010759 | 0.0026965 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_194-3_0_6_load_69 | 40 | 0.0066533 | 0.0016675 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_194-3_0_6_load_34 | 41 | 0.016234 | 0.0040685 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_194-3_0_6_load_40 | 43 | 0.0067189 | 0.0016839 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_194-3_0_6_load_37 | 44 | 0.0051204 | 0.0012833 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_194-3_0_6_load_51 | 47 | 0.0063436 | 0.0015899 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_194-3_0_6_load_117 | 49 | 0.0053256 | 0.0013347 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_194-3_0_6_load_125 | 50 | 0.0012805 | 0.00032092 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_194-3_0_6_load_123 | 51 | 0.0013548 | 0.00033954 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_194-3_0_6_load_134 | 53 | 0.0042469 | 0.0010644 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_194-3_0_6_load_103 | 55 | 0.0079837 | 0.0020009 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_194-3_0_6_load_50 | 56 | 0.0063462 | 0.0015905 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_194-3_0_6_load_31 | 57 | 0.0017646 | 0.00044225 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_194-3_0_6_load_26 | 58 | 0.011915 | 0.0029863 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_194-3_0_6_load_100 | 59 | 0.012947 | 0.0032448 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_194-3_0_6_load_105 | 60 | 0.0046531 | 0.0011662 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_194-3_0_6_load_96 | 61 | 0.0077523 | 0.0019429 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_194-3_0_6_load_95 | 62 | 0.0097691 | 0.0024484 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_194-3_0_6_load_102 | 63 | 0.010789 | 0.002704 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_194-3_0_6_load_101 | 64 | 0.010794 | 0.0027052 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_194-3_0_6_load_88 | 67 | 0.0021223 | 0.0005319 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_194-3_0_6_load_84 | 68 | 0.002107 | 0.00052808 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_194-3_0_6_load_107 | 69 | 0.0021712 | 0.00054415 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_194-3_0_6_load_70 | 70 | 0.0017797 | 0.00044603 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_194-3_0_6_load_29 | 72 | 0.0018622 | 0.00046672 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_194-3_0_6_load_58 | 74 | 0.0034299 | 0.00085962 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_194-3_0_6_load_112 | 75 | 0.0030318 | 0.00075985 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_194-3_0_6_load_110 | 76 | 0.00305 | 0.00076439 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_194-3_0_6_load_115 | 77 | 0.0017364 | 0.00043519 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_194-3_0_6_load_59 | 78 | 0.0043476 | 0.0010896 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_194-3_0_6_load_109 | 80 | 0.0026667 | 0.00066834 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_194-3_0_6_load_114 | 81 | 0.0019594 | 0.00049108 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_194-3_0_6_load_35 | 82 | 0.0039044 | 0.00097853 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_194-3_0_6_load_36 | 83 | 0.0025882 | 0.00064867 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_194-3_0_6_load_54 | 84 | 0.0015818 | 0.00039644 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_194-3_0_6_load_53 | 85 | 0.0057609 | 0.0014438 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_194-3_0_6_load_44 | 86 | 0.0063521 | 0.001592 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_194-3_0_6_load_45 | 87 | 0.0067242 | 0.0016852 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_194-3_0_6_load_49 | 90 | 0.0040402 | 0.0010126 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_194-3_0_6_load_56 | 91 | 0.005215 | 0.001307 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_194-3_0_6_load_65 | 92 | 0.0034153 | 0.00085596 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_194-3_0_6_load_55 | 93 | 0.0038475 | 0.00096428 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_194-3_0_6_load_60 | 95 | 0.0016849 | 0.00042227 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_194-3_0_6_load_61 | 96 | 0.0037845 | 0.00094849 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_194-3_0_6_load_62 | 97 | 0.0044576 | 0.0011172 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_194-3_0_6_load_63 | 98 | 0.00423 | 0.0010601 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_194-3_0_6_load_64 | 99 | 0.001688 | 0.00042306 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_194-3_0_6_load_126 | 101 | 0.0011989 | 0.00030047 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_194-3_0_6_load_68 | 102 | 0.0012802 | 0.00032085 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_194-3_0_6_load_122 | 103 | 0.0012891 | 0.00032308 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_194-3_0_6_load_124 | 104 | 0.0038363 | 0.00096147 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_194-3_0_6_load_71 | 105 | 0.0021402 | 0.0005364 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_194-3_0_6_load_108 | 106 | 0.0020243 | 0.00050733 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_194-3_0_6_load_73 | 107 | 0.002508 | 0.00062856 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_194-3_0_6_load_74 | 108 | 0.001365 | 0.00034209 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_194-3_0_6_load_75 | 109 | 0.0017818 | 0.00044657 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_194-3_0_6_load_76 | 110 | 0.00213 | 0.00053384 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_194-3_0_6_load_82 | 111 | 0.0018301 | 0.00045866 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_194-3_0_6_load_78 | 112 | 0.00093608 | 0.0002346 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_194-3_0_6_load_79 | 113 | 0.0010708 | 0.00026838 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_194-3_0_6_load_80 | 114 | 0.0028354 | 0.00071063 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_194-3_0_6_load_113 | 115 | 0.0022363 | 0.00056046 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_194-3_0_6_load_118 | 116 | 0.0014753 | 0.00036975 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_194-3_0_6_load_119 | 117 | 0.001313 | 0.00032907 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_194-3_0_6_load_111 | 118 | 0.0018401 | 0.00046117 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_194-3_0_6_load_120 | 119 | 0.0013028 | 0.00032651 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_194-3_0_6_load_121 | 120 | 0.0012683 | 0.00031787 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_194-3_0_6_load_127 | 121 | 0.0022894 | 0.00057378 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_194-3_0_6_load_129 | 123 | 0.0022078 | 0.00055333 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_194-3_0_6_load_137 | 125 | 0.0021162 | 0.00053037 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_194-3_0_6_load_138 | 126 | 0.0021892 | 0.00054866 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_194-3_0_6_load_136 | 127 | 0.0023657 | 0.00059291 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 71 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_194-3_0_6_line_0 |  | 0 | 1 | 0.034208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_194-3_0_6_line_1 |  | 0 | 2 | 0.034361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_194-3_0_6_line_2 |  | 1 | 3 | 0.026589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_194-3_0_6_line_3 |  | 2 | 4 | 0.008727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_194-3_0_6_line_4 |  | 3 | 5 | 0.030626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_194-3_0_6_line_5 |  | 3 | 6 | 0.029519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_194-3_0_6_line_6 |  | 4 | 37 | 0.0084582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_194-3_0_6_line_7 |  | 4 | 30 | 0.024954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_194-3_0_6_line_8 |  | 5 | 41 | 0.039149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_194-3_0_6_line_9 |  | 6 | 21 | 0.0016663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_194-3_0_6_line_10 |  | 7 | 8 | 0.026193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_194-3_0_6_line_11 |  | 7 | 9 | 0.018193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_194-3_0_6_line_12 |  | 8 | 18 | 0.019527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_194-3_0_6_line_13 |  | 9 | 17 | 0.020457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_194-3_0_6_line_14 |  | 10 | 11 | 0.060747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_194-3_0_6_line_15 |  | 10 | 12 | 0.005421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_194-3_0_6_line_16 |  | 11 | 17 | 0.024917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_194-3_0_6_line_17 |  | 12 | 48 | 0.014466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_194-3_0_6_line_18 |  | 13 | 14 | 0.037624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_194-3_0_6_line_19 |  | 13 | 15 | 0.031031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_194-3_0_6_line_20 |  | 13 | 16 | 0.020284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_194-3_0_6_line_21 |  | 14 | 50 | 0.017284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_194-3_0_6_line_22 |  | 14 | 51 | 0.020047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_194-3_0_6_line_23 |  | 15 | 19 | 0.007645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_194-3_0_6_line_24 |  | 15 | 20 | 0.015405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_194-3_0_6_line_25 |  | 16 | 52 | 0.0034733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_194-3_0_6_line_26 |  | 20 | 53 | 0.013115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_194-3_0_6_line_27 |  | 20 | 54 | 0.000638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_194-3_0_6_line_28 |  | 21 | 22 | 0.024106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_194-3_0_6_line_29 |  | 22 | 23 | 0.014992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_194-3_0_6_line_30 |  | 23 | 55 | 0.0058623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_194-3_0_6_line_31 |  | 24 | 25 | 0.035434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_194-3_0_6_line_32 |  | 24 | 26 | 0.016775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_194-3_0_6_line_33 |  | 25 | 56 | 0.011592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_194-3_0_6_line_34 |  | 27 | 28 | 0.005511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_194-3_0_6_line_35 |  | 27 | 29 | 0.011912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_194-3_0_6_line_36 |  | 28 | 57 | 0.017322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_194-3_0_6_line_37 |  | 28 | 58 | 0.023691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_194-3_0_6_line_38 |  | 30 | 31 | 0.014377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_194-3_0_6_line_39 |  | 31 | 59 | 0.02045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_194-3_0_6_line_40 |  | 32 | 33 | 0.034637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_194-3_0_6_line_41 |  | 32 | 34 | 0.013999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_194-3_0_6_line_42 |  | 33 | 35 | 0.014854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_194-3_0_6_line_43 |  | 33 | 36 | 0.0012963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_194-3_0_6_line_44 |  | 34 | 60 | 0.032348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_194-3_0_6_line_45 |  | 36 | 61 | 0.015172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_194-3_0_6_line_46 |  | 38 | 39 | 0.007683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_194-3_0_6_line_47 |  | 38 | 40 | 0.018601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_194-3_0_6_line_48 |  | 39 | 69 | 0.011042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_194-3_0_6_line_49 |  | 40 | 70 | 0.0016756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_194-3_0_6_line_50 |  | 41 | 82 | 0.026796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_194-3_0_6_line_51 |  | 42 | 43 | 0.014119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_194-3_0_6_line_52 |  | 42 | 44 | 0.033208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_194-3_0_6_line_53 |  | 43 | 46 | 0.012025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_194-3_0_6_line_54 |  | 44 | 52 | 0.010132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_194-3_0_6_line_55 |  | 45 | 46 | 0.011768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_194-3_0_6_line_56 |  | 45 | 47 | 0.032014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_194-3_0_6_line_57 |  | 46 | 87 | 0.007085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_194-3_0_6_line_58 |  | 47 | 56 | 0.018253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_194-3_0_6_line_59 |  | 48 | 49 | 0.0051181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_194-3_0_6_line_60 |  | 49 | 86 | 0.020982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_194-3_0_6_line_61 |  | 50 | 103 | 0.015572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_194-3_0_6_line_62 |  | 51 | 104 | 5.7269e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_194-3_0_6_line_63 |  | 52 | 86 | 0.019972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_194-3_0_6_line_64 |  | 54 | 127 | 0.010614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_194-3_0_6_line_65 |  | 54 | 124 | 0.012941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_194-3_0_6_line_66 |  | 55 | 60 | 0.028918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_194-3_0_6_line_67 |  | 57 | 77 | 0.0058706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_194-3_0_6_line_68 |  | 58 | 71 | 0.023691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_194-3_0_6_line_69 |  | 59 | 64 | 0.015117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_194-3_0_6_line_70 |  | 61 | 62 | 0.017795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_194-3_0_6_line_71 |  | 63 | 64 | 0.020764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_194-3_0_6_line_72 |  | 65 | 66 | 0.00416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_194-3_0_6_line_73 |  | 65 | 67 | 0.019711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_194-3_0_6_line_74 |  | 65 | 68 | 0.01732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_194-3_0_6_line_75 |  | 66 | 111 | 0.028988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_194-3_0_6_line_76 |  | 67 | 115 | 0.016351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_194-3_0_6_line_77 |  | 70 | 105 | 0.010273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_194-3_0_6_line_78 |  | 71 | 72 | 0.011307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_194-3_0_6_line_79 |  | 71 | 73 | 0.015933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_194-3_0_6_line_80 |  | 72 | 74 | 0.019696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_194-3_0_6_line_81 |  | 73 | 75 | 0.0064424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_194-3_0_6_line_82 |  | 73 | 76 | 0.025887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_194-3_0_6_line_83 |  | 74 | 78 | 0.013655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_194-3_0_6_line_84 |  | 75 | 79 | 0.030362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_194-3_0_6_line_85 |  | 76 | 80 | 0.013176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_194-3_0_6_line_86 |  | 77 | 81 | 0.0078634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_194-3_0_6_line_87 |  | 78 | 95 | 0.011071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_194-3_0_6_line_88 |  | 79 | 115 | 0.013021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_194-3_0_6_line_89 |  | 79 | 114 | 0.016897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_194-3_0_6_line_90 |  | 80 | 118 | 0.0069686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_194-3_0_6_line_91 |  | 81 | 106 | 0.015541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_194-3_0_6_line_92 |  | 82 | 83 | 0.00096306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_194-3_0_6_line_93 |  | 83 | 84 | 0.017183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_194-3_0_6_line_94 |  | 84 | 85 | 0.011646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_194-3_0_6_line_95 |  | 85 | 93 | 0.0090534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_194-3_0_6_line_96 |  | 87 | 88 | 0.037571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_194-3_0_6_line_97 |  | 88 | 89 | 0.007623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_194-3_0_6_line_98 |  | 88 | 90 | 0.019056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_194-3_0_6_line_99 |  | 89 | 91 | 0.0075738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_194-3_0_6_line_100 |  | 90 | 92 | 0.033213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_194-3_0_6_line_101 |  | 91 | 93 | 0.015614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_194-3_0_6_line_102 |  | 92 | 94 | 0.021707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_194-3_0_6_line_103 |  | 94 | 102 | 0.020827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_194-3_0_6_line_104 |  | 95 | 96 | 0.011197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_194-3_0_6_line_105 |  | 96 | 97 | 0.0047019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_194-3_0_6_line_106 |  | 97 | 98 | 0.024212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_194-3_0_6_line_107 |  | 98 | 99 | 0.010489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_194-3_0_6_line_108 |  | 99 | 100 | 0.032755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_194-3_0_6_line_109 |  | 100 | 101 | 0.007603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_194-3_0_6_line_110 |  | 101 | 102 | 0.0059551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_194-3_0_6_line_111 |  | 103 | 120 | 0.015141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_194-3_0_6_line_112 |  | 105 | 106 | 0.0080832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_194-3_0_6_line_113 |  | 107 | 108 | 0.016285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_194-3_0_6_line_114 |  | 107 | 109 | 0.019086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_194-3_0_6_line_115 |  | 108 | 110 | 0.0097665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_194-3_0_6_line_116 |  | 110 | 111 | 0.0083873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_194-3_0_6_line_117 |  | 112 | 113 | 0.021756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_194-3_0_6_line_118 |  | 112 | 114 | 0.015308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_194-3_0_6_line_119 |  | 116 | 117 | 0.0050384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_194-3_0_6_line_120 |  | 117 | 119 | 0.01042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_194-3_0_6_line_121 |  | 119 | 120 | 0.0044972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_194-3_0_6_line_122 |  | 121 | 122 | 0.0085802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_194-3_0_6_line_123 |  | 122 | 123 | 0.01039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_194-3_0_6_line_124 |  | 122 | 124 | 0.015367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_194-3_0_6_line_125 |  | 124 | 125 | 0.011125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_194-3_0_6_line_126 |  | 124 | 126 | 0.01048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_194-3_0_6_trafo_27 | 0.63 MVA 20/0.4 kV | 128 | 71 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2693761.9123 | 1247455.361 | 2693766.3778 | 1247457.6778 | 2693771.3374 | 1247463.1382 | 2693772.3334 | 1247468.458 | 2693772.261 | 1247473.0381 | 2693767.8829 | 1247476.6494 | 2693768.7696 | 1247482.7173
1 | 2693773.7377 | 1247516.717 | 2693768.7696 | 1247482.7173
2 | 2693741.3993 | 1247454.1803 | 2693760.094 | 1247448.5382 | 2693761.9123 | 1247455.361
3 | 2693773.7377 | 1247516.717 | 2693770.5343 | 1247522.96 | 2693770.5374 | 1247524.6725
4 | 2693741.3993 | 1247454.1803 | 2693726.3469 | 1247427.5082
5 | 2693741.3993 | 1247454.1803 | 2693738.1541 | 1247455.4188 | 2693727.3129 | 1247459.7952 | 2693715.3713 | 1247464.499 | 2693713.9817 | 1247465.1134
6 | 2693770.5374 | 1247524.6725 | 2693762.1575 | 1247525.8206
7 | 2693769.1466 | 1247549.5472 | 2693770.2277 | 1247541.3803 | 2693770.5461 | 1247535.1028 | 2693770.5374 | 1247524.6725
8 | 2693726.3469 | 1247427.5082 | 2693707.1061 | 1247393.4141
9 | 2693712.4578 | 1247465.7873 | 2693713.9817 | 1247465.1134
10 | 2693715.5635 | 1247158.1019 | 2693717.0978 | 1247154.7124 | 2693717.7866 | 1247153.1888 | 2693734.4742 | 1247165.6065
11 | 2693734.4742 | 1247165.6065 | 2693736.8106 | 1247172.6376 | 2693738.2561 | 1247183.3242
12 | 2693695.9988 | 1247158.9934 | 2693715.5635 | 1247158.1019
13 | 2693740.9982 | 1247203.5961 | 2693738.2561 | 1247183.3242
14 | 2693688.5184 | 1247231.2414 | 2693711.7313 | 1247227.9834 | 2693713.2148 | 1247233.5333 | 2693744.3382 | 1247228.2879
15 | 2693688.5184 | 1247231.2414 | 2693683.1509 | 1247232.0007
16 | 2693744.3382 | 1247228.2879 | 2693740.9982 | 1247203.5961
17 | 2693670.0875 | 1247235.4535 | 2693679.3528 | 1247234.2545 | 2693679.963 | 1247232.4516 | 2693683.1509 | 1247232.0007
18 | 2693623.226 | 1247220.7912 | 2693585.7949 | 1247225.5596
19 | 2693623.226 | 1247220.7912 | 2693641.4239 | 1247214.1179 | 2693638.5048 | 1247202.841
20 | 2693623.226 | 1247220.7912 | 2693625.2097 | 1247240.9781
21 | 2693585.7949 | 1247225.5596 | 2693579.8286 | 1247209.3381
22 | 2693585.7949 | 1247225.5596 | 2693578.5755 | 1247226.3574 | 2693566.2183 | 1247223.0848
23 | 2693638.5048 | 1247202.841 | 2693631.0083 | 1247204.4461
24 | 2693638.5048 | 1247202.841 | 2693642.0392 | 1247196.214 | 2693641.2266 | 1247188.3618
25 | 2693625.5493 | 1247244.4348 | 2693625.2097 | 1247240.9781
26 | 2693641.2266 | 1247188.3618 | 2693654.2287 | 1247186.3767
27 | 2693641.161 | 1247187.727 | 2693641.2266 | 1247188.3618
28 | 2693712.4578 | 1247465.7873 | 2693715.5628 | 1247472.4525 | 2693700.71 | 1247480.2015
29 | 2693700.71 | 1247480.2015 | 2693703.0745 | 1247495.0057 | 2693703.0745 | 1247495.0057
30 | 2693697.7175 | 1247497.3866 | 2693703.0745 | 1247495.0057
31 | 2693735.1021 | 1247307.3911 | 2693699.8244 | 1247311.6813
32 | 2693735.1021 | 1247307.3911 | 2693739.8809 | 1247323.4707
33 | 2693699.8244 | 1247311.6813 | 2693698.4568 | 1247300.1705
34 | 2693664.8356 | 1247454.9266 | 2693667.3871 | 1247459.8151
35 | 2693667.3871 | 1247459.8151 | 2693655.4911 | 1247459.2027
36 | 2693664.8356 | 1247454.9266 | 2693654.5084 | 1247454.9858 | 2693647.7719 | 1247456.8686
37 | 2693664.8356 | 1247454.9266 | 2693653.4344 | 1247434.1593
38 | 2693769.1466 | 1247549.5472 | 2693757.0772 | 1247557.359
39 | 2693757.0772 | 1247557.359 | 2693741.1067 | 1247567.6956 | 2693740.1972 | 1247568.7939
40 | 2693681.4267 | 1247557.011 | 2693684.7843 | 1247558.2094 | 2693687.9204 | 1247562.4288 | 2693700.0319 | 1247557.9612 | 2693710.6404 | 1247550.6121
41 | 2693710.6404 | 1247550.6121 | 2693709.8719 | 1247536.6338
42 | 2693681.4267 | 1247557.011 | 2693683.4893 | 1247571.7212
43 | 2693681.4267 | 1247557.011 | 2693681.3807 | 1247555.7155
44 | 2693709.8719 | 1247536.6338 | 2693701.3988 | 1247536.0105 | 2693698.251 | 1247532.5248 | 2693690.0118 | 1247532.3945 | 2693690.109 | 1247521.4798
45 | 2693680.8417 | 1247540.5531 | 2693681.3807 | 1247555.7155
46 | 2693596.281 | 1247492.3839 | 2693601.3642 | 1247498.1574
47 | 2693601.3642 | 1247498.1574 | 2693606.208 | 1247493.7416 | 2693608.4432 | 1247489.4848 | 2693612.8954 | 1247485.4742 | 2693613.587 | 1247484.4371
48 | 2693596.281 | 1247492.3839 | 2693588.7247 | 1247497.791 | 2693587.0221 | 1247498.1961
49 | 2693613.587 | 1247484.4371 | 2693614.5167 | 1247483.043
50 | 2693693.2008 | 1247370.5339 | 2693699.0963 | 1247379.2213 | 2693707.1061 | 1247393.4141
51 | 2693659.5347 | 1247249.7644 | 2693661.2183 | 1247263.7829
52 | 2693659.5347 | 1247249.7644 | 2693626.6669 | 1247254.5045
53 | 2693662.6522 | 1247275.7223 | 2693661.2183 | 1247263.7829
54 | 2693625.5493 | 1247244.4348 | 2693626.6669 | 1247254.5045
55 | 2693674.2798 | 1247273.7044 | 2693667.7807 | 1247274.8137 | 2693662.6522 | 1247275.7223
56 | 2693674.2798 | 1247273.7044 | 2693694.9909 | 1247270.9962 | 2693696.3034 | 1247282.0446
57 | 2693662.6522 | 1247275.7223 | 2693663.3589 | 1247282.7719
58 | 2693696.3034 | 1247282.0446 | 2693698.4568 | 1247300.1705
59 | 2693670.0875 | 1247235.4535 | 2693665.026 | 1247236.2125
60 | 2693665.026 | 1247236.2125 | 2693661.0993 | 1247236.8014 | 2693660.7949 | 1247237.8974 | 2693645.1868 | 1247240.7924
61 | 2693579.8286 | 1247209.3381 | 2693574.4532 | 1247194.7231
62 | 2693566.1629 | 1247223.0701 | 2693566.2183 | 1247223.0848
63 | 2693625.5493 | 1247244.4348 | 2693645.1868 | 1247240.7924
64 | 2693641.161 | 1247187.727 | 2693630.5949 | 1247189.0167
65 | 2693641.161 | 1247187.727 | 2693639.9595 | 1247174.8426
66 | 2693697.7175 | 1247497.3866 | 2693690.2941 | 1247500.6859 | 2693690.109 | 1247521.4798
67 | 2693647.7719 | 1247456.8686 | 2693647.4293 | 1247456.9644 | 2693642.4975 | 1247459.4325
68 | 2693642.0369 | 1247413.3905 | 2693647.3529 | 1247423.0818 | 2693653.4344 | 1247434.1593
69 | 2693740.1972 | 1247568.7939 | 2693735.9625 | 1247573.9079 | 2693735.021 | 1247582.3327
70 | 2693679.0786 | 1247522.8627 | 2693680.6424 | 1247534.9484 | 2693680.8417 | 1247540.5531
71 | 2693737.9136 | 1247602.8942 | 2693735.021 | 1247582.3327
72 | 2693557.1601 | 1247446.8763 | 2693554.4299 | 1247443.7309
73 | 2693557.1601 | 1247446.8763 | 2693560.8785 | 1247444.3664 | 2693573.5421 | 1247441.7754 | 2693575.4154 | 1247440.4433
74 | 2693557.1601 | 1247446.8763 | 2693568.3659 | 1247460.0822
75 | 2693554.4299 | 1247443.7309 | 2693535.442 | 1247421.827
76 | 2693575.4154 | 1247440.4433 | 2693580.0741 | 1247437.1305 | 2693584.0512 | 1247427.2673
77 | 2693614.5167 | 1247483.043 | 2693615.882 | 1247480.9957 | 2693618.0549 | 1247473.4917
78 | 2693642.0369 | 1247413.3905 | 2693637.5223 | 1247403.0243
79 | 2693626.2893 | 1247416.0995 | 2693642.0369 | 1247413.3905
80 | 2693637.5223 | 1247403.0243 | 2693629.8852 | 1247385.4885 | 2693629.6367 | 1247384.976
81 | 2693626.2893 | 1247416.0995 | 2693621.0195 | 1247414.0035 | 2693620.2567 | 1247414.1162
82 | 2693626.2893 | 1247416.0995 | 2693628.9599 | 1247431.6201 | 2693627.9184 | 1247433.9499 | 2693621.2778 | 1247437.6184
83 | 2693629.6367 | 1247384.976 | 2693623.6783 | 1247372.69
84 | 2693590.1626 | 1247415.8401 | 2693600.947 | 1247416.9667 | 2693620.2567 | 1247414.1162
85 | 2693609.6221 | 1247443.7457 | 2693612.7918 | 1247442.3063 | 2693621.2778 | 1247437.6184
86 | 2693642.4975 | 1247459.4325 | 2693635.4655 | 1247462.9516
87 | 2693618.8472 | 1247362.7285 | 2693623.6783 | 1247372.69
88 | 2693590.1626 | 1247415.8401 | 2693586.2536 | 1247421.8052 | 2693584.0512 | 1247427.2673
89 | 2693590.1626 | 1247415.8401 | 2693577.8587 | 1247404.2593
90 | 2693603.1358 | 1247444.8225 | 2693605.693 | 1247445.5301 | 2693609.6221 | 1247443.7457
91 | 2693620.3031 | 1247465.7275 | 2693620.3243 | 1247465.6542 | 2693633.838 | 1247463.7661 | 2693635.4655 | 1247462.9516
92 | 2693692.66 | 1247369.737 | 2693693.2008 | 1247370.5339
93 | 2693692.66 | 1247369.737 | 2693683.0113 | 1247355.5193
94 | 2693683.0113 | 1247355.5193 | 2693676.4716 | 1247345.8828
95 | 2693670.8662 | 1247338.7803 | 2693675.5105 | 1247344.4666 | 2693676.4716 | 1247345.8828
96 | 2693651.0677 | 1247315.1694 | 2693664.9622 | 1247298.7652 | 2693663.3589 | 1247282.7719
97 | 2693651.0677 | 1247315.1694 | 2693656.1982 | 1247320.8213
98 | 2693651.0677 | 1247315.1694 | 2693637.2898 | 1247302.0052
99 | 2693656.1982 | 1247320.8213 | 2693660.9892 | 1247326.6873
100 | 2693613.2761 | 1247279.0612 | 2693637.2898 | 1247302.0052
101 | 2693660.9892 | 1247326.6873 | 2693670.8662 | 1247338.7803
102 | 2693600.4686 | 1247261.6965 | 2693605.1791 | 1247270.0327 | 2693612.3479 | 1247278.1743 | 2693613.2761 | 1247279.0612
103 | 2693600.4686 | 1247261.6965 | 2693593.4925 | 1247267.6576 | 2693586.3221 | 1247276.8403 | 2693586.3221 | 1247276.8403
104 | 2693618.8472 | 1247362.7285 | 2693618.5166 | 1247362.0467 | 2693613.7192 | 1247352.7749
105 | 2693611.5584 | 1247348.5989 | 2693613.7192 | 1247352.7749
106 | 2693611.5584 | 1247348.5989 | 2693600.432 | 1247327.0952
107 | 2693600.432 | 1247327.0952 | 2693598.7761 | 1247323.8949 | 2693595.5389 | 1247317.8171
108 | 2693580.1411 | 1247288.9075 | 2693595.5389 | 1247317.8171
109 | 2693580.1411 | 1247288.9075 | 2693583.6072 | 1247282.1406
110 | 2693586.3221 | 1247276.8403 | 2693583.6072 | 1247282.1406
111 | 2693574.4532 | 1247194.7231 | 2693569.2266 | 1247180.5125
112 | 2693618.0549 | 1247473.4917 | 2693620.3031 | 1247465.7275
113 | 2693514.4894 | 1247394.7379 | 2693517.8399 | 1247401.5216 | 2693523.551 | 1247408.1098
114 | 2693514.4894 | 1247394.7379 | 2693512.6645 | 1247391.0431 | 2693503.276 | 1247379.3897
115 | 2693523.551 | 1247408.1098 | 2693529.9482 | 1247415.4894
116 | 2693535.442 | 1247421.827 | 2693529.9482 | 1247415.4894
117 | 2693575.711 | 1247389.1028 | 2693585.083 | 1247386.8712 | 2693588.5483 | 1247380.2987 | 2693587.8533 | 1247375.6584
118 | 2693575.711 | 1247389.1028 | 2693575.711 | 1247389.1028 | 2693577.8587 | 1247404.2593
119 | 2693562.3381 | 1247161.7836 | 2693564.0773 | 1247166.5124
120 | 2693567.6742 | 1247176.2917 | 2693564.0773 | 1247166.5124
121 | 2693567.6742 | 1247176.2917 | 2693569.2266 | 1247180.5125
122 | 2693638.7738 | 1247159.5234 | 2693638.5977 | 1247157.2855 | 2693638.0341 | 1247150.9752
123 | 2693638.7738 | 1247159.5234 | 2693635.7883 | 1247157.7082 | 2693628.9224 | 1247158.6004
124 | 2693638.7738 | 1247159.5234 | 2693639.8238 | 1247173.3949 | 2693639.9595 | 1247174.8426
125 | 2693639.9595 | 1247174.8426 | 2693637.6522 | 1247172.6601 | 2693629.7485 | 1247173.7361
126 | 2693639.9595 | 1247174.8426 | 2693642.025 | 1247172.7292 | 2693649.5185 | 1247171.8024

## bus_geodata
| x | y | coords
0 | 2693768.7696 | 1247482.7173
1 | 2693761.9123 | 1247455.361
2 | 2693773.7377 | 1247516.717
3 | 2693741.3993 | 1247454.1803
4 | 2693770.5374 | 1247524.6725
5 | 2693726.3469 | 1247427.5082
6 | 2693713.9817 | 1247465.1134
7 | 2693734.4742 | 1247165.6065
8 | 2693715.5635 | 1247158.1019
9 | 2693738.2561 | 1247183.3242
10 | 2693688.5184 | 1247231.2414
11 | 2693744.3382 | 1247228.2879
12 | 2693683.1509 | 1247232.0007
13 | 2693623.226 | 1247220.7912
14 | 2693585.7949 | 1247225.5596
15 | 2693638.5048 | 1247202.841
16 | 2693625.2097 | 1247240.9781
17 | 2693740.9982 | 1247203.5961
18 | 2693695.9988 | 1247158.9934
19 | 2693631.0083 | 1247204.4461
20 | 2693641.2266 | 1247188.3618
21 | 2693712.4578 | 1247465.7873
22 | 2693700.71 | 1247480.2015
23 | 2693703.0745 | 1247495.0057
24 | 2693735.1021 | 1247307.3911
25 | 2693699.8244 | 1247311.6813
26 | 2693739.8809 | 1247323.4707
27 | 2693667.3871 | 1247459.8151
28 | 2693664.8356 | 1247454.9266
29 | 2693655.4911 | 1247459.2027
30 | 2693769.1466 | 1247549.5472
31 | 2693757.0772 | 1247557.359
32 | 2693710.6404 | 1247550.6121
33 | 2693681.4267 | 1247557.011
34 | 2693709.8719 | 1247536.6338
35 | 2693683.4893 | 1247571.7212
36 | 2693681.3807 | 1247555.7155
37 | 2693762.1575 | 1247525.8206
38 | 2693601.3642 | 1247498.1574
39 | 2693596.281 | 1247492.3839
40 | 2693613.587 | 1247484.4371
41 | 2693707.1061 | 1247393.4141
42 | 2693659.5347 | 1247249.7644
43 | 2693661.2183 | 1247263.7829
44 | 2693626.6669 | 1247254.5045
45 | 2693674.2798 | 1247273.7044
46 | 2693662.6522 | 1247275.7223
47 | 2693696.3034 | 1247282.0446
48 | 2693670.0875 | 1247235.4535
49 | 2693665.026 | 1247236.2125
50 | 2693579.8286 | 1247209.3381
51 | 2693566.2183 | 1247223.0848
52 | 2693625.5493 | 1247244.4348
53 | 2693654.2287 | 1247186.3767
54 | 2693641.161 | 1247187.727
55 | 2693697.7175 | 1247497.3866
56 | 2693698.4568 | 1247300.1705
57 | 2693647.7719 | 1247456.8686
58 | 2693653.4344 | 1247434.1593
59 | 2693740.1972 | 1247568.7939
60 | 2693690.109 | 1247521.4798
61 | 2693680.8417 | 1247540.5531
62 | 2693679.0786 | 1247522.8627
63 | 2693737.9136 | 1247602.8942
64 | 2693735.021 | 1247582.3327
65 | 2693557.1601 | 1247446.8763
66 | 2693554.4299 | 1247443.7309
67 | 2693575.4154 | 1247440.4433
68 | 2693568.3659 | 1247460.0822
69 | 2693587.0221 | 1247498.1961
70 | 2693614.5167 | 1247483.043
71 | 2693642.0369 | 1247413.3905
72 | 2693637.5223 | 1247403.0243
73 | 2693626.2893 | 1247416.0995
74 | 2693629.6367 | 1247384.976
75 | 2693620.2567 | 1247414.1162
76 | 2693621.2778 | 1247437.6184
77 | 2693642.4975 | 1247459.4325
78 | 2693623.6783 | 1247372.69
79 | 2693590.1626 | 1247415.8401
80 | 2693609.6221 | 1247443.7457
81 | 2693635.4655 | 1247462.9516
82 | 2693693.2008 | 1247370.5339
83 | 2693692.66 | 1247369.737
84 | 2693683.0113 | 1247355.5193
85 | 2693676.4716 | 1247345.8828
86 | 2693645.1868 | 1247240.7924
87 | 2693663.3589 | 1247282.7719
88 | 2693651.0677 | 1247315.1694
89 | 2693656.1982 | 1247320.8213
90 | 2693637.2898 | 1247302.0052
91 | 2693660.9892 | 1247326.6873
92 | 2693613.2761 | 1247279.0612
93 | 2693670.8662 | 1247338.7803
94 | 2693600.4686 | 1247261.6965
95 | 2693618.8472 | 1247362.7285
96 | 2693613.7192 | 1247352.7749
97 | 2693611.5584 | 1247348.5989
98 | 2693600.432 | 1247327.0952
99 | 2693595.5389 | 1247317.8171
100 | 2693580.1411 | 1247288.9075
101 | 2693583.6072 | 1247282.1406
102 | 2693586.3221 | 1247276.8403
103 | 2693574.4532 | 1247194.7231
104 | 2693566.1629 | 1247223.0701
105 | 2693618.0549 | 1247473.4917
106 | 2693620.3031 | 1247465.7275
107 | 2693514.4894 | 1247394.7379
108 | 2693523.551 | 1247408.1098
109 | 2693503.276 | 1247379.3897
110 | 2693529.9482 | 1247415.4894
111 | 2693535.442 | 1247421.827
112 | 2693575.711 | 1247389.1028
113 | 2693587.8533 | 1247375.6584
114 | 2693577.8587 | 1247404.2593
115 | 2693584.0512 | 1247427.2673
116 | 2693562.3381 | 1247161.7836
117 | 2693564.0773 | 1247166.5124
118 | 2693603.1358 | 1247444.8225
119 | 2693567.6742 | 1247176.2917
120 | 2693569.2266 | 1247180.5125
121 | 2693638.0341 | 1247150.9752
122 | 2693638.7738 | 1247159.5234
123 | 2693628.9224 | 1247158.6004
124 | 2693639.9595 | 1247174.8426
125 | 2693629.7485 | 1247173.7361
126 | 2693649.5185 | 1247171.8024
127 | 2693630.5949 | 1247189.0167
128 | 2693626.2893 | 1247416.0995

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97331 | -0.51305 | 0.016926 | 0.004242
1 | 0.97388 | -0.50169 | 0 | 0
2 | 0.97286 | -0.52179 | 0 | 0
3 | 0.97433 | -0.49287 | 0 | 0
4 | 0.97275 | -0.52401 | 0 | 0
5 | 0.97541 | -0.47153 | 0.014533 | 0.0036423
6 | 0.97378 | -0.50367 | 0.018104 | 0.0045373
7 | 0.97171 | -0.54459 | 0 | 0
8 | 0.97166 | -0.54571 | 0 | 0
9 | 0.97175 | -0.54381 | 0.003113 | 0.0007802
10 | 0.9728 | -0.52312 | 0 | 0
11 | 0.97213 | -0.53634 | 0 | 0
12 | 0.97286 | -0.52194 | 0.0052046 | 0.0013044
13 | 0.97341 | -0.51103 | 0 | 0
14 | 0.97295 | -0.52012 | 0 | 0
15 | 0.97286 | -0.5219 | 0 | 0
16 | 0.97402 | -0.49904 | 0.0051545 | 0.0012918
17 | 0.97186 | -0.54176 | 0.0063678 | 0.0015959
18 | 0.97162 | -0.54655 | 0.002317 | 0.00058068
19 | 0.97284 | -0.52241 | 0.0036129 | 0.00090549
20 | 0.97264 | -0.52628 | 0 | 0
21 | 0.97376 | -0.50415 | 0 | 0
22 | 0.97341 | -0.51097 | 0 | 0
23 | 0.9732 | -0.51522 | 0.0037375 | 0.0009367
24 | 0.97735 | -0.43385 | 0 | 0
25 | 0.97761 | -0.4287 | 0 | 0
26 | 0.97722 | -0.43628 | 0.0079573 | 0.0019943
27 | 0.99856 | -0.027679 | 0 | 0
28 | 0.99859 | -0.027051 | 0 | 0
29 | 0.99849 | -0.029036 | 0.0065178 | 0.0016335
30 | 0.97249 | -0.52913 | 0 | 0
31 | 0.97219 | -0.53504 | 0.010004 | 0.0025072
32 | 0.97221 | -0.53463 | 0 | 0
33 | 0.97109 | -0.55683 | 0 | 0
34 | 0.97244 | -0.53015 | 0.010501 | 0.0026318
35 | 0.97096 | -0.55941 | 0.0094184 | 0.0023605
36 | 0.97106 | -0.55743 | 0.0077656 | 0.0019463
37 | 0.97266 | -0.52569 | 0.010759 | 0.0026965
38 | 0.9976 | -0.046072 | 0 | 0
39 | 0.99759 | -0.046364 | 0 | 0
40 | 0.99764 | -0.045364 | 0.0066533 | 0.0016675
41 | 0.97693 | -0.44173 | 0.016234 | 0.0040685
42 | 0.97697 | -0.44116 | 0 | 0
43 | 0.9779 | -0.42284 | 0.0067189 | 0.0016839
44 | 0.97476 | -0.48439 | 0.0051204 | 0.0012833
45 | 0.97855 | -0.41022 | 0 | 0
46 | 0.97877 | -0.4058 | 0 | 0
47 | 0.97794 | -0.42226 | 0.0063436 | 0.0015899
48 | 0.97309 | -0.51741 | 0 | 0
49 | 0.97317 | -0.51581 | 0.0053256 | 0.0013347
50 | 0.97283 | -0.52265 | 0.0012805 | 0.00032092
51 | 0.97286 | -0.52204 | 0.0013548 | 0.00033954
52 | 0.97414 | -0.49666 | 0 | 0
53 | 0.97259 | -0.52731 | 0.0042469 | 0.0010644
54 | 0.97263 | -0.52641 | 0 | 0
55 | 0.97312 | -0.51678 | 0.0079837 | 0.0020009
56 | 0.97769 | -0.42702 | 0.0063462 | 0.0015905
57 | 0.99827 | -0.033178 | 0.0017646 | 0.00044225
58 | 0.99917 | -0.01598 | 0.011915 | 0.0029863
59 | 0.97153 | -0.54807 | 0.012947 | 0.0032448
60 | 0.97278 | -0.52342 | 0.0046531 | 0.0011662
61 | 0.97081 | -0.56235 | 0.0077523 | 0.0019429
62 | 0.97065 | -0.56556 | 0.0097691 | 0.0024484
63 | 0.97102 | -0.55823 | 0.010789 | 0.002704
64 | 0.97123 | -0.55409 | 0.010794 | 0.0027052
65 | 0.99822 | -0.034207 | 0 | 0
66 | 0.99819 | -0.034907 | 0 | 0
67 | 0.99843 | -0.030165 | 0.0021223 | 0.0005319
68 | 0.99819 | -0.034846 | 0.002107 | 0.00052808
69 | 0.99757 | -0.046784 | 0.0021712 | 0.00054415
70 | 0.99765 | -0.045105 | 0.0017797 | 0.00044603
71 | 1 | 0 | -0.42598 | -0.1094
72 | 0.99909 | -0.017077 | 0.0018622 | 0.00046672
73 | 0.99954 | -0.0087576 | 0 | 0
74 | 0.99751 | -0.046738 | 0.0034299 | 0.00085962
75 | 0.9994 | -0.011451 | 0.0030318 | 0.00075985
76 | 0.99937 | -0.012171 | 0.00305 | 0.00076439
77 | 0.99818 | -0.035075 | 0.0017364 | 0.00043519
78 | 0.99643 | -0.067151 | 0.0043476 | 0.0010896
79 | 0.99883 | -0.022547 | 0 | 0
80 | 0.99931 | -0.013208 | 0.0026667 | 0.00066834
81 | 0.99806 | -0.037376 | 0.0019594 | 0.00049108
82 | 0.97807 | -0.4194 | 0.0039044 | 0.00097853
83 | 0.97812 | -0.41858 | 0.0025882 | 0.00064867
84 | 0.97887 | -0.40379 | 0.0015818 | 0.00039644
85 | 0.97939 | -0.39369 | 0.0057609 | 0.0014438
86 | 0.97361 | -0.50719 | 0.0063521 | 0.001592
87 | 0.97942 | -0.39311 | 0.0067242 | 0.0016852
88 | 0.98126 | -0.35726 | 0 | 0
89 | 0.9809 | -0.36436 | 0 | 0
90 | 0.98264 | -0.3305 | 0.0040402 | 0.0010126
91 | 0.98053 | -0.37142 | 0.005215 | 0.001307
92 | 0.98508 | -0.28342 | 0.0034153 | 0.00085596
93 | 0.97981 | -0.38561 | 0.0038475 | 0.00096428
94 | 0.98669 | -0.25244 | 0 | 0
95 | 0.99556 | -0.083522 | 0.0016849 | 0.00042227
96 | 0.99468 | -0.10003 | 0.0037845 | 0.00094849
97 | 0.99432 | -0.10689 | 0.0044576 | 0.0011172
98 | 0.99248 | -0.14181 | 0.00423 | 0.0010601
99 | 0.99169 | -0.15679 | 0.001688 | 0.00042306
100 | 0.98924 | -0.20346 | 0 | 0
101 | 0.98867 | -0.21433 | 0.0011989 | 0.00030047
102 | 0.98823 | -0.22282 | 0.0012802 | 0.00032085
103 | 0.97273 | -0.52455 | 0.0012891 | 0.00032308
104 | 0.97286 | -0.52204 | 0.0038363 | 0.00096147
105 | 0.99775 | -0.043198 | 0.0021402 | 0.0005364
106 | 0.99785 | -0.041394 | 0.0020243 | 0.00050733
107 | 0.99776 | -0.043118 | 0.002508 | 0.00062856
108 | 0.99782 | -0.041895 | 0.001365 | 0.00034209
109 | 0.99773 | -0.043714 | 0.0017818 | 0.00044657
110 | 0.99787 | -0.040928 | 0.00213 | 0.00053384
111 | 0.99793 | -0.039785 | 0.0018301 | 0.00045866
112 | 0.99872 | -0.024514 | 0.00093608 | 0.0002346
113 | 0.9987 | -0.024921 | 0.0010708 | 0.00026838
114 | 0.99875 | -0.023977 | 0.0028354 | 0.00071063
115 | 0.99864 | -0.026207 | 0.0022363 | 0.00056046
116 | 0.9726 | -0.52706 | 0.0014753 | 0.00036975
117 | 0.97261 | -0.52692 | 0.001313 | 0.00032907
118 | 0.9993 | -0.013432 | 0.0018401 | 0.00046117
119 | 0.97264 | -0.52639 | 0.0013028 | 0.00032651
120 | 0.97265 | -0.52605 | 0.0012683 | 0.00031787
121 | 0.97245 | -0.53015 | 0.0022894 | 0.00057378
122 | 0.97246 | -0.52978 | 0 | 0
123 | 0.97244 | -0.53021 | 0.0022078 | 0.00055333
124 | 0.97253 | -0.52851 | 0 | 0
125 | 0.97251 | -0.52894 | 0.0021162 | 0.00053037
126 | 0.97251 | -0.52893 | 0.0021892 | 0.00054866
127 | 0.97261 | -0.52687 | 0.0023657 | 0.00059291
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.072302 | -0.018148 | 0.072341 | 0.018172 | 3.9191e-05 | 2.3381e-05 | 0.11055 | 0.11055 | 0.11055 | 0.97331 | -0.51305 | 0.97388 | -0.50169 | 7.5925
1 | 0.055376 | 0.013906 | -0.055353 | -0.013893 | 2.3094e-05 | 1.3073e-05 | 0.08467 | 0.084671 | 0.084671 | 0.97331 | -0.51305 | 0.97286 | -0.52179 | 5.8153
2 | -0.072341 | -0.018172 | 0.072371 | 0.01819 | 3.0461e-05 | 1.8171e-05 | 0.11055 | 0.11055 | 0.11055 | 0.97388 | -0.50169 | 0.97433 | -0.49287 | 7.5924
3 | 0.055353 | 0.013893 | -0.055347 | -0.01389 | 5.8655e-06 | 3.3205e-06 | 0.084671 | 0.084671 | 0.084671 | 0.97286 | -0.52179 | 0.97275 | -0.52401 | 5.8153
4 | -0.15222 | -0.038256 | 0.15237 | 0.038354 | 0.00015522 | 9.7812e-05 | 0.23251 | 0.23251 | 0.23251 | 0.97433 | -0.49287 | 0.97541 | -0.47153 | 15.9689
5 | 0.079846 | 0.020066 | -0.079805 | -0.020041 | 4.1164e-05 | 2.4875e-05 | 0.12196 | 0.12196 | 0.12196 | 0.97433 | -0.49287 | 0.97378 | -0.50367 | 8.3766
6 | 0.01076 | 0.002697 | -0.010759 | -0.0026965 | 8.5934e-07 | 4.4499e-07 | 0.01646 | 0.01646 | 0.01646 | 0.97275 | -0.52401 | 0.97266 | -0.52569 | 4.522
7 | 0.044587 | 0.011193 | -0.044576 | -0.011187 | 1.0885e-05 | 5.7276e-06 | 0.068211 | 0.068212 | 0.068212 | 0.97275 | -0.52401 | 0.97249 | -0.52913 | 4.6849
8 | -0.16691 | -0.041996 | 0.16714 | 0.042146 | 0.00023805 | 0.00015039 | 0.25468 | 0.25468 | 0.25468 | 0.97541 | -0.47153 | 0.97693 | -0.44173 | 17.4916
9 | 0.061701 | 0.015504 | -0.061699 | -0.015503 | 1.3891e-06 | 8.0609e-07 | 0.094298 | 0.094298 | 0.094298 | 0.97378 | -0.50367 | 0.97376 | -0.50415 | 6.4765
10 | 0.0023172 | 0.00058025 | -0.002317 | -0.0005805 | 1.2367e-07 | -2.4531e-07 | 0.0035482 | 0.0035483 | 0.0035483 | 0.97171 | -0.54459 | 0.97166 | -0.54571 | 0.97481
11 | -0.0023172 | -0.00058025 | 0.0023173 | 0.00058008 | 8.5889e-08 | -1.7041e-07 | 0.0035482 | 0.0035481 | 0.0035482 | 0.97171 | -0.54459 | 0.97175 | -0.54381 | 0.97477
12 | 0.002317 | 0.0005805 | -0.002317 | -0.00058068 | 9.2197e-08 | -1.8285e-07 | 0.0035483 | 0.0035484 | 0.0035484 | 0.97166 | -0.54571 | 0.97162 | -0.54655 | 0.97483
13 | -0.0054303 | -0.0013603 | 0.0054308 | 0.0013604 | 5.3037e-07 | 8.5983e-08 | 0.008315 | 0.0083149 | 0.008315 | 0.97175 | -0.54381 | 0.97186 | -0.54176 | 2.2843
14 | 0.011809 | 0.0029619 | -0.011802 | -0.0029579 | 7.4338e-06 | 4.0039e-06 | 0.018064 | 0.018065 | 0.018065 | 0.9728 | -0.52312 | 0.97213 | -0.53634 | 4.9628
15 | -0.011809 | -0.0029619 | 0.01181 | 0.0029623 | 6.6337e-07 | 3.5725e-07 | 0.018064 | 0.018064 | 0.018064 | 0.9728 | -0.52312 | 0.97286 | -0.52194 | 4.9627
16 | 0.011802 | 0.0029579 | -0.011799 | -0.0029563 | 3.0492e-06 | 1.6426e-06 | 0.018065 | 0.018065 | 0.018065 | 0.97213 | -0.53634 | 0.97186 | -0.54176 | 4.9628
17 | -0.017014 | -0.0042667 | 0.017018 | 0.0042689 | 3.674e-06 | 2.1717e-06 | 0.026025 | 0.026025 | 0.026025 | 0.97286 | -0.52194 | 0.97309 | -0.51741 | 7.1497
18 | 0.013128 | 0.0032919 | -0.013123 | -0.0032888 | 5.6829e-06 | 3.1696e-06 | 0.020069 | 0.02007 | 0.02007 | 0.97341 | -0.51103 | 0.97295 | -0.52012 | 5.5136
19 | 0.019043 | 0.0047766 | -0.019033 | -0.0047706 | 9.8621e-06 | 5.9262e-06 | 0.029112 | 0.029112 | 0.029112 | 0.97341 | -0.51103 | 0.97286 | -0.5219 | 7.9977
20 | -0.032171 | -0.0080685 | 0.03219 | 0.00808 | 1.8399e-05 | 1.1523e-05 | 0.049181 | 0.049181 | 0.049181 | 0.97341 | -0.51103 | 0.97402 | -0.49904 | 13.5113
21 | 0.0079311 | 0.0019877 | -0.0079302 | -0.0019873 | 9.5362e-07 | 3.957e-07 | 0.01213 | 0.01213 | 0.01213 | 0.97295 | -0.52012 | 0.97283 | -0.52265 | 3.3324
22 | 0.0051916 | 0.0013011 | -0.0051911 | -0.001301 | 4.7392e-07 | 5.437e-08 | 0.0079399 | 0.00794 | 0.00794 | 0.97295 | -0.52012 | 0.97286 | -0.52204 | 2.1813
23 | 0.003613 | 0.00090545 | -0.0036129 | -0.00090549 | 8.7552e-08 | -3.8892e-08 | 0.0055262 | 0.0055262 | 0.0055262 | 0.97286 | -0.5219 | 0.97284 | -0.52241 | 1.5182
24 | 0.01542 | 0.0038652 | -0.015417 | -0.0038633 | 3.2135e-06 | 1.8654e-06 | 0.023586 | 0.023586 | 0.023586 | 0.97286 | -0.5219 | 0.97264 | -0.52628 | 6.4796
25 | -0.037344 | -0.0093719 | 0.037349 | 0.0093745 | 4.24e-06 | 2.6704e-06 | 0.057056 | 0.057055 | 0.057056 | 0.97402 | -0.49904 | 0.97414 | -0.49666 | 15.6746
26 | 0.0042471 | 0.0010643 | -0.0042469 | -0.0010644 | 2.0763e-07 | -2.988e-08 | 0.0064975 | 0.0064976 | 0.0064976 | 0.97264 | -0.52628 | 0.97259 | -0.52731 | 1.785
27 | 0.01117 | 0.002799 | -0.01117 | -0.0027989 | 6.9862e-08 | 3.6793e-08 | 0.017088 | 0.017088 | 0.017088 | 0.97264 | -0.52628 | 0.97263 | -0.52641 | 4.6945
28 | 0.061699 | 0.015503 | -0.061679 | -0.015491 | 2.0096e-05 | 1.1662e-05 | 0.094298 | 0.094299 | 0.094299 | 0.97376 | -0.50415 | 0.97341 | -0.51097 | 6.4766
29 | 0.061679 | 0.015491 | -0.061667 | -0.015484 | 1.2498e-05 | 7.2534e-06 | 0.094299 | 0.094299 | 0.094299 | 0.97341 | -0.51097 | 0.9732 | -0.51522 | 6.4766
30 | 0.057929 | 0.014547 | -0.057925 | -0.014545 | 4.3128e-06 | 2.4688e-06 | 0.088584 | 0.088585 | 0.088585 | 0.9732 | -0.51522 | 0.97312 | -0.51678 | 6.0841
31 | -0.0079582 | -0.0019947 | 0.0079601 | 0.0019955 | 1.9507e-06 | 8.043e-07 | 0.012116 | 0.012116 | 0.012116 | 0.97735 | -0.43385 | 0.97761 | -0.4287 | 3.3287
32 | 0.0079582 | 0.0019947 | -0.0079573 | -0.0019943 | 9.2351e-07 | 3.8086e-07 | 0.012116 | 0.012117 | 0.012117 | 0.97735 | -0.43385 | 0.97722 | -0.43628 | 3.3287
33 | -0.0079601 | -0.0019955 | 0.0079608 | 0.0019957 | 6.3814e-07 | 2.6306e-07 | 0.012116 | 0.012116 | 0.012116 | 0.97761 | -0.4287 | 0.97769 | -0.42702 | 3.3286
34 | -0.0065183 | -0.0016336 | 0.0065185 | 0.0016337 | 1.9498e-07 | 5.2693e-08 | 0.0097133 | 0.0097133 | 0.0097133 | 0.99856 | -0.027679 | 0.99859 | -0.027051 | 2.6685
35 | 0.0065183 | 0.0016336 | -0.0065178 | -0.0016335 | 4.2145e-07 | 1.1391e-07 | 0.0097133 | 0.0097133 | 0.0097133 | 0.99856 | -0.027679 | 0.99849 | -0.029036 | 2.6685
36 | 0.020244 | 0.0050779 | -0.020238 | -0.0050743 | 5.9115e-06 | 3.5568e-06 | 0.030167 | 0.030167 | 0.030167 | 0.99859 | -0.027051 | 0.99827 | -0.033178 | 8.2877
37 | -0.026762 | -0.0067116 | 0.026776 | 0.0067203 | 1.413e-05 | 8.7329e-06 | 0.03988 | 0.03988 | 0.03988 | 0.99859 | -0.027051 | 0.99917 | -0.01598 | 10.9561
38 | 0.044576 | 0.011187 | -0.044563 | -0.01118 | 1.2543e-05 | 7.6706e-06 | 0.068212 | 0.068212 | 0.068212 | 0.97249 | -0.52913 | 0.97219 | -0.53504 | 9.3697
39 | 0.034559 | 0.0086723 | -0.034538 | -0.0086588 | 2.146e-05 | 1.3481e-05 | 0.0529 | 0.0529 | 0.0529 | 0.97219 | -0.53504 | 0.97153 | -0.54807 | 14.5329
40 | 0.03475 | 0.0087253 | -0.034713 | -0.0087022 | 3.675e-05 | 2.3091e-05 | 0.053192 | 0.053192 | 0.053192 | 0.97221 | -0.53463 | 0.97109 | -0.55683 | 14.6132
41 | -0.03475 | -0.0087253 | 0.034757 | 0.0087297 | 7.4268e-06 | 4.4059e-06 | 0.053192 | 0.053192 | 0.053192 | 0.97221 | -0.53463 | 0.97244 | -0.53015 | 7.3066
42 | 0.0094195 | 0.002361 | -0.0094184 | -0.0023605 | 1.1605e-06 | 5.5897e-07 | 0.014434 | 0.014434 | 0.014434 | 0.97109 | -0.55683 | 0.97096 | -0.55941 | 3.9654
43 | 0.025293 | 0.0063411 | -0.025293 | -0.0063407 | 7.3021e-07 | 4.513e-07 | 0.038758 | 0.038758 | 0.038758 | 0.97109 | -0.55683 | 0.97106 | -0.55743 | 10.6478
44 | -0.045258 | -0.011361 | 0.045272 | 0.011369 | 1.4547e-05 | 7.7044e-06 | 0.06926 | 0.069259 | 0.06926 | 0.97244 | -0.53015 | 0.97278 | -0.52342 | 4.7569
45 | 0.017527 | 0.0043944 | -0.017523 | -0.004392 | 4.1042e-06 | 2.4391e-06 | 0.026858 | 0.026858 | 0.026858 | 0.97106 | -0.55743 | 0.97081 | -0.56235 | 7.3787
46 | 0.0021713 | 0.00054396 | -0.0021712 | -0.00054404 | 3.0218e-08 | -8.0972e-08 | 0.0032386 | 0.0032386 | 0.0032386 | 0.9976 | -0.046072 | 0.99759 | -0.046364 | 0.88973
47 | -0.0021713 | -0.00054396 | 0.0021713 | 0.00054376 | 7.3159e-08 | -1.9606e-07 | 0.0032386 | 0.0032385 | 0.0032386 | 0.9976 | -0.046072 | 0.99764 | -0.045364 | 0.88972
48 | 0.0021712 | 0.00054404 | -0.0021712 | -0.00054415 | 4.343e-08 | -1.1636e-07 | 0.0032386 | 0.0032387 | 0.0032387 | 0.99759 | -0.046364 | 0.99757 | -0.046784 | 0.88974
49 | -0.0088247 | -0.0022112 | 0.0088248 | 0.0022113 | 1.0886e-07 | 4.779e-08 | 0.013162 | 0.013162 | 0.013162 | 0.99764 | -0.045364 | 0.99765 | -0.045105 | 3.616
50 | -0.18338 | -0.046215 | 0.18357 | 0.046339 | 0.00019611 | 0.00012417 | 0.2794 | 0.2794 | 0.2794 | 0.97693 | -0.44173 | 0.97807 | -0.4194 | 19.1898
51 | -0.071376 | -0.017987 | 0.071438 | 0.018027 | 6.2616e-05 | 3.9897e-05 | 0.10875 | 0.10875 | 0.10875 | 0.97697 | -0.44116 | 0.9779 | -0.42284 | 29.8757
52 | 0.071376 | 0.017987 | -0.071228 | -0.017893 | 0.00014727 | 9.3838e-05 | 0.10875 | 0.10875 | 0.10875 | 0.97697 | -0.44116 | 0.97476 | -0.48439 | 29.8758
53 | -0.078157 | -0.019711 | 0.078221 | 0.019752 | 6.3827e-05 | 4.0699e-05 | 0.11897 | 0.11897 | 0.11897 | 0.9779 | -0.42284 | 0.97877 | -0.4058 | 32.6844
54 | 0.066108 | 0.01661 | -0.066069 | -0.016585 | 3.8704e-05 | 2.4645e-05 | 0.10093 | 0.10093 | 0.10093 | 0.97476 | -0.48439 | 0.97414 | -0.49666 | 27.7284
55 | -0.020666 | -0.0051851 | 0.02067 | 0.0051878 | 4.3585e-06 | 2.6416e-06 | 0.031427 | 0.031427 | 0.031427 | 0.97855 | -0.41022 | 0.97877 | -0.4058 | 8.6338
56 | 0.020666 | 0.0051851 | -0.020654 | -0.0051779 | 1.1857e-05 | 7.1865e-06 | 0.031427 | 0.031427 | 0.031427 | 0.97855 | -0.41022 | 0.97794 | -0.42226 | 8.6338
57 | -0.098891 | -0.02494 | 0.098951 | 0.024978 | 6.0097e-05 | 3.8373e-05 | 0.1504 | 0.1504 | 0.1504 | 0.97877 | -0.4058 | 0.97942 | -0.39311 | 41.3182
58 | 0.01431 | 0.0035881 | -0.014307 | -0.0035862 | 3.2455e-06 | 1.8482e-06 | 0.021775 | 0.021775 | 0.021775 | 0.97794 | -0.42226 | 0.97769 | -0.42702 | 5.9821
59 | -0.017018 | -0.0042689 | 0.017019 | 0.0042696 | 1.2999e-06 | 7.6835e-07 | 0.026025 | 0.026025 | 0.026025 | 0.97309 | -0.51741 | 0.97317 | -0.51581 | 7.1497
60 | -0.022345 | -0.0056044 | 0.022354 | 0.00561 | 9.1859e-06 | 5.6181e-06 | 0.034168 | 0.034168 | 0.034168 | 0.97317 | -0.51581 | 0.97361 | -0.50719 | 9.3868
61 | 0.0066497 | 0.0016664 | -0.0066491 | -0.0016662 | 6.0412e-07 | 1.9331e-07 | 0.010171 | 0.010171 | 0.010171 | 0.97283 | -0.52265 | 0.97273 | -0.52455 | 2.7943
62 | 0.0038363 | 0.00096147 | -0.0038363 | -0.00096147 | 7.4001e-10 | -2.3995e-10 | 0.0058678 | 0.0058678 | 0.0058678 | 0.97286 | -0.52204 | 0.97286 | -0.52204 | 1.612
63 | 0.028721 | 0.0072109 | -0.028706 | -0.007202 | 1.4418e-05 | 8.9792e-06 | 0.043876 | 0.043876 | 0.043876 | 0.97414 | -0.49666 | 0.97361 | -0.50719 | 12.0538
64 | 0.0023658 | 0.00059281 | -0.0023657 | -0.00059291 | 5.214e-08 | -9.8359e-08 | 0.0036193 | 0.0036194 | 0.0036194 | 0.97263 | -0.52641 | 0.97261 | -0.52687 | 0.99433
65 | 0.0088039 | 0.0022061 | -0.008803 | -0.0022057 | 8.8036e-07 | 4.0284e-07 | 0.013469 | 0.013469 | 0.013469 | 0.97263 | -0.52641 | 0.97253 | -0.52851 | 3.7002
66 | 0.049941 | 0.012544 | -0.049925 | -0.012535 | 1.5815e-05 | 8.6849e-06 | 0.076376 | 0.076377 | 0.076377 | 0.97312 | -0.51678 | 0.97278 | -0.52342 | 5.2457
67 | 0.018473 | 0.0046321 | -0.018472 | -0.0046311 | 1.6693e-06 | 9.9163e-07 | 0.027537 | 0.027537 | 0.027537 | 0.99827 | -0.033178 | 0.99818 | -0.035075 | 7.5651
68 | -0.038692 | -0.0097066 | 0.038721 | 0.0097252 | 2.9501e-05 | 1.857e-05 | 0.057625 | 0.057625 | 0.057625 | 0.99917 | -0.01598 | 1 | 0 | 15.8311
69 | 0.021591 | 0.005414 | -0.021585 | -0.0054103 | 6.1998e-06 | 3.7807e-06 | 0.03307 | 0.03307 | 0.03307 | 0.97153 | -0.54807 | 0.97123 | -0.55409 | 9.0853
70 | 0.0097706 | 0.0024491 | -0.0097691 | -0.0024484 | 1.4966e-06 | 7.3786e-07 | 0.014976 | 0.014976 | 0.014976 | 0.97081 | -0.56235 | 0.97065 | -0.56556 | 4.1143
71 | -0.010789 | -0.002704 | 0.010791 | 0.0027051 | 2.1284e-06 | 1.1053e-06 | 0.016533 | 0.016533 | 0.016533 | 0.97102 | -0.55823 | 0.97123 | -0.55409 | 4.5421
72 | 0.0096185 | 0.0024109 | -0.0096181 | -0.0024107 | 3.207e-07 | 1.5087e-07 | 0.014338 | 0.014338 | 0.014338 | 0.99822 | -0.034207 | 0.99819 | -0.034907 | 3.939
73 | -0.011726 | -0.0029387 | 0.011728 | 0.0029399 | 2.2582e-06 | 1.1875e-06 | 0.017479 | 0.017479 | 0.017479 | 0.99822 | -0.034207 | 0.99843 | -0.030165 | 4.8019
74 | 0.0021071 | 0.00052789 | -0.002107 | -0.00052808 | 6.4076e-08 | -1.854e-07 | 0.0031409 | 0.003141 | 0.003141 | 0.99822 | -0.034207 | 0.99819 | -0.034846 | 0.86291
75 | 0.0096181 | 0.0024107 | -0.0096159 | -0.0024097 | 2.2348e-06 | 1.0514e-06 | 0.014338 | 0.014338 | 0.014338 | 0.99819 | -0.034907 | 0.99793 | -0.039785 | 3.9391
76 | -0.01385 | -0.0034718 | 0.013853 | 0.0034733 | 2.6127e-06 | 1.4582e-06 | 0.020642 | 0.020642 | 0.020642 | 0.99843 | -0.030165 | 0.99864 | -0.026207 | 5.6708
77 | -0.010604 | -0.0026573 | 0.010605 | 0.0026578 | 9.6373e-07 | 4.8263e-07 | 0.015817 | 0.015817 | 0.015817 | 0.99765 | -0.045105 | 0.99775 | -0.043198 | 4.3452
78 | 0.35406 | 0.091755 | -0.35376 | -0.091566 | 0.00029542 | 0.00018847 | 0.52792 | 0.52792 | 0.52792 | 1 | 0 | 0.99909 | -0.017077 | 36.2582
79 | 0.031552 | 0.0079194 | -0.031539 | -0.0079112 | 1.3173e-05 | 8.2216e-06 | 0.046954 | 0.046954 | 0.046954 | 1 | 0 | 0.99954 | -0.0087576 | 12.8995
80 | 0.3519 | 0.0911 | -0.35139 | -0.090775 | 0.00050923 | 0.00032488 | 0.52515 | 0.52515 | 0.52515 | 0.99909 | -0.017077 | 0.99751 | -0.046738 | 36.0677
81 | 0.023981 | 0.006017 | -0.023978 | -0.0060151 | 3.0794e-06 | 1.8864e-06 | 0.035702 | 0.035702 | 0.035702 | 0.99954 | -0.0087576 | 0.9994 | -0.011451 | 9.8083
82 | 0.0075582 | 0.0018942 | -0.007557 | -0.0018938 | 1.2291e-06 | 4.4734e-07 | 0.011252 | 0.011252 | 0.011252 | 0.99954 | -0.0087576 | 0.99937 | -0.012171 | 3.0912
83 | 0.34796 | 0.089915 | -0.34761 | -0.089694 | 0.00034618 | 0.00022084 | 0.52003 | 0.52003 | 0.52003 | 0.99751 | -0.046738 | 0.99643 | -0.067151 | 35.7163
84 | 0.020946 | 0.0052552 | -0.020935 | -0.0052485 | 1.1075e-05 | 6.6903e-06 | 0.031188 | 0.031188 | 0.031188 | 0.9994 | -0.011451 | 0.99883 | -0.022547 | 8.5682
85 | 0.004507 | 0.0011294 | -0.0045068 | -0.0011294 | 2.2251e-07 | -3.0223e-08 | 0.0067107 | 0.0067108 | 0.0067108 | 0.99937 | -0.012171 | 0.99931 | -0.013208 | 1.8436
86 | 0.016735 | 0.0041959 | -0.016733 | -0.0041948 | 1.8354e-06 | 1.0719e-06 | 0.024948 | 0.024948 | 0.024948 | 0.99818 | -0.035075 | 0.99806 | -0.037376 | 6.8539
87 | 0.34327 | 0.088605 | -0.34299 | -0.08843 | 0.00027372 | 0.00017461 | 0.51354 | 0.51354 | 0.51354 | 0.99643 | -0.067151 | 0.99556 | -0.083522 | 35.2704
88 | 0.016092 | 0.0040354 | -0.016089 | -0.0040338 | 2.8065e-06 | 1.6257e-06 | 0.023974 | 0.023974 | 0.023974 | 0.99883 | -0.022547 | 0.99864 | -0.026207 | 6.5862
89 | 0.0048428 | 0.0012132 | -0.0048424 | -0.0012132 | 3.2979e-07 | -1.0073e-08 | 0.0072144 | 0.0072144 | 0.0072144 | 0.99883 | -0.022547 | 0.99875 | -0.023977 | 1.982
90 | 0.0018401 | 0.00046109 | -0.0018401 | -0.00046117 | 1.9619e-08 | -7.874e-08 | 0.00274 | 0.00274 | 0.00274 | 0.99931 | -0.013208 | 0.9993 | -0.013432 | 0.75275
91 | 0.014774 | 0.0037037 | -0.014771 | -0.0037021 | 2.8276e-06 | 1.6066e-06 | 0.022027 | 0.022027 | 0.022027 | 0.99806 | -0.037376 | 0.99785 | -0.041394 | 6.0514
92 | -0.18748 | -0.047318 | 0.18748 | 0.047322 | 7.3512e-06 | 4.6564e-06 | 0.28534 | 0.28534 | 0.28534 | 0.97807 | -0.4194 | 0.97812 | -0.41858 | 19.5977
93 | -0.19007 | -0.047971 | 0.19021 | 0.048056 | 0.0001348 | 8.541e-05 | 0.28928 | 0.28928 | 0.28928 | 0.97812 | -0.41858 | 0.97887 | -0.40379 | 19.8681
94 | -0.19179 | -0.048453 | 0.19188 | 0.048512 | 9.2891e-05 | 5.8864e-05 | 0.29168 | 0.29168 | 0.29168 | 0.97887 | -0.40379 | 0.97939 | -0.39369 | 20.0333
95 | -0.19764 | -0.049955 | 0.19772 | 0.050004 | 7.6611e-05 | 4.8575e-05 | 0.30044 | 0.30044 | 0.30044 | 0.97939 | -0.39369 | 0.97981 | -0.38561 | 20.6344
96 | -0.10568 | -0.026663 | 0.10586 | 0.026778 | 0.00018173 | 0.00011536 | 0.16061 | 0.16061 | 0.16061 | 0.97942 | -0.39311 | 0.98126 | -0.35726 | 22.0624
97 | 0.20706 | 0.052452 | -0.20699 | -0.052407 | 7.0549e-05 | 4.4766e-05 | 0.31419 | 0.31419 | 0.31419 | 0.98126 | -0.35726 | 0.9809 | -0.36436 | 21.5792
98 | -0.31292 | -0.07923 | 0.31332 | 0.079487 | 0.00040275 | 0.00025679 | 0.47481 | 0.47481 | 0.47481 | 0.98126 | -0.35726 | 0.98264 | -0.3305 | 32.6104
99 | 0.20699 | 0.052407 | -0.20692 | -0.052362 | 7.0094e-05 | 4.4478e-05 | 0.31419 | 0.31419 | 0.31419 | 0.9809 | -0.36436 | 0.98053 | -0.37142 | 21.5792
100 | -0.31736 | -0.080499 | 0.31808 | 0.080959 | 0.00072016 | 0.00045922 | 0.48092 | 0.48092 | 0.48092 | 0.98264 | -0.3305 | 0.98508 | -0.28342 | 33.0305
101 | 0.2017 | 0.051055 | -0.20157 | -0.050968 | 0.00013732 | 8.7095e-05 | 0.30628 | 0.30628 | 0.30628 | 0.98053 | -0.37142 | 0.97981 | -0.38561 | 21.0357
102 | -0.3215 | -0.081815 | 0.32198 | 0.082121 | 0.00048083 | 0.00030662 | 0.48608 | 0.48608 | 0.48608 | 0.98508 | -0.28342 | 0.98669 | -0.25244 | 33.3848
103 | -0.32198 | -0.082121 | 0.32244 | 0.082415 | 0.00046133 | 0.00029419 | 0.48608 | 0.48608 | 0.48608 | 0.98669 | -0.25244 | 0.98823 | -0.22282 | 33.3848
104 | 0.34131 | 0.088008 | -0.34103 | -0.087833 | 0.00027413 | 0.00017486 | 0.51102 | 0.51102 | 0.51102 | 0.99556 | -0.083522 | 0.99468 | -0.10003 | 35.0975
105 | 0.33725 | 0.086885 | -0.33714 | -0.086813 | 0.00011258 | 7.1805e-05 | 0.50536 | 0.50536 | 0.50536 | 0.99468 | -0.10003 | 0.99432 | -0.10689 | 34.7087
106 | 0.33268 | 0.085696 | -0.33211 | -0.085336 | 0.00056449 | 0.00036002 | 0.49869 | 0.49869 | 0.49869 | 0.99432 | -0.10689 | 0.99248 | -0.14181 | 34.2505
107 | 0.32788 | 0.084275 | -0.32765 | -0.084123 | 0.00023838 | 0.00015202 | 0.49235 | 0.49235 | 0.49235 | 0.99248 | -0.14181 | 0.99169 | -0.15679 | 33.815
108 | 0.32596 | 0.0837 | -0.32522 | -0.083231 | 0.00073672 | 0.00046982 | 0.48981 | 0.48981 | 0.48981 | 0.99169 | -0.15679 | 0.98924 | -0.20346 | 33.6411
109 | 0.32522 | 0.083231 | -0.32505 | -0.083121 | 0.00017101 | 0.00010906 | 0.48981 | 0.48981 | 0.48981 | 0.98924 | -0.20346 | 0.98867 | -0.21433 | 33.6411
110 | 0.32385 | 0.082821 | -0.32372 | -0.082736 | 0.00013296 | 8.4789e-05 | 0.48801 | 0.48801 | 0.48801 | 0.98867 | -0.21433 | 0.98823 | -0.22282 | 33.5172
111 | 0.00536 | 0.0013431 | -0.0053596 | -0.001343 | 3.8172e-07 | 5.6359e-08 | 0.0081992 | 0.0081993 | 0.0081993 | 0.97273 | -0.52455 | 0.97265 | -0.52605 | 2.2526
112 | -0.012746 | -0.0031942 | 0.012747 | 0.0031948 | 1.0952e-06 | 5.9537e-07 | 0.019008 | 0.019008 | 0.019008 | 0.99775 | -0.043198 | 0.99785 | -0.041394 | 5.2221
113 | -0.0042899 | -0.0010749 | 0.0042901 | 0.0010749 | 2.4995e-07 | -5.2736e-08 | 0.0063977 | 0.0063976 | 0.0063977 | 0.99776 | -0.043118 | 0.99782 | -0.041895 | 1.7576
114 | 0.0017819 | 0.00044635 | -0.0017818 | -0.00044657 | 5.0542e-08 | -2.1692e-07 | 0.0026573 | 0.0026574 | 0.0026574 | 0.99776 | -0.043118 | 0.99773 | -0.043714 | 0.73006
115 | -0.0056551 | -0.001417 | 0.0056553 | 0.001417 | 2.6046e-07 | 3.9116e-08 | 0.0084331 | 0.0084331 | 0.0084331 | 0.99782 | -0.041895 | 0.99787 | -0.040928 | 2.3168
116 | -0.0077854 | -0.0019508 | 0.0077858 | 0.001951 | 4.2391e-07 | 1.6173e-07 | 0.011609 | 0.011609 | 0.011609 | 0.99787 | -0.040928 | 0.99793 | -0.039785 | 3.1894
117 | 0.0010709 | 0.00026811 | -0.0010708 | -0.00026838 | 2.0767e-08 | -2.714e-07 | 0.0015954 | 0.0015955 | 0.0015955 | 0.99872 | -0.024514 | 0.9987 | -0.024921 | 0.43832
118 | -0.0020069 | -0.00050271 | 0.002007 | 0.00050254 | 5.1322e-08 | -1.6748e-07 | 0.0029901 | 0.00299 | 0.0029901 | 0.99872 | -0.024514 | 0.99875 | -0.023977 | 0.82145
119 | -0.0014753 | -0.00036975 | 0.0014753 | 0.00036969 | 9.6259e-09 | -5.6368e-08 | 0.0022571 | 0.0022571 | 0.0022571 | 0.9726 | -0.52706 | 0.97261 | -0.52692 | 0.62009
120 | -0.0027883 | -0.00069877 | 0.0027884 | 0.00069868 | 7.1108e-08 | -8.381e-08 | 0.0042659 | 0.0042659 | 0.0042659 | 0.97261 | -0.52692 | 0.97264 | -0.52639 | 1.172
121 | -0.0040912 | -0.0010252 | 0.0040913 | 0.0010252 | 6.6066e-08 | -1.3534e-08 | 0.006259 | 0.006259 | 0.006259 | 0.97264 | -0.52639 | 0.97265 | -0.52605 | 1.7195
122 | -0.0022894 | -0.00057378 | 0.0022894 | 0.0005737 | 3.9487e-08 | -8.1178e-08 | 0.0035032 | 0.0035032 | 0.0035032 | 0.97245 | -0.53015 | 0.97246 | -0.52978 | 0.96242
123 | 0.0022079 | 0.00055323 | -0.0022078 | -0.00055333 | 4.4469e-08 | -1.0044e-07 | 0.0033783 | 0.0033784 | 0.0033784 | 0.97246 | -0.52978 | 0.97244 | -0.53021 | 0.92812
124 | -0.0044973 | -0.0011269 | 0.0044976 | 0.0011269 | 2.7288e-07 | -1.6021e-08 | 0.0068815 | 0.0068814 | 0.0068815 | 0.97246 | -0.52978 | 0.97253 | -0.52851 | 1.8905
125 | 0.0021162 | 0.00053026 | -0.0021162 | -0.00053037 | 4.3738e-08 | -1.1005e-07 | 0.0032379 | 0.0032379 | 0.0032379 | 0.97253 | -0.52851 | 0.97251 | -0.52894 | 0.88954
126 | 0.0021892 | 0.00054856 | -0.0021892 | -0.00054866 | 4.4094e-08 | -1.0182e-07 | 0.0033496 | 0.0033496 | 0.0033496 | 0.97253 | -0.52851 | 0.97251 | -0.52893 | 0.92023

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42598 | 0.1094

## res_load
| p_mw | q_mvar
0 | 0.016926 | 0.004242
1 | 0.014533 | 0.0036423
2 | 0.018104 | 0.0045373
3 | 0.003113 | 0.0007802
4 | 0.0052046 | 0.0013044
5 | 0.0051545 | 0.0012918
6 | 0.0063678 | 0.0015959
7 | 0.002317 | 0.00058068
8 | 0.0036129 | 0.00090549
9 | 0.0037375 | 0.0009367
10 | 0.0079573 | 0.0019943
11 | 0.0065178 | 0.0016335
12 | 0.010004 | 0.0025072
13 | 0.010501 | 0.0026318
14 | 0.0094184 | 0.0023605
15 | 0.0077656 | 0.0019463
16 | 0.010759 | 0.0026965
17 | 0.0066533 | 0.0016675
18 | 0.016234 | 0.0040685
19 | 0.0067189 | 0.0016839
20 | 0.0051204 | 0.0012833
21 | 0.0063436 | 0.0015899
22 | 0.0053256 | 0.0013347
23 | 0.0012805 | 0.00032092
24 | 0.0013548 | 0.00033954
25 | 0.0042469 | 0.0010644
26 | 0.0079837 | 0.0020009
27 | 0.0063462 | 0.0015905
28 | 0.0017646 | 0.00044225
29 | 0.011915 | 0.0029863
30 | 0.012947 | 0.0032448
31 | 0.0046531 | 0.0011662
32 | 0.0077523 | 0.0019429
33 | 0.0097691 | 0.0024484
34 | 0.010789 | 0.002704
35 | 0.010794 | 0.0027052
36 | 0.0021223 | 0.0005319
37 | 0.002107 | 0.00052808
38 | 0.0021712 | 0.00054415
39 | 0.0017797 | 0.00044603
40 | 0.0018622 | 0.00046672
41 | 0.0034299 | 0.00085962
42 | 0.0030318 | 0.00075985
43 | 0.00305 | 0.00076439
44 | 0.0017364 | 0.00043519
45 | 0.0043476 | 0.0010896
46 | 0.0026667 | 0.00066834
47 | 0.0019594 | 0.00049108
48 | 0.0039044 | 0.00097853
49 | 0.0025882 | 0.00064867
50 | 0.0015818 | 0.00039644
51 | 0.0057609 | 0.0014438
52 | 0.0063521 | 0.001592
53 | 0.0067242 | 0.0016852
54 | 0.0040402 | 0.0010126
55 | 0.005215 | 0.001307
56 | 0.0034153 | 0.00085596
57 | 0.0038475 | 0.00096428
58 | 0.0016849 | 0.00042227
59 | 0.0037845 | 0.00094849
60 | 0.0044576 | 0.0011172
61 | 0.00423 | 0.0010601
62 | 0.001688 | 0.00042306
63 | 0.0011989 | 0.00030047
64 | 0.0012802 | 0.00032085
65 | 0.0012891 | 0.00032308
66 | 0.0038363 | 0.00096147
67 | 0.0021402 | 0.0005364
68 | 0.0020243 | 0.00050733
69 | 0.002508 | 0.00062856
70 | 0.001365 | 0.00034209
71 | 0.0017818 | 0.00044657
72 | 0.00213 | 0.00053384
73 | 0.0018301 | 0.00045866
74 | 0.00093608 | 0.0002346
75 | 0.0010708 | 0.00026838
76 | 0.0028354 | 0.00071063
77 | 0.0022363 | 0.00056046
78 | 0.0014753 | 0.00036975
79 | 0.001313 | 0.00032907
80 | 0.0018401 | 0.00046117
81 | 0.0013028 | 0.00032651
82 | 0.0012683 | 0.00031787
83 | 0.0022894 | 0.00057378
84 | 0.0022078 | 0.00055333
85 | 0.0021162 | 0.00053037
86 | 0.0021892 | 0.00054866
87 | 0.0023657 | 0.00059291

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1