## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_194-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_194-9_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_194-9_0_4_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_194-9_0_4_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_194-9_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_194-9_0_4_node_38 | 0.4 | n |  | TRUE
6 | bus_LV_194-9_0_4_node_39 | 0.4 | n |  | TRUE
7 | bus_LV_194-9_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_194-9_0_4_node_46 | 0.4 | n |  | TRUE
9 | bus_LV_194-9_0_4_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_194-9_0_4_node_81 | 0.4 | n |  | TRUE
11 | bus_LV_194-9_0_4_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_194-9_0_4_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_194-9_0_4_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_194-9_0_4_node_70 | 0.4 | n |  | TRUE
15 | bus_LV_194-9_0_4_node_44 | 0.4 | n |  | TRUE
16 | bus_LV_194-9_0_4_node_84 | 0.4 | n |  | TRUE
17 | bus_LV_194-9_0_4_node_72 | 0.4 | n |  | TRUE
18 | bus_LV_194-9_0_4_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_194-9_0_4_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_194-9_0_4_node_41 | 0.4 | n |  | TRUE
21 | bus_LV_194-9_0_4_node_77 | 0.4 | n |  | TRUE
22 | bus_LV_194-9_0_4_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_194-9_0_4_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_194-9_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_194-9_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_194-9_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_194-9_0_4_node_53 | 0.4 | n |  | TRUE
28 | bus_LV_194-9_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_194-9_0_4_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_194-9_0_4_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_194-9_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_194-9_0_4_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_194-9_0_4_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_194-9_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_194-9_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_194-9_0_4_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_194-9_0_4_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_194-9_0_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_194-9_0_4_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_194-9_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_194-9_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_194-9_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_194-9_0_4_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_194-9_0_4_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_194-9_0_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_194-9_0_4_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_194-9_0_4_node_82 | 0.4 | n |  | TRUE
48 | bus_LV_194-9_0_4_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_194-9_0_4_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_194-9_0_4_node_61 | 0.4 | n |  | TRUE
51 | bus_LV_194-9_0_4_node_62 | 0.4 | n |  | TRUE
52 | bus_LV_194-9_0_4_node_83 | 0.4 | n |  | TRUE
53 | bus_LV_194-9_0_4_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_194-9_0_4_node_78 | 0.4 | n |  | TRUE
55 | bus_LV_194-9_0_4_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_194-9_0_4_node_67 | 0.4 | n |  | TRUE
57 | bus_LV_194-9_0_4_node_71 | 0.4 | n |  | TRUE
58 | bus_LV_194-9_0_4_node_73 | 0.4 | n |  | TRUE
59 | bus_LV_194-9_0_4_node_66 | 0.4 | n |  | TRUE
60 | bus_LV_194-9_0_4_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_194-9_0_4_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_194-9_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_194-9_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_194-9_0_4_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_194-9_0_4_node_69 | 0.4 | n |  | TRUE
66 | bus_LV_194-9_0_4_node_65 | 0.4 | n |  | TRUE
67 | bus_LV_194-9_0_4_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_194-9_0_4_node_75 | 0.4 | n |  | TRUE
69 | bus_LV_194-9_0_4_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_194-9_0_4_node_68 | 0.4 | n |  | TRUE
71 | bus_LV_194-9_0_4_node_80 | 0.4 | n |  | TRUE
72 | bus_LV_194-9_0_4_node_79 | 0.4 | n |  | TRUE
73 | bus_LV_194-9_0_4_node_74 | 0.4 | n |  | TRUE
74 | bus_MV_365_0_node_44 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_194-9_0_4_load_0 | 0 | 0.0092792 | 0.0023256 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_194-9_0_4_load_7 | 2 | 0.0069525 | 0.0017425 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_194-9_0_4_load_8 | 3 | 0.0094517 | 0.0023688 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_194-9_0_4_load_38 | 5 | 0.0071924 | 0.0018026 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_194-9_0_4_load_39 | 6 | 0.015311 | 0.0038372 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_194-9_0_4_load_46 | 8 | 0.0076307 | 0.0019124 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_194-9_0_4_load_43 | 9 | 0.0090994 | 0.0022805 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_194-9_0_4_load_81 | 10 | 0.0069605 | 0.0017445 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_194-9_0_4_load_45 | 13 | 0.010229 | 0.0025637 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_194-9_0_4_load_70 | 14 | 0.022794 | 0.0057127 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_194-9_0_4_load_84 | 16 | 0.0046891 | 0.0011752 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_194-9_0_4_load_33 | 18 | 0.0056127 | 0.0014067 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_194-9_0_4_load_77 | 21 | 0.013034 | 0.0032666 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_194-9_0_4_load_9 | 22 | 0.0058055 | 0.001455 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_194-9_0_4_load_10 | 23 | 0.0058772 | 0.001473 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_194-9_0_4_load_53 | 27 | 0.006668 | 0.0016712 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_194-9_0_4_load_52 | 30 | 0.0056141 | 0.001407 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_194-9_0_4_load_18 | 31 | 0.0056161 | 0.0014075 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_194-9_0_4_load_36 | 32 | 0.0073798 | 0.0018496 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_194-9_0_4_load_54 | 33 | 0.0061882 | 0.0015509 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_194-9_0_4_load_32 | 34 | 0.0040578 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_194-9_0_4_load_30 | 35 | 0.0042183 | 0.0010572 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_194-9_0_4_load_55 | 37 | 0.0055072 | 0.0013802 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_194-9_0_4_load_21 | 39 | 0.0056468 | 0.0014152 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_194-9_0_4_load_57 | 43 | 0.0050621 | 0.0012687 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_194-9_0_4_load_42 | 45 | 0.013734 | 0.003442 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_194-9_0_4_load_24 | 46 | 0.015075 | 0.0037781 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_194-9_0_4_load_82 | 47 | 0.028012 | 0.0070204 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_194-9_0_4_load_61 | 50 | 0.011514 | 0.0028856 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_194-9_0_4_load_83 | 52 | 0.016929 | 0.0042428 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_194-9_0_4_load_59 | 53 | 0.0048784 | 0.0012226 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_194-9_0_4_load_78 | 54 | 0.01425 | 0.0035714 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_194-9_0_4_load_47 | 55 | 0.0091008 | 0.0022809 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_194-9_0_4_load_71 | 57 | 0.016303 | 0.004086 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_194-9_0_4_load_73 | 58 | 0.012027 | 0.0030142 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_194-9_0_4_load_48 | 61 | 0.0041722 | 0.0010456 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_194-9_0_4_load_60 | 64 | 0.005 | 0.0012531 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_194-9_0_4_load_69 | 65 | 0.016914 | 0.0042392 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_194-9_0_4_load_75 | 68 | 0.010769 | 0.0026988 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_194-9_0_4_load_68 | 70 | 0.021228 | 0.0053203 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_194-9_0_4_load_80 | 71 | 0.0092027 | 0.0023064 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_194-9_0_4_load_79 | 72 | 0.010207 | 0.0025582 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_194-9_0_4_line_0 |  | 0 | 1 | 0.013975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_194-9_0_4_line_1 |  | 1 | 2 | 0.026423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_194-9_0_4_line_2 |  | 1 | 3 | 0.007746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_194-9_0_4_line_3 |  | 2 | 10 | 0.02133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_194-9_0_4_line_4 |  | 4 | 5 | 0.017903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_194-9_0_4_line_5 |  | 4 | 6 | 0.043706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_194-9_0_4_line_6 |  | 5 | 11 | 0.0078118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_194-9_0_4_line_7 |  | 6 | 12 | 0.0091428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_194-9_0_4_line_8 |  | 7 | 8 | 0.03088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_194-9_0_4_line_9 |  | 7 | 9 | 0.016885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_194-9_0_4_line_10 |  | 8 | 10 | 0.021148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_194-9_0_4_line_11 |  | 9 | 15 | 0.0068567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_194-9_0_4_line_12 |  | 11 | 32 | 0.012232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_194-9_0_4_line_13 |  | 12 | 20 | 0.021944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_194-9_0_4_line_14 |  | 12 | 45 | 0.0090826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_194-9_0_4_line_15 |  | 13 | 14 | 0.020639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_194-9_0_4_line_16 |  | 14 | 57 | 0.012858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_194-9_0_4_line_17 |  | 15 | 55 | 0.012385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_194-9_0_4_line_18 |  | 16 | 17 | 0.025545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_194-9_0_4_line_19 |  | 17 | 57 | 0.019641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_194-9_0_4_line_20 |  | 17 | 67 | 0.046509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_194-9_0_4_line_21 |  | 18 | 19 | 0.020399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_194-9_0_4_line_22 |  | 19 | 36 | 0.008669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_194-9_0_4_line_23 |  | 19 | 32 | 0.036962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_194-9_0_4_line_24 |  | 20 | 21 | 0.017115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_194-9_0_4_line_25 |  | 21 | 54 | 0.021321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_194-9_0_4_line_26 |  | 22 | 23 | 0.019487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_194-9_0_4_line_27 |  | 23 | 24 | 0.0015941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_194-9_0_4_line_28 |  | 24 | 25 | 0.022909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_194-9_0_4_line_29 |  | 25 | 31 | 0.021776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_194-9_0_4_line_30 |  | 25 | 26 | 0.017782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_194-9_0_4_line_31 |  | 26 | 27 | 0.030786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_194-9_0_4_line_32 |  | 27 | 33 | 0.019674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_194-9_0_4_line_33 |  | 28 | 29 | 0.005796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_194-9_0_4_line_34 |  | 28 | 30 | 0.018881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_194-9_0_4_line_35 |  | 29 | 35 | 0.0094104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_194-9_0_4_line_36 |  | 29 | 34 | 0.0071572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_194-9_0_4_line_37 |  | 30 | 36 | 0.014123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_194-9_0_4_line_38 |  | 31 | 38 | 0.0023793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_194-9_0_4_line_39 |  | 33 | 37 | 0.02228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_194-9_0_4_line_40 |  | 38 | 39 | 0.012746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_194-9_0_4_line_41 |  | 39 | 40 | 0.042933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_194-9_0_4_line_42 |  | 40 | 41 | 0.030054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_194-9_0_4_line_43 |  | 40 | 42 | 0.012726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_194-9_0_4_line_44 |  | 41 | 46 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_194-9_0_4_line_45 |  | 42 | 47 | 0.017948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_194-9_0_4_line_46 |  | 43 | 44 | 0.0020799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_194-9_0_4_line_47 |  | 44 | 49 | 0.020176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_194-9_0_4_line_48 |  | 44 | 48 | 0.016167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_194-9_0_4_line_49 |  | 46 | 48 | 0.0025458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_194-9_0_4_line_50 |  | 47 | 52 | 0.030889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_194-9_0_4_line_51 |  | 49 | 53 | 0.0045141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_194-9_0_4_line_52 |  | 50 | 51 | 0.018311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_194-9_0_4_line_53 |  | 51 | 69 | 0.012926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_194-9_0_4_line_54 |  | 52 | 71 | 0.022004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_194-9_0_4_line_55 |  | 53 | 63 | 0.0028754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_194-9_0_4_line_56 |  | 54 | 72 | 0.021138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_194-9_0_4_line_57 |  | 55 | 56 | 0.021516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_194-9_0_4_line_58 |  | 56 | 58 | 0.021453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_194-9_0_4_line_59 |  | 56 | 59 | 0.057402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_194-9_0_4_line_60 |  | 56 | 60 | 0.041256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_194-9_0_4_line_61 |  | 58 | 73 | 0.012155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_194-9_0_4_line_62 |  | 59 | 65 | 0.013528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_194-9_0_4_line_63 |  | 60 | 71 | 0.017481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_194-9_0_4_line_64 |  | 60 | 72 | 0.028921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_194-9_0_4_line_65 |  | 61 | 62 | 0.016628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_194-9_0_4_line_66 |  | 62 | 63 | 0.062292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_194-9_0_4_line_67 |  | 63 | 64 | 0.040284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_194-9_0_4_line_68 |  | 65 | 66 | 0.012698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_194-9_0_4_line_69 |  | 66 | 70 | 0.013308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_194-9_0_4_line_70 |  | 67 | 68 | 0.024521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_194-9_0_4_line_71 |  | 68 | 73 | 0.010824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_194-9_0_4_line_72 |  | 69 | 70 | 0.0024835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_194-9_0_4_trafo_78 | 0.63 MVA 20/0.4 kV | 74 | 54 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2693788.8207 | 1247366.5077 | 2693775.0011 | 1247368.5836
1 | 2693788.8207 | 1247366.5077 | 2693793.492 | 1247392.514
2 | 2693788.8207 | 1247366.5077 | 2693796.4064 | 1247364.9398
3 | 2693793.492 | 1247392.514 | 2693797.2629 | 1247413.5084
4 | 2693772.1605 | 1247337.1329 | 2693769.7391 | 1247319.3944
5 | 2693772.1605 | 1247337.1329 | 2693786.4118 | 1247334.4785 | 2693800.2829 | 1247331.9849 | 2693807.4001 | 1247330.9522 | 2693815.237 | 1247329.7752
6 | 2693770.4655 | 1247312.9655 | 2693768.8976 | 1247313.2298 | 2693769.7391 | 1247319.3944
7 | 2693824.2784 | 1247328.4173 | 2693815.237 | 1247329.7752
8 | 2693806.461 | 1247464.7171 | 2693801.0017 | 1247434.3237
9 | 2693806.461 | 1247464.7171 | 2693823.1698 | 1247462.285
10 | 2693797.2629 | 1247413.5084 | 2693801.0017 | 1247434.3237
11 | 2693829.955 | 1247461.2973 | 2693823.1698 | 1247462.285
12 | 2693770.4655 | 1247312.9655 | 2693768.8486 | 1247300.8411
13 | 2693824.2784 | 1247328.4173 | 2693831.3068 | 1247349.211
14 | 2693824.2784 | 1247328.4173 | 2693833.292 | 1247327.3004
15 | 2693826.7439 | 1247499.509 | 2693826.7439 | 1247499.509 | 2693829.6332 | 1247519.9449
16 | 2693829.6332 | 1247519.9449 | 2693831.3496 | 1247532.0845 | 2693831.7699 | 1247532.5096
17 | 2693829.955 | 1247461.2973 | 2693842.1616 | 1247459.2045
18 | 2693845.5798 | 1247546.4762 | 2693825.8713 | 1247562.7287
19 | 2693845.5798 | 1247546.4762 | 2693831.7699 | 1247532.5096
20 | 2693845.5798 | 1247546.4762 | 2693877.0888 | 1247520.6107 | 2693881.5278 | 1247516.9671
21 | 2693763.9624 | 1247264.2033 | 2693743.8749 | 1247267.7531
22 | 2693763.9624 | 1247264.2033 | 2693772.5503 | 1247262.8492
23 | 2693763.9624 | 1247264.2033 | 2693768.8486 | 1247300.8411
24 | 2693831.3068 | 1247349.211 | 2693834.0741 | 1247366.1008
25 | 2693834.0741 | 1247366.1008 | 2693837.5214 | 1247387.1411
26 | 2693799.3441 | 1247274.2404 | 2693802.2811 | 1247293.5052
27 | 2693802.5214 | 1247295.081 | 2693802.2811 | 1247293.5052
28 | 2693802.5214 | 1247295.081 | 2693825.3062 | 1247292.1281
29 | 2693825.3062 | 1247292.1281 | 2693837.4463 | 1247285.8932 | 2693845.1428 | 1247283.2798
30 | 2693825.3062 | 1247292.1281 | 2693822.6914 | 1247274.54
31 | 2693822.6914 | 1247274.54 | 2693835.5263 | 1247259.2536 | 2693833.8482 | 1247248.5589
32 | 2693833.8482 | 1247248.5589 | 2693830.7985 | 1247229.1225
33 | 2693767.6221 | 1247224.3641 | 2693768.3545 | 1247230.1134
34 | 2693768.3545 | 1247230.1134 | 2693770.7549 | 1247248.841
35 | 2693767.6221 | 1247224.3641 | 2693758.3425 | 1247225.9279
36 | 2693767.6221 | 1247224.3641 | 2693774.6352 | 1247222.9352
37 | 2693772.5503 | 1247262.8492 | 2693770.7549 | 1247248.841
38 | 2693847.3958 | 1247282.5147 | 2693845.1428 | 1247283.2798
39 | 2693830.7985 | 1247229.1225 | 2693830.7985 | 1247229.1225 | 2693833.6397 | 1247228.6004 | 2693831.5048 | 1247209.3268
40 | 2693847.3958 | 1247282.5147 | 2693859.9441 | 1247280.0781
41 | 2693866.3196 | 1247322.5336 | 2693859.9441 | 1247280.0781
42 | 2693866.3196 | 1247322.5336 | 2693867.8953 | 1247322.2584 | 2693896.2079 | 1247319.4155
43 | 2693866.3196 | 1247322.5336 | 2693867.8953 | 1247322.2584 | 2693869.8066 | 1247333.2192
44 | 2693896.2079 | 1247319.4155 | 2693894.2745 | 1247301.4406
45 | 2693869.8066 | 1247333.2192 | 2693868.05 | 1247339.6741 | 2693869.4731 | 1247350.8423
46 | 2693892.5954 | 1247282.8082 | 2693892.2772 | 1247280.7528
47 | 2693907.1181 | 1247268.7608 | 2693892.5954 | 1247282.8082
48 | 2693894.0022 | 1247298.9094 | 2693893.0061 | 1247285.9727 | 2693892.5954 | 1247282.8082
49 | 2693894.0022 | 1247298.9094 | 2693894.2745 | 1247301.4406
50 | 2693869.4731 | 1247350.8423 | 2693870.4352 | 1247358.3928 | 2693866.4574 | 1247364.39 | 2693868.1715 | 1247380.3798
51 | 2693907.1181 | 1247268.7608 | 2693910.5245 | 1247265.7988
52 | 2693925.9072 | 1247395.4216 | 2693930.677 | 1247394.7411 | 2693928.6548 | 1247381.4007
53 | 2693925.9072 | 1247395.4216 | 2693927.8803 | 1247408.1959
54 | 2693868.1715 | 1247380.3798 | 2693868.6819 | 1247385.141 | 2693865.9373 | 1247390.068 | 2693867.633 | 1247401.5184
55 | 2693912.6944 | 1247263.912 | 2693910.5245 | 1247265.7988
56 | 2693837.5214 | 1247387.1411 | 2693840.9391 | 1247408.0009
57 | 2693862.4158 | 1247453.1048 | 2693856.7916 | 1247456.6963 | 2693842.1616 | 1247459.2045
58 | 2693862.4158 | 1247453.1048 | 2693870.3238 | 1247462.2258 | 2693871.7102 | 1247471.504
59 | 2693917.42 | 1247440.9552 | 2693901.4766 | 1247441.7144 | 2693881.6195 | 1247444.4243 | 2693873.2136 | 1247446.226 | 2693862.4158 | 1247453.1048
60 | 2693867.0408 | 1247418.6406 | 2693870.1602 | 1247439.1723 | 2693873.2136 | 1247446.226 | 2693862.4158 | 1247453.1048
61 | 2693873.5065 | 1247483.5257 | 2693871.7102 | 1247471.504
62 | 2693917.42 | 1247440.9552 | 2693918.5163 | 1247438.9822 | 2693921.6919 | 1247435.4631 | 2693924.0283 | 1247432.9427 | 2693924.8792 | 1247432.6337 | 2693927.0804 | 1247432.4462
63 | 2693867.0408 | 1247418.6406 | 2693869.0355 | 1247410.9885 | 2693867.633 | 1247401.5184
64 | 2693867.0408 | 1247418.6406 | 2693841.1778 | 1247409.4576 | 2693840.9391 | 1247408.0009
65 | 2693965.5798 | 1247291.6487 | 2693966.461 | 1247299.4353 | 2693965.4084 | 1247299.5965 | 2693963.6744 | 1247299.8581 | 2693960.5091 | 1247300.3416 | 2693958.9491 | 1247300.5838 | 2693957.77 | 1247300.7634
66 | 2693912.6944 | 1247263.912 | 2693923.4781 | 1247266.0511 | 2693945.1725 | 1247271.3766 | 2693947.8838 | 1247273.321 | 2693957.4337 | 1247285.148 | 2693965.5798 | 1247291.6487
67 | 2693912.6944 | 1247263.912 | 2693915.8249 | 1247260.3811 | 2693927.8572 | 1247250.4753 | 2693923.4224 | 1247230.9937
68 | 2693927.0804 | 1247432.4462 | 2693924.9673 | 1247419.9254
69 | 2693924.9673 | 1247419.9254 | 2693929.6104 | 1247419.1428 | 2693928.268 | 1247410.6489
70 | 2693881.5278 | 1247516.9671 | 2693875.7166 | 1247508.5242 | 2693874.4597 | 1247494.3077
71 | 2693873.5065 | 1247483.5257 | 2693874.4597 | 1247494.3077
72 | 2693927.8803 | 1247408.1959 | 2693928.268 | 1247410.6489

## bus_geodata
| x | y | coords
0 | 2693775.0011 | 1247368.5836
1 | 2693788.8207 | 1247366.5077
2 | 2693793.492 | 1247392.514
3 | 2693796.4064 | 1247364.9398
4 | 2693772.1605 | 1247337.1329
5 | 2693769.7391 | 1247319.3944
6 | 2693815.237 | 1247329.7752
7 | 2693806.461 | 1247464.7171
8 | 2693801.0017 | 1247434.3237
9 | 2693823.1698 | 1247462.285
10 | 2693797.2629 | 1247413.5084
11 | 2693770.4655 | 1247312.9655
12 | 2693824.2784 | 1247328.4173
13 | 2693826.7439 | 1247499.509
14 | 2693829.6332 | 1247519.9449
15 | 2693829.955 | 1247461.2973
16 | 2693825.8713 | 1247562.7287
17 | 2693845.5798 | 1247546.4762
18 | 2693743.8749 | 1247267.7531
19 | 2693763.9624 | 1247264.2033
20 | 2693831.3068 | 1247349.211
21 | 2693834.0741 | 1247366.1008
22 | 2693799.3441 | 1247274.2403
23 | 2693802.2811 | 1247293.5052
24 | 2693802.5214 | 1247295.081
25 | 2693825.3062 | 1247292.1281
26 | 2693822.6914 | 1247274.54
27 | 2693833.8482 | 1247248.5589
28 | 2693768.3545 | 1247230.1134
29 | 2693767.6221 | 1247224.3641
30 | 2693770.7549 | 1247248.841
31 | 2693845.1428 | 1247283.2798
32 | 2693768.8486 | 1247300.8411
33 | 2693830.7985 | 1247229.1225
34 | 2693774.6352 | 1247222.9352
35 | 2693758.3425 | 1247225.9279
36 | 2693772.5503 | 1247262.8492
37 | 2693831.5048 | 1247209.3268
38 | 2693847.3958 | 1247282.5147
39 | 2693859.9441 | 1247280.0781
40 | 2693866.3197 | 1247322.5336
41 | 2693896.2079 | 1247319.4155
42 | 2693869.8066 | 1247333.2192
43 | 2693892.2772 | 1247280.7528
44 | 2693892.5954 | 1247282.8082
45 | 2693833.292 | 1247327.3004
46 | 2693894.2745 | 1247301.4406
47 | 2693869.4731 | 1247350.8423
48 | 2693894.0022 | 1247298.9094
49 | 2693907.1181 | 1247268.7608
50 | 2693928.6547 | 1247381.4007
51 | 2693925.9072 | 1247395.4216
52 | 2693868.1715 | 1247380.3798
53 | 2693910.5245 | 1247265.7988
54 | 2693837.5214 | 1247387.1411
55 | 2693842.1616 | 1247459.2045
56 | 2693862.4158 | 1247453.1048
57 | 2693831.7699 | 1247532.5096
58 | 2693871.7102 | 1247471.504
59 | 2693917.42 | 1247440.9552
60 | 2693867.0408 | 1247418.6406
61 | 2693957.77 | 1247300.7634
62 | 2693965.5798 | 1247291.6487
63 | 2693912.6944 | 1247263.912
64 | 2693923.4224 | 1247230.9937
65 | 2693927.0804 | 1247432.4462
66 | 2693924.9673 | 1247419.9254
67 | 2693881.5278 | 1247516.9671
68 | 2693874.4597 | 1247494.3077
69 | 2693927.8803 | 1247408.1959
70 | 2693928.268 | 1247410.6489
71 | 2693867.633 | 1247401.5184
72 | 2693840.9391 | 1247408.0009
73 | 2693873.5065 | 1247483.5257
74 | 2693831.3068 | 1247349.211

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98609 | -0.26747 | 0.0092792 | 0.0023256
1 | 0.98621 | -0.26515 | 0 | 0
2 | 0.98666 | -0.25628 | 0.0069525 | 0.0017425
3 | 0.98614 | -0.26646 | 0.0094517 | 0.0023688
4 | 0.9945 | -0.10569 | 0 | 0
5 | 0.99394 | -0.11645 | 0.0071924 | 0.0018026
6 | 0.99586 | -0.079478 | 0.015311 | 0.0038372
7 | 0.98894 | -0.21194 | 0 | 0
8 | 0.9878 | -0.23414 | 0.0076307 | 0.0019124
9 | 0.98957 | -0.19983 | 0.0090994 | 0.0022805
10 | 0.98717 | -0.24648 | 0.0069605 | 0.0017445
11 | 0.99375 | -0.12016 | 0 | 0
12 | 0.99627 | -0.071545 | 0 | 0
13 | 0.9837 | -0.31389 | 0.010229 | 0.0025637
14 | 0.98389 | -0.31008 | 0.022794 | 0.0057127
15 | 0.98988 | -0.19381 | 0 | 0
16 | 0.98506 | -0.28718 | 0.0046891 | 0.0011752
17 | 0.98517 | -0.28503 | 0 | 0
18 | 0.99269 | -0.14073 | 0.0056127 | 0.0014067
19 | 0.99279 | -0.1387 | 0 | 0
20 | 0.99753 | -0.04725 | 0 | 0
21 | 0.99852 | -0.028345 | 0.013034 | 0.0032666
22 | 0.98239 | -0.33922 | 0.0058055 | 0.001455
23 | 0.98249 | -0.33717 | 0.0058772 | 0.001473
24 | 0.98251 | -0.33684 | 0 | 0
25 | 0.98276 | -0.33201 | 0 | 0
26 | 0.98245 | -0.3379 | 0 | 0
27 | 0.98193 | -0.34812 | 0.006668 | 0.0016712
28 | 0.99236 | -0.14707 | 0 | 0
29 | 0.99232 | -0.14792 | 0 | 0
30 | 0.9925 | -0.1443 | 0.0056141 | 0.001407
31 | 0.98336 | -0.3202 | 0.0056161 | 0.0014075
32 | 0.99345 | -0.12596 | 0.0073798 | 0.0018496
33 | 0.98172 | -0.35228 | 0.0061882 | 0.0015509
34 | 0.99229 | -0.14843 | 0.0040578 | 0.001017
35 | 0.99228 | -0.14862 | 0.0042183 | 0.0010572
36 | 0.99268 | -0.14083 | 0 | 0
37 | 0.98161 | -0.3545 | 0.0055072 | 0.0013802
38 | 0.98344 | -0.31868 | 0 | 0
39 | 0.98386 | -0.31049 | 0.0056468 | 0.0014152
40 | 0.98549 | -0.2786 | 0 | 0
41 | 0.98455 | -0.29706 | 0 | 0
42 | 0.98638 | -0.26137 | 0 | 0
43 | 0.98364 | -0.31481 | 0.0050621 | 0.0012687
44 | 0.98365 | -0.31462 | 0 | 0
45 | 0.99616 | -0.073735 | 0.013734 | 0.003442
46 | 0.98398 | -0.30818 | 0.015075 | 0.0037781
47 | 0.98763 | -0.23712 | 0.028012 | 0.0070204
48 | 0.98393 | -0.30906 | 0 | 0
49 | 0.98339 | -0.31973 | 0 | 0
50 | 0.98723 | -0.24539 | 0.011514 | 0.0028856
51 | 0.98742 | -0.24162 | 0 | 0
52 | 0.99058 | -0.18015 | 0.016929 | 0.0042428
53 | 0.98333 | -0.32088 | 0.0048784 | 0.0012226
54 | 1 | 0 | -0.40693 | -0.10324
55 | 0.99044 | -0.18294 | 0.0091008 | 0.0022809
56 | 0.9916 | -0.16061 | 0 | 0
57 | 0.98428 | -0.30244 | 0.016303 | 0.004086
58 | 0.99008 | -0.18986 | 0.012027 | 0.0030142
59 | 0.98898 | -0.21127 | 0 | 0
60 | 0.9951 | -0.093212 | 0 | 0
61 | 0.983 | -0.32729 | 0.0041722 | 0.0010456
62 | 0.98306 | -0.32604 | 0 | 0
63 | 0.9833 | -0.32135 | 0 | 0
64 | 0.98312 | -0.32499 | 0.005 | 0.0012531
65 | 0.98836 | -0.22325 | 0.016914 | 0.0042392
66 | 0.98798 | -0.23067 | 0 | 0
67 | 0.98749 | -0.24002 | 0 | 0
68 | 0.98871 | -0.21637 | 0.010769 | 0.0026988
69 | 0.98756 | -0.23896 | 0 | 0
70 | 0.98758 | -0.23845 | 0.021228 | 0.0053203
71 | 0.99302 | -0.13319 | 0.0092027 | 0.0023064
72 | 0.99789 | -0.039976 | 0.010207 | 0.0025582
73 | 0.98936 | -0.20387 | 0 | 0
74 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0092792 | -0.0023256 | 0.0092802 | 0.0023261 | 1.0275e-06 | 4.7929e-07 | 0.014002 | 0.014002 | 0.014002 | 0.98609 | -0.26747 | 0.98621 | -0.26515 | 3.8468
1 | -0.018732 | -0.0046952 | 0.01874 | 0.0046999 | 7.9155e-06 | 4.7286e-06 | 0.028264 | 0.028264 | 0.028264 | 0.98621 | -0.26515 | 0.98666 | -0.25628 | 7.7649
2 | 0.0094523 | 0.0023691 | -0.0094517 | -0.0023688 | 5.9083e-07 | 2.793e-07 | 0.014262 | 0.014262 | 0.014262 | 0.98621 | -0.26515 | 0.98614 | -0.26646 | 3.9181
3 | -0.025693 | -0.0064424 | 0.025705 | 0.0064498 | 1.201e-05 | 7.4141e-06 | 0.038749 | 0.038749 | 0.038749 | 0.98666 | -0.25628 | 0.98717 | -0.24648 | 10.6454
4 | 0.034123 | 0.0085683 | -0.034105 | -0.0085574 | 1.7504e-05 | 1.0971e-05 | 0.051062 | 0.051062 | 0.051062 | 0.9945 | -0.10569 | 0.99394 | -0.11645 | 14.0279
5 | -0.034123 | -0.0085683 | 0.034165 | 0.0085951 | 4.2733e-05 | 2.6781e-05 | 0.051062 | 0.051061 | 0.051062 | 0.9945 | -0.10569 | 0.99586 | -0.079478 | 14.0279
6 | 0.026913 | 0.0067548 | -0.026908 | -0.0067518 | 4.7562e-06 | 2.9427e-06 | 0.040294 | 0.040294 | 0.040294 | 0.99394 | -0.11645 | 0.99375 | -0.12016 | 11.0698
7 | -0.049476 | -0.012432 | 0.049495 | 0.012444 | 1.8744e-05 | 1.1877e-05 | 0.073939 | 0.073939 | 0.073939 | 0.99586 | -0.079478 | 0.99627 | -0.071545 | 20.3128
8 | 0.040358 | 0.010146 | -0.040315 | -0.010119 | 4.2717e-05 | 2.6943e-05 | 0.060736 | 0.060736 | 0.060736 | 0.98894 | -0.21194 | 0.9878 | -0.23414 | 16.6857
9 | -0.040358 | -0.010146 | 0.040381 | 0.01016 | 2.3357e-05 | 1.4732e-05 | 0.060736 | 0.060736 | 0.060736 | 0.98894 | -0.21194 | 0.98957 | -0.19983 | 16.6857
10 | 0.032685 | 0.0082063 | -0.032665 | -0.0081942 | 1.9229e-05 | 1.2036e-05 | 0.049241 | 0.049241 | 0.049241 | 0.9878 | -0.23414 | 0.98717 | -0.24648 | 13.5278
11 | -0.049481 | -0.012441 | 0.049495 | 0.01245 | 1.424e-05 | 9.0255e-06 | 0.074419 | 0.074419 | 0.074419 | 0.98957 | -0.19983 | 0.98988 | -0.19381 | 20.4447
12 | 0.026908 | 0.0067518 | -0.0269 | -0.0067472 | 7.4473e-06 | 4.6079e-06 | 0.040294 | 0.040294 | 0.040294 | 0.99375 | -0.12016 | 0.99345 | -0.12596 | 11.0698
13 | -0.06323 | -0.015887 | 0.063303 | 0.015934 | 7.3414e-05 | 4.6699e-05 | 0.094453 | 0.094453 | 0.094453 | 0.99627 | -0.071545 | 0.99753 | -0.04725 | 25.9487
14 | 0.013735 | 0.0034428 | -0.013734 | -0.003442 | 1.4334e-06 | 7.9912e-07 | 0.020515 | 0.020515 | 0.020515 | 0.99627 | -0.071545 | 0.99616 | -0.073735 | 5.6359
15 | -0.010229 | -0.0025637 | 0.010231 | 0.0025646 | 1.8531e-06 | 9.239e-07 | 0.015473 | 0.015473 | 0.015473 | 0.9837 | -0.31389 | 0.98389 | -0.31008 | 4.2509
16 | -0.033025 | -0.0082773 | 0.033037 | 0.0082848 | 1.2029e-05 | 7.5349e-06 | 0.049946 | 0.049946 | 0.049946 | 0.98389 | -0.31008 | 0.98428 | -0.30244 | 13.7215
17 | -0.049495 | -0.01245 | 0.049521 | 0.012466 | 2.572e-05 | 1.6302e-05 | 0.074419 | 0.074418 | 0.074419 | 0.98988 | -0.19381 | 0.99044 | -0.18294 | 20.4446
18 | -0.0046891 | -0.0011752 | 0.0046896 | 0.0011752 | 4.8063e-07 | -1.7637e-08 | 0.0070833 | 0.0070832 | 0.0070833 | 0.98506 | -0.28718 | 0.98517 | -0.28503 | 1.946
19 | 0.049381 | 0.012397 | -0.04934 | -0.012371 | 4.0983e-05 | 2.5979e-05 | 0.074593 | 0.074593 | 0.074593 | 0.98517 | -0.28503 | 0.98428 | -0.30244 | 20.4926
20 | -0.054071 | -0.013572 | 0.054187 | 0.013646 | 0.00011635 | 7.3868e-05 | 0.081676 | 0.081676 | 0.081676 | 0.98517 | -0.28503 | 0.98749 | -0.24002 | 22.4385
21 | -0.0056127 | -0.0014067 | 0.0056132 | 0.0014068 | 5.4145e-07 | 8.2784e-08 | 0.0084133 | 0.0084132 | 0.0084133 | 0.99269 | -0.14073 | 0.99279 | -0.1387 | 2.3113
22 | 0.013896 | 0.0034838 | -0.013894 | -0.003483 | 1.4102e-06 | 7.9042e-07 | 0.020827 | 0.020827 | 0.020827 | 0.99279 | -0.1387 | 0.99268 | -0.14083 | 5.7218
23 | -0.019509 | -0.0048906 | 0.019521 | 0.0048977 | 1.1851e-05 | 7.1064e-06 | 0.029241 | 0.02924 | 0.029241 | 0.99279 | -0.1387 | 0.99345 | -0.12596 | 8.0331
24 | -0.063303 | -0.015934 | 0.06336 | 0.01597 | 5.7258e-05 | 3.6422e-05 | 0.094453 | 0.094453 | 0.094453 | 0.99753 | -0.04725 | 0.99852 | -0.028345 | 25.9487
25 | -0.076394 | -0.019237 | 0.076498 | 0.019303 | 0.00010368 | 6.6077e-05 | 0.11388 | 0.11388 | 0.11388 | 0.99852 | -0.028345 | 1 | 0 | 31.2847
26 | -0.0058055 | -0.001455 | 0.005806 | 0.0014551 | 5.6507e-07 | 1.1489e-07 | 0.0087935 | 0.0087934 | 0.0087935 | 0.98239 | -0.33922 | 0.98249 | -0.33717 | 2.4158
27 | -0.011683 | -0.0029281 | 0.011683 | 0.0029282 | 1.8716e-07 | 9.9597e-08 | 0.017695 | 0.017695 | 0.017695 | 0.98249 | -0.33717 | 0.98251 | -0.33684 | 4.8612
28 | -0.011683 | -0.0029282 | 0.011686 | 0.0029296 | 2.6898e-06 | 1.4313e-06 | 0.017695 | 0.017695 | 0.017695 | 0.98251 | -0.33684 | 0.98276 | -0.33201 | 4.8612
29 | -0.030067 | -0.0075417 | 0.030084 | 0.0075522 | 1.6925e-05 | 1.0556e-05 | 0.045527 | 0.045527 | 0.045527 | 0.98276 | -0.33201 | 0.98336 | -0.3202 | 12.5074
30 | 0.01838 | 0.0046121 | -0.018375 | -0.004609 | 5.1655e-06 | 3.0807e-06 | 0.027832 | 0.027832 | 0.027832 | 0.98276 | -0.33201 | 0.98245 | -0.3379 | 7.6463
31 | 0.018375 | 0.004609 | -0.018366 | -0.0046036 | 8.943e-06 | 5.3339e-06 | 0.027832 | 0.027833 | 0.027833 | 0.98245 | -0.3379 | 0.98193 | -0.34812 | 7.6463
32 | 0.011698 | 0.0029325 | -0.011696 | -0.0029312 | 2.3187e-06 | 1.2351e-06 | 0.017728 | 0.017728 | 0.017728 | 0.98193 | -0.34812 | 0.98172 | -0.35228 | 4.8703
33 | 0.0082767 | 0.0020743 | -0.0082763 | -0.0020741 | 3.3477e-07 | 1.3937e-07 | 0.012411 | 0.012411 | 0.012411 | 0.99236 | -0.14707 | 0.99232 | -0.14792 | 3.4095
34 | -0.0082767 | -0.0020743 | 0.0082777 | 0.0020747 | 1.0905e-06 | 4.5396e-07 | 0.012411 | 0.01241 | 0.012411 | 0.99236 | -0.14707 | 0.9925 | -0.1443 | 3.4095
35 | 0.0042184 | 0.0010572 | -0.0042183 | -0.0010572 | 1.4121e-07 | -3.1192e-08 | 0.0063257 | 0.0063257 | 0.0063257 | 0.99232 | -0.14792 | 0.99228 | -0.14862 | 1.7378
36 | 0.0040579 | 0.001017 | -0.0040578 | -0.001017 | 9.9378e-08 | -2.8855e-08 | 0.006085 | 0.006085 | 0.006085 | 0.99232 | -0.14792 | 0.99229 | -0.14843 | 1.6717
37 | -0.013892 | -0.0034817 | 0.013894 | 0.003483 | 2.2973e-06 | 1.2877e-06 | 0.020828 | 0.020827 | 0.020828 | 0.9925 | -0.1443 | 0.99268 | -0.14083 | 5.7218
38 | -0.0357 | -0.0089597 | 0.035702 | 0.0089614 | 2.6042e-06 | 1.6365e-06 | 0.054025 | 0.054025 | 0.054025 | 0.98336 | -0.3202 | 0.98344 | -0.31868 | 14.842
39 | 0.0055078 | 0.0013803 | -0.0055072 | -0.0013802 | 5.823e-07 | 9.0994e-08 | 0.0083483 | 0.0083484 | 0.0083484 | 0.98172 | -0.35228 | 0.98161 | -0.3545 | 2.2935
40 | -0.035702 | -0.0089614 | 0.035716 | 0.0089701 | 1.3951e-05 | 8.7666e-06 | 0.054025 | 0.054025 | 0.054025 | 0.98344 | -0.31868 | 0.98386 | -0.31049 | 14.842
41 | -0.041363 | -0.010385 | 0.041426 | 0.010425 | 6.3022e-05 | 3.9788e-05 | 0.062565 | 0.062565 | 0.062565 | 0.98386 | -0.31049 | 0.98549 | -0.2786 | 17.1883
42 | 0.034248 | 0.0086042 | -0.034218 | -0.0085853 | 3.0147e-05 | 1.8911e-05 | 0.051719 | 0.051719 | 0.051719 | 0.98549 | -0.2786 | 0.98455 | -0.29706 | 14.2086
43 | -0.075674 | -0.019029 | 0.075736 | 0.019069 | 6.2328e-05 | 3.9728e-05 | 0.11428 | 0.11428 | 0.11428 | 0.98549 | -0.2786 | 0.98638 | -0.26137 | 31.3967
44 | 0.034218 | 0.0085853 | -0.0342 | -0.0085739 | 1.8134e-05 | 1.1376e-05 | 0.051719 | 0.051719 | 0.051719 | 0.98455 | -0.29706 | 0.98398 | -0.30818 | 14.2086
45 | -0.075736 | -0.019069 | 0.075824 | 0.019125 | 8.7907e-05 | 5.6031e-05 | 0.11428 | 0.11428 | 0.11428 | 0.98638 | -0.26137 | 0.98763 | -0.23712 | 31.3967
46 | -0.0050621 | -0.0012687 | 0.0050621 | 0.0012687 | 4.5738e-08 | 2.8707e-09 | 0.0076577 | 0.0076577 | 0.0076577 | 0.98364 | -0.31481 | 0.98365 | -0.31462 | 2.1038
47 | 0.014057 | 0.0035236 | -0.014054 | -0.0035217 | 3.4213e-06 | 1.9336e-06 | 0.021265 | 0.021265 | 0.021265 | 0.98365 | -0.31462 | 0.98339 | -0.31973 | 5.842
48 | -0.019119 | -0.0047923 | 0.019124 | 0.0047954 | 5.0715e-06 | 3.0405e-06 | 0.028923 | 0.028923 | 0.028923 | 0.98365 | -0.31462 | 0.98393 | -0.30906 | 7.9458
49 | 0.019125 | 0.0047958 | -0.019124 | -0.0047954 | 7.9861e-07 | 4.7877e-07 | 0.028923 | 0.028923 | 0.028923 | 0.98398 | -0.30818 | 0.98393 | -0.30906 | 7.9458
50 | -0.10384 | -0.026146 | 0.10412 | 0.026327 | 0.00028366 | 0.00018115 | 0.15649 | 0.15649 | 0.15649 | 0.98763 | -0.23712 | 0.99058 | -0.18015 | 42.9912
51 | 0.014054 | 0.0035217 | -0.014053 | -0.0035213 | 7.6549e-07 | 4.3264e-07 | 0.021265 | 0.021265 | 0.021265 | 0.98339 | -0.31973 | 0.98333 | -0.32088 | 5.842
52 | -0.011514 | -0.0028856 | 0.011516 | 0.0028867 | 2.068e-06 | 1.0894e-06 | 0.017354 | 0.017354 | 0.017354 | 0.98723 | -0.24539 | 0.98742 | -0.24162 | 4.7677
53 | -0.011516 | -0.0028867 | 0.011517 | 0.0028875 | 1.4598e-06 | 7.6894e-07 | 0.017354 | 0.017354 | 0.017354 | 0.98742 | -0.24162 | 0.98756 | -0.23896 | 4.7677
54 | -0.12105 | -0.030569 | 0.12132 | 0.030744 | 0.00027307 | 0.00017448 | 0.18192 | 0.18192 | 0.18192 | 0.99058 | -0.18015 | 0.99302 | -0.13319 | 49.9774
55 | 0.0091744 | 0.0022986 | -0.0091742 | -0.0022985 | 2.0782e-07 | 9.653e-08 | 0.013883 | 0.013883 | 0.013883 | 0.98333 | -0.32088 | 0.9833 | -0.32135 | 3.814
56 | 0.32878 | 0.08394 | -0.32815 | -0.083535 | 0.00063383 | 0.00040482 | 0.48978 | 0.48978 | 0.48978 | 1 | 0 | 0.99789 | -0.039976 | 44.8517
57 | -0.058622 | -0.014747 | 0.058684 | 0.014787 | 6.2613e-05 | 3.9795e-05 | 0.088091 | 0.088091 | 0.088091 | 0.99044 | -0.18294 | 0.9916 | -0.16061 | 24.2009
58 | 0.077234 | 0.019519 | -0.077126 | -0.01945 | 0.00010817 | 6.8955e-05 | 0.11596 | 0.11596 | 0.11596 | 0.9916 | -0.16061 | 0.99008 | -0.18986 | 31.8565
59 | 0.049833 | 0.012556 | -0.049712 | -0.01248 | 0.00012045 | 7.6351e-05 | 0.074804 | 0.074805 | 0.074805 | 0.9916 | -0.16061 | 0.98898 | -0.21127 | 20.5507
60 | -0.18575 | -0.046862 | 0.18635 | 0.047246 | 0.00060151 | 0.0003839 | 0.27885 | 0.27885 | 0.27885 | 0.9916 | -0.16061 | 0.9951 | -0.093212 | 38.304
61 | 0.0651 | 0.016436 | -0.065056 | -0.016408 | 4.3672e-05 | 2.7794e-05 | 0.097883 | 0.097883 | 0.097883 | 0.99008 | -0.18986 | 0.98936 | -0.20387 | 26.8908
62 | 0.049712 | 0.01248 | -0.049684 | -0.012462 | 2.8387e-05 | 1.7994e-05 | 0.074805 | 0.074805 | 0.074805 | 0.98898 | -0.21127 | 0.98836 | -0.22325 | 20.5507
63 | 0.13078 | 0.033211 | -0.13052 | -0.03305 | 0.00025108 | 0.00016047 | 0.19571 | 0.19571 | 0.19571 | 0.9951 | -0.093212 | 0.99302 | -0.13319 | 53.7658
64 | -0.31713 | -0.080457 | 0.31794 | 0.080977 | 0.00081415 | 0.00051993 | 0.47456 | 0.47456 | 0.47456 | 0.9951 | -0.093212 | 0.99789 | -0.039976 | 43.4579
65 | -0.0041722 | -0.0010456 | 0.0041724 | 0.0010456 | 2.4871e-07 | -5.1633e-08 | 0.0063156 | 0.0063155 | 0.0063156 | 0.983 | -0.32729 | 0.98306 | -0.32604 | 1.7351
66 | -0.0041724 | -0.0010456 | 0.0041733 | 0.0010454 | 9.3167e-07 | -1.937e-07 | 0.0063155 | 0.0063152 | 0.0063155 | 0.98306 | -0.32604 | 0.9833 | -0.32135 | 1.735
67 | 0.0050008 | 0.0012532 | -0.005 | -0.0012531 | 8.6515e-07 | 4.2796e-08 | 0.0075676 | 0.0075678 | 0.0075678 | 0.9833 | -0.32135 | 0.98312 | -0.32499 | 2.0791
68 | 0.03277 | 0.0082228 | -0.032758 | -0.0082156 | 1.1592e-05 | 7.2561e-06 | 0.049339 | 0.049339 | 0.049339 | 0.98836 | -0.22325 | 0.98798 | -0.23067 | 13.5548
69 | 0.032758 | 0.0082156 | -0.032746 | -0.008208 | 1.2149e-05 | 7.6048e-06 | 0.049339 | 0.04934 | 0.04934 | 0.98798 | -0.23067 | 0.98758 | -0.23845 | 13.5548
70 | -0.054187 | -0.013646 | 0.054248 | 0.013685 | 6.1343e-05 | 3.8946e-05 | 0.081676 | 0.081676 | 0.081676 | 0.98749 | -0.24002 | 0.98871 | -0.21637 | 22.4385
71 | -0.065017 | -0.016384 | 0.065056 | 0.016408 | 3.8889e-05 | 2.475e-05 | 0.097883 | 0.097883 | 0.097883 | 0.98871 | -0.21637 | 0.98936 | -0.20387 | 26.8908
72 | -0.011517 | -0.0028875 | 0.011518 | 0.0028876 | 2.8048e-07 | 1.4773e-07 | 0.017354 | 0.017354 | 0.017354 | 0.98756 | -0.23896 | 0.98758 | -0.23845 | 4.7676

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42118 | 0.10681

## res_load
| p_mw | q_mvar
0 | 0.0092792 | 0.0023256
1 | 0.0069525 | 0.0017425
2 | 0.0094517 | 0.0023688
3 | 0.0071924 | 0.0018026
4 | 0.015311 | 0.0038372
5 | 0.0076307 | 0.0019124
6 | 0.0090994 | 0.0022805
7 | 0.0069605 | 0.0017445
8 | 0.010229 | 0.0025637
9 | 0.022794 | 0.0057127
10 | 0.0046891 | 0.0011752
11 | 0.0056127 | 0.0014067
12 | 0.013034 | 0.0032666
13 | 0.0058055 | 0.001455
14 | 0.0058772 | 0.001473
15 | 0.006668 | 0.0016712
16 | 0.0056141 | 0.001407
17 | 0.0056161 | 0.0014075
18 | 0.0073798 | 0.0018496
19 | 0.0061882 | 0.0015509
20 | 0.0040578 | 0.001017
21 | 0.0042183 | 0.0010572
22 | 0.0055072 | 0.0013802
23 | 0.0056468 | 0.0014152
24 | 0.0050621 | 0.0012687
25 | 0.013734 | 0.003442
26 | 0.015075 | 0.0037781
27 | 0.028012 | 0.0070204
28 | 0.011514 | 0.0028856
29 | 0.016929 | 0.0042428
30 | 0.0048784 | 0.0012226
31 | 0.01425 | 0.0035714
32 | 0.0091008 | 0.0022809
33 | 0.016303 | 0.004086
34 | 0.012027 | 0.0030142
35 | 0.0041722 | 0.0010456
36 | 0.005 | 0.0012531
37 | 0.016914 | 0.0042392
38 | 0.010769 | 0.0026988
39 | 0.021228 | 0.0053203
40 | 0.0092027 | 0.0023064
41 | 0.010207 | 0.0025582

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1