## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_198-13_1_3_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_198-13_1_3_node_71 | 0.4 | n |  | TRUE
2 | bus_LV_198-13_1_3_node_81 | 0.4 | n |  | TRUE
3 | bus_LV_198-13_1_3_node_91 | 0.4 | n |  | TRUE
4 | bus_LV_198-13_1_3_node_56 | 0.4 | n |  | TRUE
5 | bus_LV_198-13_1_3_node_50 | 0.4 | n |  | TRUE
6 | bus_LV_198-13_1_3_node_46 | 0.4 | n |  | TRUE
7 | bus_LV_198-13_1_3_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_198-13_1_3_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_198-13_1_3_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_198-13_1_3_node_80 | 0.4 | n |  | TRUE
11 | bus_LV_198-13_1_3_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_198-13_1_3_node_68 | 0.4 | n |  | TRUE
13 | bus_LV_198-13_1_3_node_62 | 0.4 | n |  | TRUE
14 | bus_LV_198-13_1_3_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_198-13_1_3_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_198-13_1_3_node_82 | 0.4 | n |  | TRUE
17 | bus_LV_198-13_1_3_node_79 | 0.4 | n |  | TRUE
18 | bus_LV_198-13_1_3_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_198-13_1_3_node_43 | 0.4 | n |  | TRUE
20 | bus_LV_198-13_1_3_node_86 | 0.4 | n |  | TRUE
21 | bus_LV_198-13_1_3_node_70 | 0.4 | n |  | TRUE
22 | bus_LV_198-13_1_3_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_198-13_1_3_node_88 | 0.4 | n |  | TRUE
24 | bus_LV_198-13_1_3_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_198-13_1_3_node_66 | 0.4 | n |  | TRUE
26 | bus_LV_198-13_1_3_node_67 | 0.4 | n |  | TRUE
27 | bus_LV_198-13_1_3_node_90 | 0.4 | n |  | TRUE
28 | bus_LV_198-13_1_3_node_89 | 0.4 | n |  | TRUE
29 | bus_LV_198-13_1_3_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_198-13_1_3_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_198-13_1_3_node_69 | 0.4 | n |  | TRUE
32 | bus_LV_198-13_1_3_node_65 | 0.4 | n |  | TRUE
33 | bus_LV_198-13_1_3_node_83 | 0.4 | n |  | TRUE
34 | bus_LV_198-13_1_3_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_198-13_1_3_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_198-13_1_3_node_54 | 0.4 | n |  | TRUE
37 | bus_LV_198-13_1_3_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_198-13_1_3_node_52 | 0.4 | n |  | TRUE
39 | bus_LV_198-13_1_3_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_198-13_1_3_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_198-13_1_3_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_198-13_1_3_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_198-13_1_3_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_198-13_1_3_node_59 | 0.4 | n |  | TRUE
45 | bus_LV_198-13_1_3_node_57 | 0.4 | n |  | TRUE
46 | bus_LV_198-13_1_3_node_58 | 0.4 | n |  | TRUE
47 | bus_LV_198-13_1_3_node_84 | 0.4 | n |  | TRUE
48 | bus_MV_362_0_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_198-13_1_3_load_81 | 2 | 0.0047796 | 0.0011979 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_198-13_1_3_load_91 | 3 | 0.0055235 | 0.0013843 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_198-13_1_3_load_46 | 6 | 0.0084583 | 0.0021198 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_198-13_1_3_load_48 | 7 | 0.0097778 | 0.0024505 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_198-13_1_3_load_80 | 10 | 0.013811 | 0.0034615 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_198-13_1_3_load_68 | 12 | 0.0036747 | 0.00092096 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_198-13_1_3_load_62 | 13 | 0.0038735 | 0.0009708 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_198-13_1_3_load_82 | 16 | 0.0059869 | 0.0015005 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_198-13_1_3_load_79 | 17 | 0.021062 | 0.0052786 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_198-13_1_3_load_86 | 20 | 0.0096851 | 0.0024273 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_198-13_1_3_load_70 | 21 | 0.0028258 | 0.00070821 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_198-13_1_3_load_88 | 23 | 0.040997 | 0.010275 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_198-13_1_3_load_90 | 27 | 0.0093631 | 0.0023466 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_198-13_1_3_load_89 | 28 | 0.0097832 | 0.0024519 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_198-13_1_3_load_37 | 30 | 0.028925 | 0.0072492 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_198-13_1_3_load_69 | 31 | 0.0070369 | 0.0017636 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_198-13_1_3_load_83 | 33 | 0.0063327 | 0.0015871 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_198-13_1_3_load_85 | 34 | 0.0035228 | 0.00088289 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_198-13_1_3_load_38 | 35 | 0.021984 | 0.0055096 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_198-13_1_3_load_53 | 37 | 0.014593 | 0.0036573 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_198-13_1_3_load_44 | 40 | 0.0068861 | 0.0017258 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_198-13_1_3_load_45 | 41 | 0.0070384 | 0.001764 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_198-13_1_3_load_47 | 42 | 0.0087285 | 0.0021876 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_198-13_1_3_load_57 | 45 | 0.0090974 | 0.00228 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_198-13_1_3_load_58 | 46 | 0.009684 | 0.0024271 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_198-13_1_3_load_84 | 47 | 0.0062799 | 0.0015739 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_198-13_1_3_line_0 |  | 0 | 1 | 0.33212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_198-13_1_3_line_1 |  | 0 | 2 | 0.054009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_198-13_1_3_line_2 |  | 1 | 3 | 0.048653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_198-13_1_3_line_3 |  | 1 | 4 | 0.041365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_198-13_1_3_line_4 |  | 1 | 5 | 0.05042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_198-13_1_3_line_5 |  | 4 | 6 | 0.013767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_198-13_1_3_line_6 |  | 5 | 7 | 0.050892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_198-13_1_3_line_7 |  | 6 | 41 | 0.01696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_198-13_1_3_line_8 |  | 7 | 42 | 0.020522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_198-13_1_3_line_9 |  | 8 | 9 | 0.051541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_198-13_1_3_line_10 |  | 8 | 10 | 0.044629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_198-13_1_3_line_11 |  | 9 | 30 | 0.051966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_198-13_1_3_line_12 |  | 11 | 12 | 0.028756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_198-13_1_3_line_13 |  | 11 | 13 | 0.015613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_198-13_1_3_line_14 |  | 12 | 34 | 0.014458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_198-13_1_3_line_15 |  | 14 | 15 | 0.1195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_198-13_1_3_line_16 |  | 14 | 16 | 0.023521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_198-13_1_3_line_17 |  | 15 | 28 | 0.0097271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_198-13_1_3_line_18 |  | 15 | 29 | 0.073371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_198-13_1_3_line_19 |  | 16 | 33 | 0.014557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_198-13_1_3_line_20 |  | 17 | 18 | 0.018532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_198-13_1_3_line_21 |  | 18 | 36 | 0.027662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_198-13_1_3_line_22 |  | 18 | 38 | 0.00353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_198-13_1_3_line_23 |  | 19 | 20 | 0.02182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_198-13_1_3_line_24 |  | 19 | 21 | 0.038119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_198-13_1_3_line_25 |  | 20 | 39 | 0.031842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_198-13_1_3_line_26 |  | 21 | 32 | 0.03525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_198-13_1_3_line_27 |  | 22 | 23 | 0.031361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_198-13_1_3_line_28 |  | 22 | 24 | 0.003349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_198-13_1_3_line_29 |  | 23 | 38 | 0.030526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_198-13_1_3_line_30 |  | 24 | 35 | 0.010077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_198-13_1_3_line_31 |  | 25 | 26 | 0.044192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_198-13_1_3_line_32 |  | 25 | 27 | 0.0041146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_198-13_1_3_line_33 |  | 26 | 28 | 0.0081806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_198-13_1_3_line_34 |  | 29 | 31 | 0.027399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_198-13_1_3_line_35 |  | 30 | 35 | 0.034988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_198-13_1_3_line_36 |  | 31 | 32 | 0.023166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_198-13_1_3_line_37 |  | 33 | 47 | 0.014904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_198-13_1_3_line_38 |  | 34 | 47 | 0.014498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_198-13_1_3_line_39 |  | 36 | 37 | 0.093969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_198-13_1_3_line_40 |  | 38 | 43 | 0.044214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_198-13_1_3_line_41 |  | 39 | 44 | 0.031812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_198-13_1_3_line_42 |  | 39 | 43 | 0.014775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_198-13_1_3_line_43 |  | 40 | 41 | 0.0018738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_198-13_1_3_line_44 |  | 42 | 43 | 0.019107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_198-13_1_3_line_45 |  | 44 | 45 | 0.019687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_198-13_1_3_line_46 |  | 45 | 46 | 0.00072354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_198-13_1_3_trafo_86 | 0.63 MVA 20/0.4 kV | 48 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2695873.9452 | 1245800.7075 | 2695885.2881 | 1245791.2948 | 2695899.0591 | 1245779.8642 | 2695906.718 | 1245773.5165 | 2695956.3298 | 1245732.1095 | 2695975.1088 | 1245715.2004 | 2695984.4558 | 1245732.9429 | 2695993.4272 | 1245744.9417 | 2696009.5323 | 1245764.8287 | 2696011.8286 | 1245767.6791 | 2696015.0358 | 1245771.6674 | 2696018.0876 | 1245775.453 | 2696021.4877 | 1245779.6668 | 2696038.2458 | 1245801.2102 | 2696065.2103 | 1245834.5278 | 2696033.7728 | 1245858.5593 | 2696035.7825 | 1245860.9048 | 2696040.2483 | 1245866.4925
1 | 2695873.9452 | 1245800.7075 | 2695842.4996 | 1245756.7965
2 | 2696019.1788 | 1245894.2059 | 2696017.832 | 1245895.2515 | 2696010.8378 | 1245886.6873 | 2696022.4029 | 1245877.0894 | 2696031.951 | 1245873.0631 | 2696040.2483 | 1245866.4925
3 | 2696013.5736 | 1245834.8809 | 2696033.7728 | 1245858.5593 | 2696035.7825 | 1245860.9048 | 2696040.2483 | 1245866.4925
4 | 2696002.17 | 1245888.1482 | 2696035.7825 | 1245860.9048 | 2696040.2483 | 1245866.4925
5 | 2696013.5736 | 1245834.8809 | 2696002.9553 | 1245843.644
6 | 2696002.17 | 1245888.1482 | 2696008.0603 | 1245892.091 | 2696027.5038 | 1245915.7682 | 2696017.3341 | 1245924.1307
7 | 2695989.8745 | 1245854.4394 | 2696002.9553 | 1245843.644
8 | 2696001.483 | 1245937.165 | 2696017.3341 | 1245924.1307
9 | 2695833.3261 | 1246014.57 | 2695835.4984 | 1246017.6075 | 2695866.5852 | 1246053.9264
10 | 2695866.5852 | 1246053.9264 | 2695901.687 | 1246026.3651
11 | 2695833.3261 | 1246014.57 | 2695873.2977 | 1245981.3626
12 | 2695871.2806 | 1246219.0842 | 2695876.3344 | 1246215.4075 | 2695893.7006 | 1246201.0914
13 | 2695871.2806 | 1246219.0842 | 2695861.0541 | 1246207.286
14 | 2695904.8569 | 1246191.8945 | 2695893.7006 | 1246201.0914
15 | 2695956.9255 | 1246148.971 | 2695959.3502 | 1246147.1422 | 2695943.2838 | 1246126.7889 | 2695946.2911 | 1246123.9799 | 2695951.8223 | 1246118.821 | 2695974.3674 | 1246098.8371 | 2695976.7292 | 1246101.3661 | 2695981.1876 | 1246101.3382 | 2695986.2728 | 1246097.1284 | 2696012.6256 | 1246075.316
16 | 2695956.9255 | 1246148.971 | 2695938.7767 | 1246163.9322
17 | 2696012.6256 | 1246075.316 | 2696015.6767 | 1246079.135 | 2696018.703 | 1246082.9108
18 | 2696012.6256 | 1246075.316 | 2696043.4069 | 1246049.2722 | 2696046.5172 | 1246046.6428 | 2696043.6787 | 1246039.4914 | 2696036.4889 | 1246029.4895 | 2696033.2619 | 1246025.8011 | 2696030.5837 | 1246022.7443
19 | 2695938.7767 | 1246163.9322 | 2695927.544 | 1246173.1921
20 | 2695955.3316 | 1245913.2539 | 2695943.4955 | 1245898.9944
21 | 2695934.0537 | 1245931.0011 | 2695955.3316 | 1245913.2539
22 | 2695955.3316 | 1245913.2539 | 2695957.7532 | 1245915.8284
23 | 2695946.0101 | 1245997.1117 | 2695962.9255 | 1245983.3284
24 | 2695946.0101 | 1245997.1117 | 2695969.6055 | 1246027.0501
25 | 2695987.6104 | 1245963.2144 | 2695962.9255 | 1245983.3284
26 | 2695991.4249 | 1246054.7349 | 2695969.6055 | 1246027.0501
27 | 2695910.1896 | 1245955.4227 | 2695934.2924 | 1245935.3584
28 | 2695908.1319 | 1245952.7763 | 2695910.1896 | 1245955.4227
29 | 2695957.7532 | 1245915.8284 | 2695934.2924 | 1245935.3584
30 | 2695908.1319 | 1245952.7763 | 2695900.2117 | 1245959.0069
31 | 2696023.8159 | 1246089.2968 | 2696001.0728 | 1246107.9651 | 2696005.3101 | 1246113.1933 | 2695998.8387 | 1246118.0811
32 | 2695998.8387 | 1246118.0811 | 2695995.5524 | 1246120.5571
33 | 2696023.8159 | 1246089.2968 | 2696021.6905 | 1246086.6381 | 2696018.703 | 1246082.9108
34 | 2696030.5837 | 1246022.7443 | 2696009.3651 | 1246040.0788
35 | 2695873.2977 | 1245981.3626 | 2695900.1265 | 1245959.0739 | 2695900.2117 | 1245959.0069
36 | 2695991.4249 | 1246054.7349 | 2696009.3651 | 1246040.0788
37 | 2695927.544 | 1246173.1921 | 2695916.0441 | 1246182.6721
38 | 2695916.0441 | 1246182.6721 | 2695904.8569 | 1246191.8945
39 | 2695934.0537 | 1245931.0011 | 2695928.9464 | 1245924.9027 | 2695901.8927 | 1245892.8741 | 2695900.7361 | 1245891.5099 | 2695915.8187 | 1245878.8552 | 2695930.4123 | 1245896.1281
40 | 2695986.725 | 1245949.3005 | 2695957.7532 | 1245915.8284
41 | 2696002.8774 | 1245989.5593 | 2695987.7269 | 1245971.4114 | 2695987.6104 | 1245963.2144
42 | 2695986.725 | 1245949.3005 | 2695988.9256 | 1245951.9826 | 2695987.6104 | 1245963.2144
43 | 2695988.4293 | 1245855.6322 | 2695989.8745 | 1245854.4394
44 | 2695986.725 | 1245949.3005 | 2696001.483 | 1245937.165
45 | 2696002.8774 | 1245989.5593 | 2696017.9541 | 1245976.8995
46 | 2696017.9541 | 1245976.8995 | 2696018.5082 | 1245976.4342

## bus_geodata
| x | y | coords
0 | 2695873.9452 | 1245800.7075
1 | 2696040.2483 | 1245866.4925
2 | 2695842.4996 | 1245756.7965
3 | 2696019.1788 | 1245894.2059
4 | 2696013.5736 | 1245834.8809
5 | 2696002.17 | 1245888.1482
6 | 2696002.9553 | 1245843.644
7 | 2696017.3341 | 1245924.1307
8 | 2695866.5852 | 1246053.9264
9 | 2695833.3261 | 1246014.57
10 | 2695901.687 | 1246026.3651
11 | 2695871.2806 | 1246219.0842
12 | 2695893.7006 | 1246201.0914
13 | 2695861.0541 | 1246207.286
14 | 2695956.9255 | 1246148.971
15 | 2696012.6256 | 1246075.316
16 | 2695938.7767 | 1246163.9322
17 | 2695943.4955 | 1245898.9944
18 | 2695955.3316 | 1245913.2539
19 | 2695946.0101 | 1245997.1117
20 | 2695962.9255 | 1245983.3284
21 | 2695969.6055 | 1246027.0501
22 | 2695910.1896 | 1245955.4227
23 | 2695934.2924 | 1245935.3584
24 | 2695908.1319 | 1245952.7763
25 | 2695998.8387 | 1246118.0811
26 | 2696023.8159 | 1246089.2968
27 | 2695995.5524 | 1246120.5571
28 | 2696018.703 | 1246082.9108
29 | 2696030.5837 | 1246022.7443
30 | 2695873.2977 | 1245981.3626
31 | 2696009.3651 | 1246040.0788
32 | 2695991.4249 | 1246054.7349
33 | 2695927.544 | 1246173.1921
34 | 2695904.8569 | 1246191.8945
35 | 2695900.2117 | 1245959.0069
36 | 2695934.0537 | 1245931.0011
37 | 2695930.4123 | 1245896.1281
38 | 2695957.7532 | 1245915.8284
39 | 2695987.6104 | 1245963.2144
40 | 2695988.4293 | 1245855.6322
41 | 2695989.8745 | 1245854.4394
42 | 2696001.483 | 1245937.165
43 | 2695986.725 | 1245949.3005
44 | 2696002.8774 | 1245989.5593
45 | 2696017.9541 | 1245976.8995
46 | 2696018.5082 | 1245976.4342
47 | 2695916.0441 | 1246182.6721
48 | 2695946.0101 | 1245997.1117

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98943 | -0.20332 | 0 | 0
1 | 0.99088 | -0.17505 | 0 | 0
2 | 0.98919 | -0.20792 | 0.0047796 | 0.0011979
3 | 0.99064 | -0.17983 | 0.0055235 | 0.0013843
4 | 0.99004 | -0.19151 | 0 | 0
5 | 0.99239 | -0.14583 | 0 | 0
6 | 0.98975 | -0.19699 | 0.0084583 | 0.0021198
7 | 0.99392 | -0.11642 | 0.0097778 | 0.0024505
8 | 0.98442 | -0.30038 | 0 | 0
9 | 0.98507 | -0.28758 | 0 | 0
10 | 0.98385 | -0.31147 | 0.013811 | 0.0034615
11 | 0.98443 | -0.29976 | 0 | 0
12 | 0.98454 | -0.29776 | 0.0036747 | 0.00092096
13 | 0.98438 | -0.30085 | 0.0038735 | 0.0009708
14 | 0.98598 | -0.26955 | 0 | 0
15 | 0.98925 | -0.20618 | 0 | 0
16 | 0.98534 | -0.28207 | 0.0059869 | 0.0015005
17 | 0.99227 | -0.14808 | 0.021062 | 0.0052786
18 | 0.99263 | -0.14117 | 0 | 0
19 | 0.99882 | -0.022349 | 0 | 0
20 | 1 | 0 | -0.27433 | -0.069349
21 | 0.99677 | -0.061518 | 0.0028258 | 0.00070821
22 | 0.98791 | -0.23237 | 0 | 0
23 | 0.98978 | -0.19619 | 0.040997 | 0.010275
24 | 0.98771 | -0.23625 | 0 | 0
25 | 0.98863 | -0.21824 | 0 | 0
26 | 0.98901 | -0.21086 | 0 | 0
27 | 0.98859 | -0.21893 | 0.0093631 | 0.0023466
28 | 0.98908 | -0.2095 | 0.0097832 | 0.0024519
29 | 0.99254 | -0.14258 | 0 | 0
30 | 0.98574 | -0.27469 | 0.028925 | 0.0072492
31 | 0.99377 | -0.11894 | 0.0070369 | 0.0017636
32 | 0.99496 | -0.096129 | 0 | 0
33 | 0.98502 | -0.28826 | 0.0063327 | 0.0015871
34 | 0.98464 | -0.2958 | 0.0035228 | 0.00088289
35 | 0.98711 | -0.24791 | 0.021984 | 0.0055096
36 | 0.99226 | -0.14832 | 0 | 0
37 | 0.991 | -0.17262 | 0.014593 | 0.0036573
38 | 0.99274 | -0.13894 | 0 | 0
39 | 0.99692 | -0.05884 | 0 | 0
40 | 0.98953 | -0.20142 | 0.0068861 | 0.0017258
41 | 0.98954 | -0.20119 | 0.0070384 | 0.001764
42 | 0.99472 | -0.10105 | 0.0087285 | 0.0021876
43 | 0.99561 | -0.083826 | 0 | 0
44 | 0.99637 | -0.069325 | 0 | 0
45 | 0.99603 | -0.075818 | 0.0090974 | 0.00228
46 | 0.99603 | -0.075942 | 0.009684 | 0.0024271
47 | 0.98478 | -0.29291 | 0.0062799 | 0.0015739
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0047806 | -0.0011979 | 0.0047871 | 0.0011977 | 6.4365e-06 | -1.5256e-07 | 0.0071896 | 0.0071881 | 0.0071896 | 0.98943 | -0.20332 | 0.99088 | -0.17505 | 1.9752
1 | 0.0047806 | 0.0011979 | -0.0047796 | -0.0011979 | 1.0469e-06 | -2.3459e-08 | 0.0071896 | 0.0071898 | 0.0071898 | 0.98943 | -0.20332 | 0.98919 | -0.20792 | 1.9752
2 | 0.0055248 | 0.0013845 | -0.0055235 | -0.0013843 | 1.2559e-06 | 1.772e-07 | 0.0082965 | 0.0082967 | 0.0082967 | 0.99088 | -0.17505 | 0.99064 | -0.17983 | 2.2793
3 | 0.022409 | 0.0056255 | -0.022391 | -0.0056148 | 1.757e-05 | 1.0712e-05 | 0.033655 | 0.033655 | 0.033655 | 0.99088 | -0.17505 | 0.99004 | -0.19151 | 9.2459
4 | -0.032721 | -0.0082077 | 0.032767 | 0.0082363 | 4.5655e-05 | 2.8569e-05 | 0.04914 | 0.049139 | 0.04914 | 0.99088 | -0.17505 | 0.99239 | -0.14583 | 13.4999
5 | 0.022391 | 0.0056148 | -0.022386 | -0.0056112 | 5.8477e-06 | 3.5656e-06 | 0.033655 | 0.033655 | 0.033655 | 0.99004 | -0.19151 | 0.98975 | -0.19699 | 9.246
6 | -0.032767 | -0.0082363 | 0.032813 | 0.0082651 | 4.6083e-05 | 2.8834e-05 | 0.049139 | 0.049139 | 0.049139 | 0.99239 | -0.14583 | 0.99392 | -0.11642 | 13.4998
7 | 0.013927 | 0.0034914 | -0.013925 | -0.0034898 | 2.7885e-06 | 1.5667e-06 | 0.020939 | 0.020939 | 0.020939 | 0.98975 | -0.19699 | 0.98954 | -0.20119 | 5.7525
8 | -0.04259 | -0.010716 | 0.042622 | 0.010735 | 3.1303e-05 | 1.9768e-05 | 0.063778 | 0.063778 | 0.063778 | 0.99392 | -0.11642 | 0.99472 | -0.10105 | 17.5213
9 | -0.013819 | -0.0034656 | 0.013827 | 0.0034703 | 8.4334e-06 | 4.7417e-06 | 0.020889 | 0.020888 | 0.020889 | 0.98442 | -0.30038 | 0.98507 | -0.28758 | 5.7387
10 | 0.013819 | 0.0034656 | -0.013811 | -0.0034615 | 7.3026e-06 | 4.1066e-06 | 0.020889 | 0.020889 | 0.020889 | 0.98442 | -0.30038 | 0.98385 | -0.31147 | 5.7387
11 | -0.013827 | -0.0034703 | 0.013836 | 0.0034751 | 8.5028e-06 | 4.7798e-06 | 0.020888 | 0.020888 | 0.020888 | 0.98507 | -0.28758 | 0.98574 | -0.27469 | 5.7386
12 | -0.0038737 | -0.00097073 | 0.0038741 | 0.0009706 | 3.697e-07 | -1.2904e-07 | 0.0058553 | 0.0058551 | 0.0058553 | 0.98443 | -0.29976 | 0.98454 | -0.29776 | 1.6086
13 | 0.0038737 | 0.00097073 | -0.0038735 | -0.0009708 | 2.0074e-07 | -7.0026e-08 | 0.0058553 | 0.0058553 | 0.0058553 | 0.98443 | -0.29976 | 0.98438 | -0.30085 | 1.6086
14 | -0.0075488 | -0.0018916 | 0.0075495 | 0.0018918 | 7.0574e-07 | 2.6779e-07 | 0.011409 | 0.011409 | 0.011409 | 0.98454 | -0.29776 | 0.98464 | -0.2958 | 3.1343
15 | -0.029702 | -0.0074546 | 0.029792 | 0.0075107 | 9.0058e-05 | 5.6108e-05 | 0.044829 | 0.044828 | 0.044829 | 0.98598 | -0.26955 | 0.98925 | -0.20618 | 12.3156
16 | 0.029702 | 0.0074546 | -0.029684 | -0.0074435 | 1.7725e-05 | 1.1044e-05 | 0.044829 | 0.044829 | 0.044829 | 0.98598 | -0.26955 | 0.98534 | -0.28207 | 12.3157
17 | 0.019154 | 0.0048023 | -0.019151 | -0.0048005 | 3.0279e-06 | 1.813e-06 | 0.028811 | 0.028811 | 0.028811 | 0.98925 | -0.20618 | 0.98908 | -0.2095 | 7.9152
18 | -0.048945 | -0.012313 | 0.049095 | 0.012408 | 0.0001492 | 9.4544e-05 | 0.07364 | 0.073639 | 0.07364 | 0.98925 | -0.20618 | 0.99254 | -0.14258 | 20.2307
19 | 0.023697 | 0.0059431 | -0.02369 | -0.0059388 | 6.9918e-06 | 4.2894e-06 | 0.035788 | 0.035788 | 0.035788 | 0.98534 | -0.28207 | 0.98502 | -0.28826 | 9.8318
20 | -0.021062 | -0.0052786 | 0.021069 | 0.0052828 | 6.9326e-06 | 4.1974e-06 | 0.031584 | 0.031584 | 0.031584 | 0.99227 | -0.14808 | 0.99263 | -0.14117 | 8.677
21 | 0.014615 | 0.0036698 | -0.01461 | -0.0036669 | 4.9801e-06 | 2.8299e-06 | 0.021911 | 0.021911 | 0.021911 | 0.99263 | -0.14117 | 0.99226 | -0.14832 | 6.0195
22 | -0.035683 | -0.0089525 | 0.035687 | 0.0089549 | 3.7882e-06 | 2.3788e-06 | 0.053495 | 0.053495 | 0.053495 | 0.99263 | -0.14117 | 0.99274 | -0.13894 | 14.6965
23 | -0.05928 | -0.015084 | 0.059344 | 0.015125 | 6.3933e-05 | 4.0632e-05 | 0.088394 | 0.088394 | 0.088394 | 0.99882 | -0.022349 | 1 | 0 | 24.284
24 | 0.05928 | 0.015084 | -0.059168 | -0.015013 | 0.00011169 | 7.0984e-05 | 0.088394 | 0.088394 | 0.088394 | 0.99882 | -0.022349 | 0.99677 | -0.061518 | 24.2841
25 | 0.21333 | 0.054224 | -0.21273 | -0.053839 | 0.00060266 | 0.00038487 | 0.31771 | 0.31771 | 0.31771 | 1 | 0 | 0.99692 | -0.05884 | 43.6418
26 | 0.056342 | 0.014305 | -0.056249 | -0.014246 | 9.3661e-05 | 5.9484e-05 | 0.084176 | 0.084176 | 0.084176 | 0.99677 | -0.061518 | 0.99496 | -0.096129 | 23.1252
27 | -0.064847 | -0.016299 | 0.064959 | 0.016371 | 0.00011224 | 7.1428e-05 | 0.097691 | 0.097691 | 0.097691 | 0.98791 | -0.23237 | 0.98978 | -0.19619 | 26.8381
28 | 0.064847 | 0.016299 | -0.064835 | -0.016291 | 1.1985e-05 | 7.6278e-06 | 0.097691 | 0.097691 | 0.097691 | 0.98791 | -0.23237 | 0.98771 | -0.23625 | 26.8381
29 | -0.10596 | -0.026645 | 0.10625 | 0.026831 | 0.00029058 | 0.00018558 | 0.15933 | 0.15932 | 0.15933 | 0.98978 | -0.19619 | 0.99274 | -0.13894 | 43.7706
30 | 0.064835 | 0.016291 | -0.064799 | -0.016269 | 3.6064e-05 | 2.2952e-05 | 0.097691 | 0.097691 | 0.097691 | 0.98771 | -0.23625 | 0.98711 | -0.24791 | 26.8381
31 | -0.0093634 | -0.0023468 | 0.0093667 | 0.0023483 | 3.2914e-06 | 1.5397e-06 | 0.014093 | 0.014093 | 0.014093 | 0.98863 | -0.21824 | 0.98901 | -0.21086 | 3.8718
32 | 0.0093634 | 0.0023468 | -0.0093631 | -0.0023466 | 3.0646e-07 | 1.4338e-07 | 0.014093 | 0.014093 | 0.014093 | 0.98863 | -0.21824 | 0.98859 | -0.21893 | 3.8718
33 | -0.0093667 | -0.0023483 | 0.0093673 | 0.0023486 | 6.0929e-07 | 2.8496e-07 | 0.014093 | 0.014093 | 0.014093 | 0.98901 | -0.21086 | 0.98908 | -0.2095 | 3.8717
34 | -0.049095 | -0.012408 | 0.04915 | 0.012443 | 5.5717e-05 | 3.5304e-05 | 0.073639 | 0.073639 | 0.073639 | 0.99254 | -0.14258 | 0.99377 | -0.11894 | 20.2306
35 | -0.04276 | -0.010724 | 0.042815 | 0.010759 | 5.4671e-05 | 3.4543e-05 | 0.064552 | 0.064552 | 0.064552 | 0.98574 | -0.27469 | 0.98711 | -0.24791 | 17.734
36 | -0.056187 | -0.014206 | 0.056249 | 0.014246 | 6.1554e-05 | 3.9094e-05 | 0.084176 | 0.084176 | 0.084176 | 0.99377 | -0.11894 | 0.99496 | -0.096129 | 23.1252
37 | 0.017357 | 0.0043517 | -0.017354 | -0.0043494 | 3.8427e-06 | 2.2697e-06 | 0.026221 | 0.026222 | 0.026222 | 0.98502 | -0.28826 | 0.98478 | -0.29291 | 7.2037
38 | -0.011072 | -0.0027747 | 0.011074 | 0.0027755 | 1.5222e-06 | 7.8979e-07 | 0.016733 | 0.016733 | 0.016733 | 0.98464 | -0.2958 | 0.98478 | -0.29291 | 4.5969
39 | 0.01461 | 0.0036669 | -0.014593 | -0.0036573 | 1.6918e-05 | 9.6154e-06 | 0.021911 | 0.021912 | 0.021912 | 0.99226 | -0.14832 | 0.991 | -0.17262 | 6.0197
40 | -0.14193 | -0.035786 | 0.14231 | 0.036025 | 0.00037548 | 0.00023916 | 0.21282 | 0.21282 | 0.21282 | 0.99274 | -0.13894 | 0.99561 | -0.083826 | 29.2336
41 | 0.018797 | 0.0047162 | -0.018787 | -0.0047106 | 9.3917e-06 | 5.5961e-06 | 0.028058 | 0.028058 | 0.028058 | 0.99692 | -0.05884 | 0.99637 | -0.069325 | 7.7083
42 | 0.19393 | 0.049123 | -0.1937 | -0.048975 | 0.00023243 | 0.00014837 | 0.28965 | 0.28965 | 0.28965 | 0.99692 | -0.05884 | 0.99561 | -0.083826 | 39.7877
43 | -0.0068861 | -0.0017258 | 0.0068861 | 0.0017258 | 7.5347e-08 | 2.4151e-08 | 0.010355 | 0.010355 | 0.010355 | 0.98953 | -0.20142 | 0.98954 | -0.20119 | 2.8448
44 | -0.05135 | -0.012923 | 0.051392 | 0.01295 | 4.2299e-05 | 2.6823e-05 | 0.076835 | 0.076835 | 0.076835 | 0.99472 | -0.10105 | 0.99561 | -0.083826 | 21.1084
45 | 0.018787 | 0.0047106 | -0.018782 | -0.0047071 | 5.8122e-06 | 3.4635e-06 | 0.028058 | 0.028058 | 0.028058 | 0.99637 | -0.069325 | 0.99603 | -0.075818 | 7.7084
46 | 0.0096841 | 0.0024271 | -0.009684 | -0.0024271 | 5.6791e-08 | 2.6929e-08 | 0.014467 | 0.014467 | 0.014467 | 0.99603 | -0.075818 | 0.99603 | -0.075942 | 3.9746

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28401 | 0.071777

## res_load
| p_mw | q_mvar
0 | 0.0047796 | 0.0011979
1 | 0.0055235 | 0.0013843
2 | 0.0084583 | 0.0021198
3 | 0.0097778 | 0.0024505
4 | 0.013811 | 0.0034615
5 | 0.0036747 | 0.00092096
6 | 0.0038735 | 0.0009708
7 | 0.0059869 | 0.0015005
8 | 0.021062 | 0.0052786
9 | 0.0096851 | 0.0024273
10 | 0.0028258 | 0.00070821
11 | 0.040997 | 0.010275
12 | 0.0093631 | 0.0023466
13 | 0.0097832 | 0.0024519
14 | 0.028925 | 0.0072492
15 | 0.0070369 | 0.0017636
16 | 0.0063327 | 0.0015871
17 | 0.0035228 | 0.00088289
18 | 0.021984 | 0.0055096
19 | 0.014593 | 0.0036573
20 | 0.0068861 | 0.0017258
21 | 0.0070384 | 0.001764
22 | 0.0087285 | 0.0021876
23 | 0.0090974 | 0.00228
24 | 0.009684 | 0.0024271
25 | 0.0062799 | 0.0015739

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1