## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_198-28_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_198-28_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_198-28_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_198-28_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_198-28_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_198-28_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_198-28_0_6_node_36 | 0.4 | n |  | TRUE
7 | bus_LV_198-28_0_6_node_124 | 0.4 | n |  | TRUE
8 | bus_LV_198-28_0_6_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_198-28_0_6_node_133 | 0.4 | n |  | TRUE
10 | bus_LV_198-28_0_6_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_198-28_0_6_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_198-28_0_6_node_125 | 0.4 | n |  | TRUE
13 | bus_LV_198-28_0_6_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_198-28_0_6_node_127 | 0.4 | n |  | TRUE
15 | bus_LV_198-28_0_6_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_198-28_0_6_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_198-28_0_6_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_198-28_0_6_node_76 | 0.4 | n |  | TRUE
19 | bus_LV_198-28_0_6_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_198-28_0_6_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_198-28_0_6_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_198-28_0_6_node_130 | 0.4 | n |  | TRUE
23 | bus_LV_198-28_0_6_node_93 | 0.4 | n |  | TRUE
24 | bus_LV_198-28_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_198-28_0_6_node_128 | 0.4 | n |  | TRUE
26 | bus_LV_198-28_0_6_node_109 | 0.4 | n |  | TRUE
27 | bus_LV_198-28_0_6_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_198-28_0_6_node_96 | 0.4 | n |  | TRUE
29 | bus_LV_198-28_0_6_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_198-28_0_6_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_198-28_0_6_node_131 | 0.4 | n |  | TRUE
32 | bus_LV_198-28_0_6_node_129 | 0.4 | n |  | TRUE
33 | bus_LV_198-28_0_6_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_198-28_0_6_node_132 | 0.4 | n |  | TRUE
35 | bus_LV_198-28_0_6_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_198-28_0_6_node_126 | 0.4 | n |  | TRUE
37 | bus_LV_198-28_0_6_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_198-28_0_6_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_198-28_0_6_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_198-28_0_6_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_198-28_0_6_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_198-28_0_6_node_110 | 0.4 | n |  | TRUE
43 | bus_LV_198-28_0_6_node_6 | 0.4 | n |  | TRUE
44 | bus_LV_198-28_0_6_node_8 | 0.4 | n |  | TRUE
45 | bus_LV_198-28_0_6_node_10 | 0.4 | n |  | TRUE
46 | bus_LV_198-28_0_6_node_11 | 0.4 | n |  | TRUE
47 | bus_LV_198-28_0_6_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_198-28_0_6_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_198-28_0_6_node_12 | 0.4 | n |  | TRUE
50 | bus_LV_198-28_0_6_node_13 | 0.4 | n |  | TRUE
51 | bus_LV_198-28_0_6_node_14 | 0.4 | n |  | TRUE
52 | bus_LV_198-28_0_6_node_15 | 0.4 | n |  | TRUE
53 | bus_LV_198-28_0_6_node_16 | 0.4 | n |  | TRUE
54 | bus_LV_198-28_0_6_node_17 | 0.4 | n |  | TRUE
55 | bus_LV_198-28_0_6_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_198-28_0_6_node_100 | 0.4 | n |  | TRUE
57 | bus_LV_198-28_0_6_node_88 | 0.4 | n |  | TRUE
58 | bus_LV_198-28_0_6_node_81 | 0.4 | n |  | TRUE
59 | bus_LV_198-28_0_6_node_92 | 0.4 | n |  | TRUE
60 | bus_LV_198-28_0_6_node_65 | 0.4 | n |  | TRUE
61 | bus_LV_198-28_0_6_node_112 | 0.4 | n |  | TRUE
62 | bus_LV_198-28_0_6_node_111 | 0.4 | n |  | TRUE
63 | bus_LV_198-28_0_6_node_63 | 0.4 | n |  | TRUE
64 | bus_LV_198-28_0_6_node_91 | 0.4 | n |  | TRUE
65 | bus_LV_198-28_0_6_node_67 | 0.4 | n |  | TRUE
66 | bus_LV_198-28_0_6_node_115 | 0.4 | n |  | TRUE
67 | bus_LV_198-28_0_6_node_123 | 0.4 | n |  | TRUE
68 | bus_LV_198-28_0_6_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_198-28_0_6_node_104 | 0.4 | n |  | TRUE
70 | bus_LV_198-28_0_6_node_108 | 0.4 | n |  | TRUE
71 | bus_LV_198-28_0_6_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_198-28_0_6_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_198-28_0_6_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_198-28_0_6_node_86 | 0.4 | n |  | TRUE
75 | bus_LV_198-28_0_6_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_198-28_0_6_node_89 | 0.4 | n |  | TRUE
77 | bus_LV_198-28_0_6_node_42 | 0.4 | n |  | TRUE
78 | bus_LV_198-28_0_6_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_198-28_0_6_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_198-28_0_6_node_94 | 0.4 | n |  | TRUE
81 | bus_LV_198-28_0_6_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_198-28_0_6_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_198-28_0_6_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_198-28_0_6_node_46 | 0.4 | n |  | TRUE
85 | bus_LV_198-28_0_6_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_198-28_0_6_node_49 | 0.4 | n |  | TRUE
87 | bus_LV_198-28_0_6_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_198-28_0_6_node_52 | 0.4 | n |  | TRUE
89 | bus_LV_198-28_0_6_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_198-28_0_6_node_101 | 0.4 | n |  | TRUE
91 | bus_LV_198-28_0_6_node_50 | 0.4 | n |  | TRUE
92 | bus_LV_198-28_0_6_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_198-28_0_6_node_51 | 0.4 | n |  | TRUE
94 | bus_LV_198-28_0_6_node_53 | 0.4 | n |  | TRUE
95 | bus_LV_198-28_0_6_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_198-28_0_6_node_98 | 0.4 | n |  | TRUE
97 | bus_LV_198-28_0_6_node_55 | 0.4 | n |  | TRUE
98 | bus_LV_198-28_0_6_node_56 | 0.4 | n |  | TRUE
99 | bus_LV_198-28_0_6_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_198-28_0_6_node_57 | 0.4 | n |  | TRUE
101 | bus_LV_198-28_0_6_node_58 | 0.4 | n |  | TRUE
102 | bus_LV_198-28_0_6_node_106 | 0.4 | n |  | TRUE
103 | bus_LV_198-28_0_6_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_198-28_0_6_node_102 | 0.4 | n |  | TRUE
105 | bus_LV_198-28_0_6_node_120 | 0.4 | n |  | TRUE
106 | bus_LV_198-28_0_6_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_198-28_0_6_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_198-28_0_6_node_117 | 0.4 | n |  | TRUE
109 | bus_LV_198-28_0_6_node_113 | 0.4 | n |  | TRUE
110 | bus_LV_198-28_0_6_node_121 | 0.4 | n |  | TRUE
111 | bus_LV_198-28_0_6_node_71 | 0.4 | n |  | TRUE
112 | bus_LV_198-28_0_6_node_78 | 0.4 | n |  | TRUE
113 | bus_LV_198-28_0_6_node_80 | 0.4 | n |  | TRUE
114 | bus_LV_198-28_0_6_node_84 | 0.4 | n |  | TRUE
115 | bus_LV_198-28_0_6_node_87 | 0.4 | n |  | TRUE
116 | bus_LV_198-28_0_6_node_90 | 0.4 | n |  | TRUE
117 | bus_LV_198-28_0_6_node_99 | 0.4 | n |  | TRUE
118 | bus_LV_198-28_0_6_node_95 | 0.4 | n |  | TRUE
119 | bus_LV_198-28_0_6_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_198-28_0_6_node_118 | 0.4 | n |  | TRUE
121 | bus_LV_198-28_0_6_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_198-28_0_6_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_198-28_0_6_node_119 | 0.4 | n |  | TRUE
124 | bus_LV_198-28_0_6_node_122 | 0.4 | n |  | TRUE
125 | bus_MV_362_0_node_211 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_198-28_0_6_load_0 | 0 | 0.083996 | 0.021051 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_198-28_0_6_load_1 | 1 | 0.018119 | 0.0045411 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_198-28_0_6_load_4 | 4 | 0.025545 | 0.0064021 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_198-28_0_6_load_124 | 7 | 0.0032673 | 0.00081886 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_198-28_0_6_load_133 | 9 | 0.0034721 | 0.00087019 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_198-28_0_6_load_125 | 12 | 0.036094 | 0.009046 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_198-28_0_6_load_127 | 14 | 0.0074585 | 0.0018693 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_198-28_0_6_load_76 | 18 | 0.000975 | 0.00024436 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_198-28_0_6_load_7 | 21 | 0.0013206 | 0.00033097 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_198-28_0_6_load_130 | 22 | 0.0014693 | 0.00036824 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_198-28_0_6_load_93 | 23 | 0.002259 | 0.00056617 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_198-28_0_6_load_128 | 25 | 0.0072047 | 0.0018057 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_198-28_0_6_load_109 | 26 | 0.0038343 | 0.00096096 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_198-28_0_6_load_96 | 28 | 0.010892 | 0.0027297 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_198-28_0_6_load_131 | 31 | 0.0053292 | 0.0013356 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_198-28_0_6_load_129 | 32 | 0.0081961 | 0.0020541 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_198-28_0_6_load_132 | 34 | 0.0012315 | 0.00030864 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_198-28_0_6_load_126 | 36 | 0.017801 | 0.0044613 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_198-28_0_6_load_18 | 39 | 0.0029936 | 0.00075027 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_198-28_0_6_load_44 | 40 | 0.0028533 | 0.00071511 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_198-28_0_6_load_54 | 41 | 0.0036921 | 0.00092533 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_198-28_0_6_load_6 | 43 | 0.0093334 | 0.0023392 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_198-28_0_6_load_10 | 45 | 0.0023966 | 0.00060065 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_198-28_0_6_load_11 | 46 | 0.0018588 | 0.00046587 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_198-28_0_6_load_47 | 47 | 0.0033895 | 0.00084949 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_198-28_0_6_load_48 | 48 | 0.0031295 | 0.00078433 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_198-28_0_6_load_12 | 49 | 0.00162 | 0.00040602 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_198-28_0_6_load_13 | 50 | 0.0020426 | 0.00051193 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_198-28_0_6_load_15 | 52 | 0.0018971 | 0.00047545 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_198-28_0_6_load_17 | 54 | 0.0036536 | 0.00091567 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_198-28_0_6_load_100 | 56 | 0.0020008 | 0.00050145 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_198-28_0_6_load_88 | 57 | 0.0027339 | 0.00068518 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_198-28_0_6_load_81 | 58 | 0.0018628 | 0.00046686 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_198-28_0_6_load_92 | 59 | 0.00197 | 0.00049372 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_198-28_0_6_load_112 | 61 | 0.0037746 | 0.00094601 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_198-28_0_6_load_111 | 62 | 0.0014796 | 0.00037081 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_198-28_0_6_load_91 | 64 | 0.0046731 | 0.0011712 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_198-28_0_6_load_123 | 67 | 0.0046934 | 0.0011763 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_198-28_0_6_load_104 | 69 | 0.0015946 | 0.00039965 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_198-28_0_6_load_108 | 70 | 0.0015335 | 0.00038434 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_198-28_0_6_load_61 | 72 | 0.0049684 | 0.0012452 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_198-28_0_6_load_86 | 74 | 0.0048853 | 0.0012244 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_198-28_0_6_load_60 | 75 | 0.0081769 | 0.0020493 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_198-28_0_6_load_89 | 76 | 0.0013556 | 0.00033973 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_198-28_0_6_load_42 | 77 | 0.0011279 | 0.00028267 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_198-28_0_6_load_77 | 78 | 0.0014848 | 0.00037213 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_198-28_0_6_load_45 | 79 | 0.0028799 | 0.00072176 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_198-28_0_6_load_94 | 80 | 0.00057116 | 0.00014315 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_198-28_0_6_load_74 | 81 | 0.00129 | 0.00032332 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_198-28_0_6_load_46 | 84 | 0.00089934 | 0.0002254 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_198-28_0_6_load_73 | 85 | 0.0012926 | 0.00032395 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_198-28_0_6_load_72 | 87 | 0.0027435 | 0.00068757 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_198-28_0_6_load_52 | 88 | 0.0022095 | 0.00055376 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_198-28_0_6_load_69 | 89 | 0.005626 | 0.00141 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_198-28_0_6_load_101 | 90 | 0.0031984 | 0.00080161 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_198-28_0_6_load_50 | 91 | 0.0027987 | 0.00070143 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_198-28_0_6_load_70 | 92 | 0.0048642 | 0.0012191 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_198-28_0_6_load_51 | 93 | 0.0019612 | 0.00049152 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_198-28_0_6_load_53 | 94 | 0.0056414 | 0.0014139 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_198-28_0_6_load_97 | 95 | 0.0014269 | 0.0003576 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_198-28_0_6_load_98 | 96 | 0.0016644 | 0.00041713 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_198-28_0_6_load_55 | 97 | 0.0018703 | 0.00046874 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_198-28_0_6_load_57 | 100 | 0.019262 | 0.0048275 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_198-28_0_6_load_58 | 101 | 0.011311 | 0.0028348 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_198-28_0_6_load_106 | 102 | 0.0018612 | 0.00046646 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_198-28_0_6_load_107 | 103 | 0.0026149 | 0.00065535 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_198-28_0_6_load_102 | 104 | 0.011394 | 0.0028556 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_198-28_0_6_load_120 | 105 | 0.0018985 | 0.00047582 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_198-28_0_6_load_105 | 106 | 0.01205 | 0.0030199 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_198-28_0_6_load_85 | 107 | 0.0092712 | 0.0023236 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_198-28_0_6_load_117 | 108 | 0.007855 | 0.0019686 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_198-28_0_6_load_113 | 109 | 0.0012534 | 0.00031412 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_198-28_0_6_load_121 | 110 | 0.006219 | 0.0015586 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_198-28_0_6_load_71 | 111 | 0.00232 | 0.00058145 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_198-28_0_6_load_78 | 112 | 0.0050331 | 0.0012614 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_198-28_0_6_load_84 | 114 | 0.0057926 | 0.0014518 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_198-28_0_6_load_87 | 115 | 0.0060504 | 0.0015164 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_198-28_0_6_load_90 | 116 | 0.0014853 | 0.00037224 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_198-28_0_6_load_99 | 117 | 0.0061031 | 0.0015296 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_198-28_0_6_load_95 | 118 | 0.0017223 | 0.00043165 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_198-28_0_6_load_103 | 119 | 0.0050548 | 0.0012669 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_198-28_0_6_load_118 | 120 | 0.0013756 | 0.00034475 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_198-28_0_6_load_114 | 121 | 0.0019729 | 0.00049447 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_198-28_0_6_load_116 | 122 | 0.0014571 | 0.00036517 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_198-28_0_6_load_119 | 123 | 0.0020318 | 0.00050922 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_198-28_0_6_load_122 | 124 | 0.0071026 | 0.0017801 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 83 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_198-28_0_6_line_0 |  | 0 | 1 | 0.034284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_198-28_0_6_line_1 |  | 0 | 2 | 0.0099949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_198-28_0_6_line_2 |  | 1 | 3 | 0.061354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_198-28_0_6_line_3 |  | 2 | 4 | 0.028576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_198-28_0_6_line_4 |  | 2 | 5 | 0.030818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_198-28_0_6_line_5 |  | 3 | 6 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_198-28_0_6_line_6 |  | 4 | 7 | 0.022007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_198-28_0_6_line_7 |  | 5 | 8 | 0.015696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_198-28_0_6_line_8 |  | 6 | 9 | 0.012303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_198-28_0_6_line_9 |  | 7 | 42 | 0.030598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_198-28_0_6_line_10 |  | 8 | 13 | 0.069979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_198-28_0_6_line_11 |  | 8 | 14 | 0.058064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_198-28_0_6_line_12 |  | 8 | 15 | 0.026945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_198-28_0_6_line_13 |  | 10 | 11 | 0.032105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_198-28_0_6_line_14 |  | 10 | 12 | 0.044977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_198-28_0_6_line_15 |  | 11 | 22 | 0.052277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_198-28_0_6_line_16 |  | 12 | 35 | 0.051052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_198-28_0_6_line_17 |  | 13 | 23 | 0.037534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_198-28_0_6_line_18 |  | 13 | 24 | 0.016526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_198-28_0_6_line_19 |  | 14 | 37 | 0.083132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_198-28_0_6_line_20 |  | 15 | 26 | 0.032512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_198-28_0_6_line_21 |  | 16 | 17 | 0.056396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_198-28_0_6_line_22 |  | 16 | 18 | 0.035874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_198-28_0_6_line_23 |  | 17 | 25 | 0.0023914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_198-28_0_6_line_24 |  | 18 | 81 | 0.02101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_198-28_0_6_line_25 |  | 19 | 20 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_198-28_0_6_line_26 |  | 19 | 21 | 0.022229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_198-28_0_6_line_27 |  | 20 | 41 | 0.018264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_198-28_0_6_line_28 |  | 21 | 43 | 0.0050093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_198-28_0_6_line_29 |  | 22 | 32 | 0.025634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_198-28_0_6_line_30 |  | 23 | 80 | 0.015108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_198-28_0_6_line_31 |  | 24 | 77 | 0.028483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_198-28_0_6_line_32 |  | 27 | 28 | 0.053861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_198-28_0_6_line_33 |  | 27 | 29 | 0.068979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_198-28_0_6_line_34 |  | 29 | 38 | 0.040388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_198-28_0_6_line_35 |  | 29 | 39 | 0.055791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_198-28_0_6_line_36 |  | 30 | 31 | 0.020465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_198-28_0_6_line_37 |  | 30 | 32 | 0.010063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_198-28_0_6_line_38 |  | 31 | 33 | 0.01115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_198-28_0_6_line_39 |  | 33 | 34 | 0.020424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_198-28_0_6_line_40 |  | 35 | 36 | 0.045005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_198-28_0_6_line_41 |  | 36 | 37 | 0.007466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_198-28_0_6_line_42 |  | 38 | 40 | 0.036219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_198-28_0_6_line_43 |  | 40 | 79 | 0.021898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_198-28_0_6_line_44 |  | 42 | 99 | 0.012298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_198-28_0_6_line_45 |  | 42 | 98 | 0.000782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_198-28_0_6_line_46 |  | 43 | 44 | 0.030458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_198-28_0_6_line_47 |  | 44 | 45 | 0.013586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_198-28_0_6_line_48 |  | 44 | 46 | 0.014139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_198-28_0_6_line_49 |  | 45 | 47 | 0.020738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_198-28_0_6_line_50 |  | 47 | 48 | 0.0027884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_198-28_0_6_line_51 |  | 48 | 86 | 0.018256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_198-28_0_6_line_52 |  | 49 | 50 | 0.019827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_198-28_0_6_line_53 |  | 49 | 51 | 0.015755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_198-28_0_6_line_54 |  | 50 | 52 | 0.0064386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_198-28_0_6_line_55 |  | 51 | 53 | 0.027113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_198-28_0_6_line_56 |  | 51 | 54 | 0.018973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_198-28_0_6_line_57 |  | 52 | 55 | 0.022753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_198-28_0_6_line_58 |  | 53 | 56 | 0.011755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_198-28_0_6_line_59 |  | 54 | 57 | 0.0065236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_198-28_0_6_line_60 |  | 55 | 58 | 0.011791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_198-28_0_6_line_61 |  | 55 | 59 | 0.012354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_198-28_0_6_line_62 |  | 56 | 72 | 0.027027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_198-28_0_6_line_63 |  | 57 | 76 | 0.01635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_198-28_0_6_line_64 |  | 58 | 83 | 0.040997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_198-28_0_6_line_65 |  | 60 | 61 | 0.024276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_198-28_0_6_line_66 |  | 60 | 62 | 0.018185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_198-28_0_6_line_67 |  | 60 | 63 | 0.042658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_198-28_0_6_line_68 |  | 61 | 105 | 0.031483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_198-28_0_6_line_69 |  | 62 | 106 | 0.027003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_198-28_0_6_line_70 |  | 63 | 64 | 0.033913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_198-28_0_6_line_71 |  | 64 | 73 | 0.034354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_198-28_0_6_line_72 |  | 65 | 66 | 0.015304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_198-28_0_6_line_73 |  | 65 | 67 | 0.01469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_198-28_0_6_line_74 |  | 66 | 108 | 0.025811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_198-28_0_6_line_75 |  | 66 | 109 | 0.013033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_198-28_0_6_line_76 |  | 67 | 110 | 0.0067165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_198-28_0_6_line_77 |  | 68 | 69 | 0.014834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_198-28_0_6_line_78 |  | 68 | 70 | 0.0077783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_198-28_0_6_line_79 |  | 68 | 71 | 0.033585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_198-28_0_6_line_80 |  | 69 | 104 | 0.023436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_198-28_0_6_line_81 |  | 70 | 103 | 0.014249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_198-28_0_6_line_82 |  | 71 | 72 | 0.011549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_198-28_0_6_line_83 |  | 73 | 74 | 0.0097744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_198-28_0_6_line_84 |  | 73 | 75 | 0.012858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_198-28_0_6_line_85 |  | 74 | 107 | 0.020901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_198-28_0_6_line_86 |  | 75 | 101 | 0.020917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_198-28_0_6_line_87 |  | 76 | 116 | 0.0024169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_198-28_0_6_line_88 |  | 77 | 78 | 0.016892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_198-28_0_6_line_89 |  | 78 | 82 | 0.011945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_198-28_0_6_line_90 |  | 79 | 84 | 0.018982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_198-28_0_6_line_91 |  | 80 | 118 | 0.020138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_198-28_0_6_line_92 |  | 81 | 85 | 0.0042486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_198-28_0_6_line_93 |  | 82 | 85 | 0.016187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_198-28_0_6_line_94 |  | 82 | 84 | 0.02141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_198-28_0_6_line_95 |  | 83 | 112 | 0.01369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_198-28_0_6_line_96 |  | 86 | 87 | 0.021416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_198-28_0_6_line_97 |  | 86 | 88 | 0.023044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_198-28_0_6_line_98 |  | 86 | 89 | 0.019331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_198-28_0_6_line_99 |  | 87 | 90 | 0.020911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_198-28_0_6_line_100 |  | 88 | 91 | 0.0071619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_198-28_0_6_line_101 |  | 89 | 92 | 0.018355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_198-28_0_6_line_102 |  | 91 | 93 | 0.0099785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_198-28_0_6_line_103 |  | 92 | 111 | 0.012851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_198-28_0_6_line_104 |  | 93 | 94 | 0.011374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_198-28_0_6_line_105 |  | 94 | 95 | 0.0032981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_198-28_0_6_line_106 |  | 95 | 96 | 0.015037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_198-28_0_6_line_107 |  | 96 | 117 | 0.0012789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_198-28_0_6_line_108 |  | 97 | 98 | 0.026731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_198-28_0_6_line_109 |  | 99 | 114 | 0.0096562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_198-28_0_6_line_110 |  | 100 | 101 | 0.034585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_198-28_0_6_line_111 |  | 102 | 103 | 0.017533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_198-28_0_6_line_112 |  | 104 | 119 | 0.025229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_198-28_0_6_line_113 |  | 105 | 120 | 0.0052344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_198-28_0_6_line_114 |  | 106 | 119 | 0.02413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_198-28_0_6_line_115 |  | 107 | 115 | 0.0030626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_198-28_0_6_line_116 |  | 109 | 121 | 0.0020531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_198-28_0_6_line_117 |  | 110 | 124 | 0.016647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_198-28_0_6_line_118 |  | 112 | 113 | 0.0052426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_198-28_0_6_line_119 |  | 113 | 114 | 0.018979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_198-28_0_6_line_120 |  | 116 | 117 | 0.015756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_198-28_0_6_line_121 |  | 120 | 123 | 0.01261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_198-28_0_6_line_122 |  | 121 | 122 | 0.014665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_198-28_0_6_line_123 |  | 122 | 123 | 0.0026587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_198-28_0_6_trafo_79 | 0.63 MVA 20/0.4 kV | 125 | 83 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2696170.6169 | 1244946.6886 | 2696204.9001 | 1244946.8917
1 | 2696160.6222 | 1244946.6294 | 2696170.6169 | 1244946.6886
2 | 2696262.7943 | 1244959.3294 | 2696255.3861 | 1244953.4047 | 2696251.5705 | 1244951.0298 | 2696246.5978 | 1244948.7029 | 2696241.3077 | 1244947.3049 | 2696231.9187 | 1244947.0191 | 2696213.518 | 1244946.9428 | 2696204.9001 | 1244946.8917
3 | 2696160.6222 | 1244946.6294 | 2696161.841 | 1244918.083
4 | 2696160.6222 | 1244946.6294 | 2696160.4009 | 1244949.5614 | 2696160.0017 | 1244977.4317
5 | 2696262.7943 | 1244959.3294 | 2696260.959 | 1244966.2382 | 2696256.3692 | 1244978.4953
6 | 2696161.841 | 1244918.083 | 2696160.1491 | 1244900.3198 | 2696160.3242 | 1244896.1603
7 | 2696160.0017 | 1244977.4317 | 2696145.6366 | 1244979.2225 | 2696144.6193 | 1244979.9732
8 | 2696256.3692 | 1244978.4953 | 2696244.0673 | 1244978.3595
9 | 2696163.6523 | 1244868.3856 | 2696163.0271 | 1244870.1212 | 2696158.2061 | 1244882.6637 | 2696160.9381 | 1244883.8311 | 2696160.5426 | 1244890.9746 | 2696160.3242 | 1244896.1603
10 | 2696144.6193 | 1244979.9732 | 2696139.3639 | 1244983.891 | 2696131.6722 | 1244989.3928 | 2696135.4708 | 1244994.2136 | 2696144.1771 | 1245000.7152 | 2696149.4529 | 1245006.2494 | 2696166.6839 | 1245029.969
11 | 2696144.6193 | 1244979.9732 | 2696147.5338 | 1244983.8568 | 2696178.8785 | 1245026.8527
12 | 2696124.7107 | 1244975.0246 | 2696131.5128 | 1244973.1223 | 2696139.3639 | 1244983.891 | 2696144.6193 | 1244979.9732
13 | 2696364.7204 | 1245121.4856 | 2696371.2185 | 1245121.0797 | 2696368.5071 | 1245110.2941 | 2696366.6397 | 1245102.9026 | 2696364.9718 | 1245096.2593
14 | 2696364.9718 | 1245096.2593 | 2696339.2137 | 1245102.5235 | 2696321.1349 | 1245106.2944
15 | 2696364.7204 | 1245121.4856 | 2696360.8698 | 1245121.7343 | 2696313.5349 | 1245131.9196
16 | 2696271.1585 | 1245116.7185 | 2696321.1349 | 1245106.2944
17 | 2696166.6839 | 1245029.969 | 2696188.741 | 1245060.3376
18 | 2696153.4339 | 1245039.8951 | 2696166.6839 | 1245029.969
19 | 2696227.8317 | 1245094.0427 | 2696226.7456 | 1245092.5128 | 2696178.8785 | 1245026.8527
20 | 2696124.7107 | 1244975.0246 | 2696119.8197 | 1244966.2609 | 2696106.3414 | 1244948.2747
21 | 2696143.8016 | 1245156.6613 | 2696146.9862 | 1245157.8694 | 2696195.7116 | 1245137.0434
22 | 2696143.8016 | 1245156.6613 | 2696146.514 | 1245152.5021 | 2696147.3177 | 1245150.0132 | 2696147.962 | 1245145.2312 | 2696148.1921 | 1245139.8975 | 2696147.2618 | 1245134.356 | 2696142.7557 | 1245122.6851
23 | 2696195.7116 | 1245137.0434 | 2696196.3986 | 1245134.7528
24 | 2696135.1882 | 1245103.0851 | 2696142.7557 | 1245122.6851
25 | 2696092.2267 | 1244819.491 | 2696082.9145 | 1244811.6565 | 2696081.1262 | 1244810.0819
26 | 2696081.1262 | 1244810.0819 | 2696089.8751 | 1244789.6474
27 | 2696092.2267 | 1244819.491 | 2696106.7402 | 1244830.5792
28 | 2696091.8467 | 1244785.0423 | 2696089.8751 | 1244789.6474
29 | 2696288.4092 | 1245136.2043 | 2696300.682 | 1245133.5772 | 2696304.2207 | 1245133.9238 | 2696313.5349 | 1245131.9196
30 | 2696188.741 | 1245060.3376 | 2696197.6196 | 1245072.5618
31 | 2696153.4339 | 1245039.8951 | 2696155.091 | 1245046.7605 | 2696154.815 | 1245055.3848 | 2696152.6853 | 1245063.223 | 2696148.9279 | 1245065.9956
32 | 2696028.1089 | 1244979.0855 | 2696026.5721 | 1245032.9243
33 | 2696029.4654 | 1245044.1682 | 2696031.4736 | 1244986.9126 | 2696032.0212 | 1244981.5618 | 2696032.2598 | 1244979.4307 | 2696028.1089 | 1244979.0855
34 | 2696028.4336 | 1245084.5378 | 2696029.4654 | 1245044.1682
35 | 2696029.4654 | 1245044.1682 | 2696085.2513 | 1245044.9045
36 | 2696278.5689 | 1245138.3107 | 2696283.4748 | 1245157.7608 | 2696283.1352 | 1245157.9824
37 | 2696278.5689 | 1245138.3107 | 2696288.4092 | 1245136.2043
38 | 2696273.7976 | 1245164.0752 | 2696283.1352 | 1245157.9824
39 | 2696273.7976 | 1245164.0752 | 2696284.9003 | 1245181.2173
40 | 2696271.1585 | 1245116.7185 | 2696247.5204 | 1245111.5754 | 2696235.2639 | 1245094.7527
41 | 2696227.8317 | 1245094.0427 | 2696235.2639 | 1245094.7527
42 | 2696028.4336 | 1245084.5378 | 2696064.6486 | 1245083.987
43 | 2696086.5437 | 1245083.654 | 2696064.6486 | 1245083.987
44 | 2696175.5236 | 1244871.725 | 2696163.6523 | 1244868.3856
45 | 2696162.9002 | 1244868.1621 | 2696163.6523 | 1244868.3856
46 | 2696103.8345 | 1244757.0426 | 2696091.8467 | 1244785.0423
47 | 2696103.8345 | 1244757.0426 | 2696116.4941 | 1244761.9737
48 | 2696103.8345 | 1244757.0426 | 2696090.6621 | 1244751.9059
49 | 2696116.4941 | 1244761.9737 | 2696135.8182 | 1244769.5008
50 | 2696138.4164 | 1244770.5128 | 2696135.8182 | 1244769.5008
51 | 2696155.1379 | 1244777.823 | 2696143.6003 | 1244772.532 | 2696138.4164 | 1244770.5128
52 | 2696270.2054 | 1244842.5755 | 2696262.4977 | 1244860.8427
53 | 2696276.33 | 1244828.0601 | 2696270.2054 | 1244842.5755
54 | 2696259.9946 | 1244866.7749 | 2696262.4977 | 1244860.8427
55 | 2696276.33 | 1244828.0601 | 2696301.5507 | 1244838.1994
56 | 2696276.33 | 1244828.0601 | 2696258.8031 | 1244820.7947
57 | 2696251.2447 | 1244887.7763 | 2696252.1452 | 1244885.378 | 2696259.9946 | 1244866.7749
58 | 2696301.5507 | 1244838.1994 | 2696306.0626 | 1244827.345
59 | 2696258.8031 | 1244820.7947 | 2696252.7767 | 1244818.2966
60 | 2696251.2447 | 1244887.7763 | 2696241.8258 | 1244886.0667 | 2696239.6434 | 1244885.668
61 | 2696251.2447 | 1244887.7763 | 2696257.7173 | 1244888.96 | 2696263.3166 | 1244890.3683
62 | 2696306.0626 | 1244827.345 | 2696310.375 | 1244816.9709 | 2696319.9295 | 1244804.3963
63 | 2696252.7767 | 1244818.2966 | 2696237.6727 | 1244812.0357
64 | 2696199.3958 | 1244877.8723 | 2696222.3855 | 1244882.5153 | 2696239.6434 | 1244885.668
65 | 2696208.4665 | 1244692.8784 | 2696210.1121 | 1244690.6701 | 2696212.0988 | 1244688.4006 | 2696214.4775 | 1244687.1271 | 2696217.1927 | 1244686.5373 | 2696230.2147 | 1244686.967
66 | 2696208.4665 | 1244692.8784 | 2696222.9695 | 1244703.8488
67 | 2696176.5569 | 1244683.187 | 2696179.7136 | 1244678.2122 | 2696205.5001 | 1244696.8445 | 2696208.4665 | 1244692.8784
68 | 2696230.2147 | 1244686.967 | 2696243.7283 | 1244687.4129 | 2696253.926 | 1244687.256 | 2696261.6759 | 1244686.807
69 | 2696222.9695 | 1244703.8488 | 2696244.5051 | 1244720.1388
70 | 2696176.5569 | 1244683.187 | 2696179.7246 | 1244684.9842 | 2696193.3382 | 1244694.1563 | 2696204.3511 | 1244702.5644
71 | 2696231.6564 | 1244723.4111 | 2696204.3511 | 1244702.5644
72 | 2696327.0256 | 1244681.0599 | 2696311.737 | 1244682.4238
73 | 2696327.0256 | 1244681.0599 | 2696325.3814 | 1244666.4626
74 | 2696311.737 | 1244682.4238 | 2696312.8524 | 1244696.5749 | 2696323.7676 | 1244700.633
75 | 2696311.737 | 1244682.4238 | 2696298.7556 | 1244683.5853
76 | 2696324.6297 | 1244659.7883 | 2696325.3814 | 1244666.4626
77 | 2696314.3919 | 1244773.0026 | 2696302.5615 | 1244764.0538
78 | 2696314.3919 | 1244773.0026 | 2696319.0784 | 1244766.7946
79 | 2696314.3919 | 1244773.0026 | 2696311.1478 | 1244777.3087 | 2696329.8282 | 1244791.3672 | 2696326.9167 | 1244795.2006
80 | 2696283.8706 | 1244749.9156 | 2696302.5615 | 1244764.0538
81 | 2696319.0784 | 1244766.7946 | 2696324.9734 | 1244758.9859 | 2696327.7651 | 1244755.5013
82 | 2696326.9167 | 1244795.2006 | 2696319.9295 | 1244804.3963
83 | 2696231.6564 | 1244723.4111 | 2696225.5096 | 1244731.0108
84 | 2696231.6564 | 1244723.4111 | 2696241.925 | 1244731.1497
85 | 2696212.3658 | 1244747.2614 | 2696225.5096 | 1244731.0108
86 | 2696241.925 | 1244731.1497 | 2696258.6293 | 1244743.7383
87 | 2696235.4401 | 1244811.1102 | 2696237.6727 | 1244812.0357
88 | 2696135.9198 | 1245076.762 | 2696146.1533 | 1245068.043 | 2696148.9279 | 1245065.9956
89 | 2696126.8273 | 1245084.509 | 2696135.9198 | 1245076.762
90 | 2696086.5437 | 1245083.654 | 2696105.5232 | 1245083.3654
91 | 2696209.454 | 1245088.8557 | 2696197.6196 | 1245072.5618
92 | 2696133.6579 | 1245099.1216 | 2696135.1882 | 1245103.0851
93 | 2696126.8273 | 1245084.509 | 2696130.1751 | 1245090.1009 | 2696133.6579 | 1245099.1216
94 | 2696126.8273 | 1245084.509 | 2696118.3397 | 1245083.1705 | 2696105.5232 | 1245083.3654
95 | 2696199.3958 | 1244877.8723 | 2696197.5346 | 1244868.2236 | 2696197.1706 | 1244864.3777
96 | 2696155.1379 | 1244777.823 | 2696156.7094 | 1244799.1813
97 | 2696155.1379 | 1244777.823 | 2696176.4251 | 1244786.6471
98 | 2696155.1379 | 1244777.823 | 2696156.831 | 1244758.5667
99 | 2696159.5218 | 1244819.8316 | 2696157.683 | 1244812.4128 | 2696156.7094 | 1244799.1813
100 | 2696176.4251 | 1244786.6471 | 2696183.0411 | 1244789.3896
101 | 2696156.831 | 1244758.5667 | 2696158.4386 | 1244740.2818
102 | 2696192.259 | 1244793.2106 | 2696183.0411 | 1244789.3896
103 | 2696159.5775 | 1244727.4815 | 2696159.4101 | 1244729.233 | 2696158.4386 | 1244740.2818
104 | 2696192.259 | 1244793.2106 | 2696202.7658 | 1244797.5659
105 | 2696205.8125 | 1244798.8289 | 2696202.7658 | 1244797.5659
106 | 2696205.8125 | 1244798.8289 | 2696219.7035 | 1244804.587
107 | 2696220.885 | 1244805.0768 | 2696219.7035 | 1244804.587
108 | 2696162.9002 | 1244868.1621 | 2696160.6743 | 1244867.4811 | 2696154.6074 | 1244864.5805 | 2696145.657 | 1244859.6094 | 2696140.824 | 1244856.5844 | 2696139.4405 | 1244855.5316
109 | 2696175.5236 | 1244871.725 | 2696178.9669 | 1244868.1781 | 2696179.8883 | 1244863.5562
110 | 2696286.2496 | 1244764.5533 | 2696258.6293 | 1244743.7383
111 | 2696338.7274 | 1244741.8184 | 2696327.7651 | 1244755.5013
112 | 2696283.8706 | 1244749.9156 | 2696263.7498 | 1244734.6959
113 | 2696266.8966 | 1244686.436 | 2696264.7209 | 1244686.6306 | 2696261.6759 | 1244686.807
114 | 2696263.7498 | 1244734.6959 | 2696244.5051 | 1244720.1388
115 | 2696210.4399 | 1244749.6426 | 2696212.3658 | 1244747.2614
116 | 2696298.7556 | 1244683.5853 | 2696296.7107 | 1244683.7683
117 | 2696324.6297 | 1244659.7883 | 2696323.8222 | 1244652.6195 | 2696314.3939 | 1244652.3324
118 | 2696196.6766 | 1244859.1584 | 2696197.1706 | 1244864.3777
119 | 2696196.6766 | 1244859.1584 | 2696188.9995 | 1244865.1384 | 2696179.8883 | 1244863.5562
120 | 2696220.885 | 1244805.0768 | 2696235.4401 | 1244811.1102
121 | 2696266.8966 | 1244686.436 | 2696279.4561 | 1244685.3122
122 | 2696282.1042 | 1244685.0752 | 2696296.7107 | 1244683.7683
123 | 2696282.1042 | 1244685.0752 | 2696279.4561 | 1244685.3122

## bus_geodata
| x | y | coords
0 | 2696170.6169 | 1244946.6886
1 | 2696204.9001 | 1244946.8917
2 | 2696160.6222 | 1244946.6294
3 | 2696262.7943 | 1244959.3294
4 | 2696161.841 | 1244918.083
5 | 2696160.0017 | 1244977.4317
6 | 2696256.3692 | 1244978.4953
7 | 2696160.3242 | 1244896.1603
8 | 2696144.6193 | 1244979.9732
9 | 2696244.0673 | 1244978.3595
10 | 2696364.9718 | 1245096.2593
11 | 2696364.7204 | 1245121.4856
12 | 2696321.1349 | 1245106.2944
13 | 2696166.6839 | 1245029.969
14 | 2696178.8785 | 1245026.8527
15 | 2696124.7107 | 1244975.0246
16 | 2696143.8016 | 1245156.6613
17 | 2696195.7116 | 1245137.0434
18 | 2696142.7557 | 1245122.6851
19 | 2696081.1262 | 1244810.0819
20 | 2696092.2267 | 1244819.491
21 | 2696089.8751 | 1244789.6474
22 | 2696313.5349 | 1245131.9196
23 | 2696188.741 | 1245060.3376
24 | 2696153.4339 | 1245039.8951
25 | 2696196.3986 | 1245134.7528
26 | 2696106.3414 | 1244948.2747
27 | 2696028.1089 | 1244979.0855
28 | 2696026.5721 | 1245032.9243
29 | 2696029.4654 | 1245044.1682
30 | 2696278.5689 | 1245138.3107
31 | 2696283.1352 | 1245157.9824
32 | 2696288.4092 | 1245136.2043
33 | 2696273.7976 | 1245164.0752
34 | 2696284.9003 | 1245181.2173
35 | 2696271.1585 | 1245116.7185
36 | 2696235.2639 | 1245094.7527
37 | 2696227.8317 | 1245094.0427
38 | 2696028.4336 | 1245084.5378
39 | 2696085.2513 | 1245044.9045
40 | 2696064.6486 | 1245083.987
41 | 2696106.7402 | 1244830.5792
42 | 2696163.6523 | 1244868.3856
43 | 2696091.8467 | 1244785.0423
44 | 2696103.8345 | 1244757.0426
45 | 2696116.4941 | 1244761.9737
46 | 2696090.6621 | 1244751.9059
47 | 2696135.8182 | 1244769.5008
48 | 2696138.4164 | 1244770.5128
49 | 2696270.2054 | 1244842.5755
50 | 2696262.4977 | 1244860.8427
51 | 2696276.33 | 1244828.0601
52 | 2696259.9946 | 1244866.7749
53 | 2696301.5507 | 1244838.1994
54 | 2696258.8031 | 1244820.7947
55 | 2696251.2447 | 1244887.7763
56 | 2696306.0626 | 1244827.345
57 | 2696252.7767 | 1244818.2966
58 | 2696239.6434 | 1244885.668
59 | 2696263.3166 | 1244890.3683
60 | 2696208.4665 | 1244692.8784
61 | 2696230.2147 | 1244686.967
62 | 2696222.9695 | 1244703.8488
63 | 2696176.5569 | 1244683.187
64 | 2696204.3511 | 1244702.5644
65 | 2696327.0256 | 1244681.0599
66 | 2696311.737 | 1244682.4238
67 | 2696325.3814 | 1244666.4626
68 | 2696314.3919 | 1244773.0026
69 | 2696302.5615 | 1244764.0538
70 | 2696319.0784 | 1244766.7946
71 | 2696326.9167 | 1244795.2006
72 | 2696319.9295 | 1244804.3963
73 | 2696231.6564 | 1244723.4111
74 | 2696225.5096 | 1244731.0108
75 | 2696241.925 | 1244731.1497
76 | 2696237.6727 | 1244812.0357
77 | 2696148.9279 | 1245065.9956
78 | 2696135.9198 | 1245076.762
79 | 2696086.5437 | 1245083.654
80 | 2696197.6196 | 1245072.5618
81 | 2696135.1882 | 1245103.0851
82 | 2696126.8273 | 1245084.509
83 | 2696199.3958 | 1244877.8723
84 | 2696105.5232 | 1245083.3654
85 | 2696133.6579 | 1245099.1216
86 | 2696155.1379 | 1244777.823
87 | 2696156.7094 | 1244799.1813
88 | 2696176.4251 | 1244786.6471
89 | 2696156.831 | 1244758.5667
90 | 2696159.5218 | 1244819.8316
91 | 2696183.0411 | 1244789.3896
92 | 2696158.4386 | 1244740.2818
93 | 2696192.259 | 1244793.2106
94 | 2696202.7658 | 1244797.5659
95 | 2696205.8125 | 1244798.8289
96 | 2696219.7035 | 1244804.587
97 | 2696139.4405 | 1244855.5316
98 | 2696162.9002 | 1244868.1621
99 | 2696175.5236 | 1244871.725
100 | 2696286.2496 | 1244764.5533
101 | 2696258.6293 | 1244743.7383
102 | 2696338.7274 | 1244741.8184
103 | 2696327.7651 | 1244755.5013
104 | 2696283.8706 | 1244749.9156
105 | 2696261.6759 | 1244686.807
106 | 2696244.5051 | 1244720.1388
107 | 2696212.3658 | 1244747.2614
108 | 2696323.7676 | 1244700.633
109 | 2696298.7556 | 1244683.5853
110 | 2696324.6297 | 1244659.7883
111 | 2696159.5775 | 1244727.4815
112 | 2696197.1706 | 1244864.3777
113 | 2696196.6766 | 1244859.1584
114 | 2696179.8883 | 1244863.5562
115 | 2696210.4399 | 1244749.6426
116 | 2696235.4401 | 1244811.1102
117 | 2696220.885 | 1244805.0768
118 | 2696209.454 | 1245088.8557
119 | 2696263.7498 | 1244734.6958
120 | 2696266.8966 | 1244686.436
121 | 2696296.7107 | 1244683.7683
122 | 2696282.1042 | 1244685.0752
123 | 2696279.4561 | 1244685.3122
124 | 2696314.3939 | 1244652.3324
125 | 2696196.6766 | 1244859.1584

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98815 | -0.2266 | 0.083996 | 0.021051
1 | 0.98748 | -0.23983 | 0.018119 | 0.0045411
2 | 0.98912 | -0.20778 | 0 | 0
3 | 0.98728 | -0.24364 | 0 | 0
4 | 0.99111 | -0.16959 | 0.025545 | 0.0064021
5 | 0.98798 | -0.22975 | 0 | 0
6 | 0.98721 | -0.24489 | 0 | 0
7 | 0.9928 | -0.13697 | 0.0032673 | 0.00081886
8 | 0.9874 | -0.24096 | 0 | 0
9 | 0.98718 | -0.24566 | 0.0034721 | 0.00087019
10 | 0.97404 | -0.50125 | 0 | 0
11 | 0.97355 | -0.51083 | 0 | 0
12 | 0.97472 | -0.48785 | 0.036094 | 0.009046
13 | 0.98491 | -0.2892 | 0 | 0
14 | 0.98531 | -0.28132 | 0.0074585 | 0.0018693
15 | 0.9873 | -0.24281 | 0 | 0
16 | 0.98205 | -0.34504 | 0 | 0
17 | 0.98168 | -0.35239 | 0 | 0
18 | 0.98229 | -0.34037 | 0.000975 | 0.00024436
19 | 0.98304 | -0.3256 | 0 | 0
20 | 0.98299 | -0.32657 | 0 | 0
21 | 0.98312 | -0.32412 | 0.0013206 | 0.00033097
22 | 0.97276 | -0.52644 | 0.0014693 | 0.00036824
23 | 0.98476 | -0.29227 | 0.002259 | 0.00056617
24 | 0.9844 | -0.29928 | 0 | 0
25 | 0.98166 | -0.3527 | 0.0072047 | 0.0018057
26 | 0.98719 | -0.24504 | 0.0038343 | 0.00096096
27 | 0.97988 | -0.3876 | 0 | 0
28 | 0.97933 | -0.39825 | 0.010892 | 0.0027297
29 | 0.98057 | -0.37397 | 0 | 0
30 | 0.97235 | -0.53463 | 0 | 0
31 | 0.97222 | -0.53711 | 0.0053292 | 0.0013356
32 | 0.97241 | -0.53342 | 0.0081961 | 0.0020541
33 | 0.97221 | -0.53736 | 0 | 0
34 | 0.97218 | -0.53783 | 0.0012315 | 0.00030864
35 | 0.9772 | -0.43897 | 0 | 0
36 | 0.9794 | -0.39608 | 0.017801 | 0.0044613
37 | 0.97988 | -0.38657 | 0 | 0
38 | 0.98109 | -0.3638 | 0 | 0
39 | 0.98042 | -0.37699 | 0.0029936 | 0.00075027
40 | 0.98156 | -0.35469 | 0.0028533 | 0.00071511
41 | 0.98293 | -0.32779 | 0.0036921 | 0.00092533
42 | 0.9952 | -0.091219 | 0 | 0
43 | 0.98314 | -0.32367 | 0.0093334 | 0.0023392
44 | 0.98355 | -0.31579 | 0 | 0
45 | 0.98375 | -0.31183 | 0.0023966 | 0.00060065
46 | 0.98352 | -0.31627 | 0.0018588 | 0.00046587
47 | 0.9841 | -0.30488 | 0.0033895 | 0.00084949
48 | 0.98416 | -0.30378 | 0.0031295 | 0.00078433
49 | 0.9928 | -0.13656 | 0.00162 | 0.00040602
50 | 0.99417 | -0.11038 | 0.0020426 | 0.00051193
51 | 0.99172 | -0.15727 | 0 | 0
52 | 0.99462 | -0.10181 | 0.0018971 | 0.00047545
53 | 0.99048 | -0.18098 | 0 | 0
54 | 0.99041 | -0.1825 | 0.0036536 | 0.00091567
55 | 0.99623 | -0.071347 | 0 | 0
56 | 0.98994 | -0.19128 | 0.0020008 | 0.00050145
57 | 0.98998 | -0.19076 | 0.0027339 | 0.00068518
58 | 0.99706 | -0.055463 | 0.0018628 | 0.00046686
59 | 0.9962 | -0.071774 | 0.00197 | 0.00049372
60 | 0.98027 | -0.37804 | 0 | 0
61 | 0.97938 | -0.39551 | 0.0037746 | 0.00094601
62 | 0.98202 | -0.34403 | 0.0014796 | 0.00037081
63 | 0.97774 | -0.4274 | 0 | 0
64 | 0.97573 | -0.46683 | 0.0046731 | 0.0011712
65 | 0.97669 | -0.44825 | 0 | 0
66 | 0.97695 | -0.44321 | 0 | 0
67 | 0.97645 | -0.45308 | 0.0046934 | 0.0011763
68 | 0.98675 | -0.25254 | 0 | 0
69 | 0.98613 | -0.26448 | 0.0015946 | 0.00039965
70 | 0.98671 | -0.25338 | 0.0015335 | 0.00038434
71 | 0.98821 | -0.22435 | 0 | 0
72 | 0.98872 | -0.21468 | 0.0049684 | 0.0012452
73 | 0.97384 | -0.50398 | 0 | 0
74 | 0.97366 | -0.50761 | 0.0048853 | 0.0012244
75 | 0.97338 | -0.51314 | 0.0081769 | 0.0020493
76 | 0.98895 | -0.21071 | 0.0013556 | 0.00033973
77 | 0.9835 | -0.31666 | 0.0011279 | 0.00028267
78 | 0.98299 | -0.32665 | 0.0014848 | 0.00037213
79 | 0.9819 | -0.34806 | 0.0028799 | 0.00072176
80 | 0.98472 | -0.2929 | 0.00057116 | 0.00014315
81 | 0.98245 | -0.33727 | 0.00129 | 0.00032332
82 | 0.98265 | -0.33339 | 0 | 0
83 | 1 | 0 | -0.50871 | -0.13014
84 | 0.98224 | -0.34133 | 0.00089934 | 0.0002254
85 | 0.98249 | -0.33654 | 0.0012926 | 0.00032395
86 | 0.98458 | -0.29553 | 0 | 0
87 | 0.98447 | -0.29781 | 0.0027435 | 0.00068757
88 | 0.98552 | -0.27736 | 0.0022095 | 0.00055376
89 | 0.98436 | -0.29998 | 0.005626 | 0.00141
90 | 0.98441 | -0.29902 | 0.0031984 | 0.00080161
91 | 0.98582 | -0.27144 | 0.0027987 | 0.00070143
92 | 0.98423 | -0.30235 | 0.0048642 | 0.0012191
93 | 0.98627 | -0.26269 | 0.0019612 | 0.00049152
94 | 0.9868 | -0.25234 | 0.0056414 | 0.0014139
95 | 0.98697 | -0.249 | 0.0014269 | 0.0003576
96 | 0.98778 | -0.23343 | 0.0016644 | 0.00041713
97 | 0.99515 | -0.092124 | 0.0018703 | 0.00046874
98 | 0.99519 | -0.091244 | 0 | 0
99 | 0.99616 | -0.072755 | 0 | 0
100 | 0.97216 | -0.53719 | 0.019262 | 0.0048275
101 | 0.97278 | -0.52491 | 0.011311 | 0.0028348
102 | 0.98662 | -0.2551 | 0.0018612 | 0.00046646
103 | 0.98665 | -0.25452 | 0.0026149 | 0.00065535
104 | 0.98516 | -0.28316 | 0.011394 | 0.0028556
105 | 0.97833 | -0.41604 | 0.0018985 | 0.00047582
106 | 0.98334 | -0.3185 | 0.01205 | 0.0030199
107 | 0.97336 | -0.5135 | 0.0092712 | 0.0023236
108 | 0.97676 | -0.44691 | 0.007855 | 0.0019686
109 | 0.97726 | -0.43705 | 0.0012534 | 0.00031412
110 | 0.97636 | -0.45472 | 0.006219 | 0.0015586
111 | 0.98421 | -0.30289 | 0.00232 | 0.00058145
112 | 0.99888 | -0.021261 | 0.0050331 | 0.0012614
113 | 0.99845 | -0.029262 | 0 | 0
114 | 0.99693 | -0.058283 | 0.0057926 | 0.0014518
115 | 0.97334 | -0.51384 | 0.0060504 | 0.0015164
116 | 0.9888 | -0.2136 | 0.0014853 | 0.00037224
117 | 0.98785 | -0.23207 | 0.0061031 | 0.0015296
118 | 0.98469 | -0.29352 | 0.0017223 | 0.00043165
119 | 0.98421 | -0.30158 | 0.0050548 | 0.0012669
120 | 0.97817 | -0.41928 | 0.0013756 | 0.00034475
121 | 0.97731 | -0.43604 | 0.0019729 | 0.00049447
122 | 0.97771 | -0.42825 | 0.0014571 | 0.00036517
123 | 0.97779 | -0.42677 | 0.0020318 | 0.00050922
124 | 0.97626 | -0.45688 | 0.0071026 | 0.0017801
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.021606 | 0.005419 | -0.021592 | -0.0054107 | 1.361e-05 | 8.2717e-06 | 0.032537 | 0.032537 | 0.032537 | 0.98815 | -0.2266 | 0.98748 | -0.23983 | 8.9387
1 | -0.1056 | -0.02647 | 0.1057 | 0.026531 | 9.4782e-05 | 6.0532e-05 | 0.15902 | 0.15902 | 0.15902 | 0.98815 | -0.2266 | 0.98912 | -0.20778 | 43.6874
2 | 0.0034731 | 0.00086961 | -0.0034724 | -0.00086999 | 6.3015e-07 | -3.8144e-07 | 0.0052332 | 0.0052335 | 0.0052335 | 0.98748 | -0.23983 | 0.98728 | -0.24364 | 1.4378
3 | -0.22677 | -0.05733 | 0.22719 | 0.057595 | 0.00041614 | 0.00026523 | 0.34132 | 0.34132 | 0.34132 | 0.98912 | -0.20778 | 0.99111 | -0.16959 | 31.2567
4 | 0.12107 | 0.030799 | -0.12094 | -0.030718 | 0.00012803 | 8.0751e-05 | 0.1823 | 0.1823 | 0.1823 | 0.98912 | -0.20778 | 0.98798 | -0.22975 | 16.6943
5 | 0.0034724 | 0.00086999 | -0.0034722 | -0.00087012 | 2.0782e-07 | -1.2571e-07 | 0.0052335 | 0.0052336 | 0.0052336 | 0.98728 | -0.24364 | 0.98721 | -0.24489 | 1.4378
6 | -0.25273 | -0.063997 | 0.25313 | 0.06425 | 0.00039654 | 0.00025293 | 0.37967 | 0.37967 | 0.37967 | 0.99111 | -0.16959 | 0.9928 | -0.13697 | 34.7688
7 | 0.12094 | 0.030718 | -0.12088 | -0.030677 | 6.5205e-05 | 4.1129e-05 | 0.1823 | 0.1823 | 0.1823 | 0.98798 | -0.22975 | 0.9874 | -0.24096 | 16.6944
8 | 0.0034722 | 0.00087012 | -0.0034721 | -0.00087019 | 1.2637e-07 | -7.642e-08 | 0.0052336 | 0.0052337 | 0.0052337 | 0.98721 | -0.24489 | 0.98718 | -0.24566 | 1.4378
9 | -0.25639 | -0.065069 | 0.25696 | 0.06543 | 0.00056565 | 0.00036083 | 0.38457 | 0.38457 | 0.38457 | 0.9928 | -0.13697 | 0.9952 | -0.091219 | 35.2172
10 | 0.038658 | 0.009763 | -0.038569 | -0.0097069 | 8.9147e-05 | 5.6161e-05 | 0.058284 | 0.058285 | 0.058285 | 0.9874 | -0.24096 | 0.98491 | -0.2892 | 16.0123
11 | 0.078386 | 0.019953 | -0.078234 | -0.019857 | 0.00015221 | 9.5929e-05 | 0.11824 | 0.11824 | 0.11824 | 0.9874 | -0.24096 | 0.98531 | -0.28132 | 16.2417
12 | 0.003835 | 0.00096067 | -0.0038347 | -0.0009608 | 3.3749e-07 | -1.2862e-07 | 0.0057792 | 0.0057793 | 0.0057793 | 0.9874 | -0.24096 | 0.9873 | -0.24281 | 1.5877
13 | 0.016252 | 0.0040809 | -0.016244 | -0.0040766 | 7.4229e-06 | 4.3512e-06 | 0.02483 | 0.02483 | 0.02483 | 0.97404 | -0.50125 | 0.97355 | -0.51083 | 6.8215
14 | -0.016252 | -0.0040809 | 0.016262 | 0.004087 | 1.0399e-05 | 6.095e-06 | 0.02483 | 0.02483 | 0.02483 | 0.97404 | -0.50125 | 0.97472 | -0.48785 | 6.8215
15 | 0.016244 | 0.0040766 | -0.016232 | -0.0040695 | 1.2087e-05 | 7.0861e-06 | 0.02483 | 0.024831 | 0.024831 | 0.97355 | -0.51083 | 0.97276 | -0.52644 | 6.8216
16 | -0.052356 | -0.013133 | 0.052478 | 0.013211 | 0.00012231 | 7.7643e-05 | 0.079931 | 0.079931 | 0.079931 | 0.97472 | -0.48785 | 0.9772 | -0.43897 | 21.9592
17 | 0.0045533 | 0.0011405 | -0.0045526 | -0.0011406 | 6.6604e-07 | -5.1326e-08 | 0.0068789 | 0.0068791 | 0.0068791 | 0.98491 | -0.2892 | 0.98476 | -0.29227 | 1.8899
18 | 0.034016 | 0.0085663 | -0.033999 | -0.0085561 | 1.6377e-05 | 1.0271e-05 | 0.051406 | 0.051406 | 0.051406 | 0.98491 | -0.2892 | 0.9844 | -0.29928 | 14.1225
19 | 0.070776 | 0.017988 | -0.070419 | -0.017761 | 0.00035676 | 0.00022727 | 0.10698 | 0.10698 | 0.10698 | 0.98531 | -0.28132 | 0.97988 | -0.38657 | 29.389
20 | 0.0038347 | 0.0009608 | -0.0038343 | -0.00096096 | 4.0723e-07 | -1.551e-07 | 0.0057793 | 0.0057795 | 0.0057795 | 0.9873 | -0.24281 | 0.98719 | -0.24504 | 1.5878
21 | 0.0072073 | 0.0018066 | -0.0072048 | -0.0018057 | 2.5222e-06 | 9.0096e-07 | 0.010921 | 0.010921 | 0.010921 | 0.98205 | -0.34504 | 0.98168 | -0.35239 | 3.0003
22 | -0.0072073 | -0.0018066 | 0.0072089 | 0.0018072 | 1.6044e-06 | 5.728e-07 | 0.010921 | 0.010921 | 0.010921 | 0.98205 | -0.34504 | 0.98229 | -0.34037 | 3.0002
23 | 0.0072048 | 0.0018057 | -0.0072047 | -0.0018057 | 1.0696e-07 | 3.8219e-08 | 0.010921 | 0.010921 | 0.010921 | 0.98168 | -0.35239 | 0.98166 | -0.3527 | 3.0003
24 | -0.0081839 | -0.0020515 | 0.0081851 | 0.002052 | 1.211e-06 | 5.0901e-07 | 0.012398 | 0.012397 | 0.012398 | 0.98229 | -0.34037 | 0.98245 | -0.33727 | 3.4059
25 | 0.0036925 | 0.00092516 | -0.0036923 | -0.00092523 | 1.7019e-07 | -7.5257e-08 | 0.0055892 | 0.0055892 | 0.0055892 | 0.98304 | -0.3256 | 0.98299 | -0.32657 | 1.5355
26 | -0.0036925 | -0.00092516 | 0.0036927 | 0.00092504 | 2.6039e-07 | -1.1519e-07 | 0.0055892 | 0.0055891 | 0.0055892 | 0.98304 | -0.3256 | 0.98312 | -0.32412 | 1.5355
27 | 0.0036923 | 0.00092523 | -0.0036921 | -0.00092533 | 2.1397e-07 | -9.4583e-08 | 0.0055892 | 0.0055893 | 0.0055893 | 0.98299 | -0.32657 | 0.98293 | -0.32779 | 1.5355
28 | -0.0050133 | -0.001256 | 0.0050135 | 0.001256 | 1.0816e-07 | 5.6992e-09 | 0.0075879 | 0.0075878 | 0.0075879 | 0.98312 | -0.32412 | 0.98314 | -0.32367 | 2.0846
29 | 0.014763 | 0.0037012 | -0.014758 | -0.0036984 | 4.9024e-06 | 2.8195e-06 | 0.022583 | 0.022583 | 0.022583 | 0.97276 | -0.52644 | 0.97241 | -0.53342 | 6.2042
30 | 0.0022936 | 0.00057442 | -0.0022935 | -0.00057457 | 6.8046e-08 | -1.4866e-07 | 0.0034656 | 0.0034656 | 0.0034656 | 0.98476 | -0.29227 | 0.98472 | -0.2929 | 0.9521
31 | 0.033999 | 0.0085561 | -0.033971 | -0.0085384 | 2.8226e-05 | 1.7703e-05 | 0.051406 | 0.051406 | 0.051406 | 0.9844 | -0.29928 | 0.9835 | -0.31666 | 14.1226
32 | 0.010897 | 0.0027325 | -0.010892 | -0.0027297 | 5.5314e-06 | 2.862e-06 | 0.016549 | 0.016549 | 0.016549 | 0.97988 | -0.3876 | 0.97933 | -0.39825 | 4.5464
33 | -0.010897 | -0.0027325 | 0.010904 | 0.0027362 | 7.0838e-06 | 3.6641e-06 | 0.016549 | 0.016548 | 0.016549 | 0.97988 | -0.3876 | 0.98057 | -0.37397 | 4.5463
34 | -0.013898 | -0.0034861 | 0.013905 | 0.0034899 | 6.7375e-06 | 3.8022e-06 | 0.021092 | 0.021091 | 0.021092 | 0.98057 | -0.37397 | 0.98109 | -0.3638 | 5.7944
35 | 0.002994 | 0.00074984 | -0.0029936 | -0.00075027 | 4.3187e-07 | -4.2726e-07 | 0.0045432 | 0.0045435 | 0.0045435 | 0.98057 | -0.37397 | 0.98042 | -0.37699 | 1.2482
36 | 0.0065615 | 0.0016441 | -0.0065608 | -0.0016439 | 7.7378e-07 | 2.4141e-07 | 0.010041 | 0.010041 | 0.010041 | 0.97235 | -0.53463 | 0.97222 | -0.53711 | 2.7586
37 | -0.0065615 | -0.0016441 | 0.0065619 | 0.0016443 | 3.8049e-07 | 1.1868e-07 | 0.010041 | 0.010041 | 0.010041 | 0.97235 | -0.53463 | 0.97241 | -0.53342 | 2.7586
38 | 0.0012315 | 0.00030827 | -0.0012315 | -0.0003084 | 1.4853e-08 | -1.2875e-07 | 0.0018847 | 0.0018848 | 0.0018848 | 0.97222 | -0.53711 | 0.97221 | -0.53736 | 0.5178
39 | 0.0012315 | 0.0003084 | -0.0012315 | -0.00030864 | 2.7209e-08 | -2.3584e-07 | 0.0018848 | 0.0018849 | 0.0018849 | 0.97221 | -0.53736 | 0.97218 | -0.53783 | 0.51783
40 | -0.052478 | -0.013211 | 0.052586 | 0.013279 | 0.00010783 | 6.8444e-05 | 0.079931 | 0.079931 | 0.079931 | 0.9772 | -0.43897 | 0.9794 | -0.39608 | 21.9591
41 | -0.070387 | -0.01774 | 0.070419 | 0.017761 | 3.204e-05 | 2.0412e-05 | 0.10698 | 0.10698 | 0.10698 | 0.9794 | -0.39608 | 0.97988 | -0.38657 | 29.389
42 | -0.013905 | -0.0034899 | 0.013911 | 0.0034933 | 6.0419e-06 | 3.4093e-06 | 0.021091 | 0.021091 | 0.021091 | 0.98109 | -0.3638 | 0.98156 | -0.35469 | 5.7943
43 | -0.016764 | -0.0042084 | 0.01677 | 0.0042115 | 5.3048e-06 | 3.1182e-06 | 0.025417 | 0.025417 | 0.025417 | 0.98156 | -0.35469 | 0.9819 | -0.34806 | 6.9826
44 | -0.25883 | -0.065898 | 0.25906 | 0.066045 | 0.00023067 | 0.00014715 | 0.38737 | 0.38737 | 0.38737 | 0.9952 | -0.091219 | 0.99616 | -0.072755 | 35.4732
45 | 0.0018704 | 0.00046843 | -0.0018704 | -0.00046844 | 2.2934e-09 | -8.6932e-09 | 0.0027965 | 0.0027965 | 0.0027965 | 0.9952 | -0.091219 | 0.99519 | -0.091244 | 0.76826
46 | -0.014347 | -0.0035952 | 0.014352 | 0.0035983 | 5.3854e-06 | 3.0603e-06 | 0.021714 | 0.021714 | 0.021714 | 0.98314 | -0.32367 | 0.98355 | -0.31579 | 5.9655
47 | -0.016211 | -0.004064 | 0.016214 | 0.0040658 | 3.0647e-06 | 1.789e-06 | 0.024526 | 0.024526 | 0.024526 | 0.98355 | -0.31579 | 0.98375 | -0.31183 | 6.738
48 | 0.0018589 | 0.00046571 | -0.0018588 | -0.00046587 | 4.1933e-08 | -1.5259e-07 | 0.0028122 | 0.0028123 | 0.0028123 | 0.98355 | -0.31579 | 0.98352 | -0.31627 | 0.77261
49 | -0.018611 | -0.0046664 | 0.018617 | 0.0046701 | 6.1632e-06 | 3.681e-06 | 0.028151 | 0.028151 | 0.028151 | 0.98375 | -0.31183 | 0.9841 | -0.30488 | 7.7339
50 | -0.022006 | -0.0055196 | 0.022008 | 0.0055203 | 1.1579e-06 | 7.0559e-07 | 0.033276 | 0.033276 | 0.033276 | 0.9841 | -0.30488 | 0.98416 | -0.30378 | 9.1419
51 | -0.025137 | -0.0063046 | 0.025147 | 0.0063107 | 9.89e-06 | 6.0975e-06 | 0.038008 | 0.038008 | 0.038008 | 0.98416 | -0.30378 | 0.98458 | -0.29553 | 10.4418
52 | -0.22693 | -0.05786 | 0.22721 | 0.058043 | 0.00028729 | 0.0001831 | 0.34047 | 0.34047 | 0.34047 | 0.9928 | -0.13656 | 0.99417 | -0.11038 | 31.1786
53 | 0.22531 | 0.057454 | -0.22508 | -0.057311 | 0.00022504 | 0.00014342 | 0.33804 | 0.33804 | 0.33804 | 0.9928 | -0.13656 | 0.99172 | -0.15727 | 30.9563
54 | -0.22926 | -0.058555 | 0.22935 | 0.058616 | 9.4978e-05 | 6.0536e-05 | 0.34353 | 0.34353 | 0.34353 | 0.99417 | -0.11038 | 0.99462 | -0.10181 | 31.4586
55 | 0.14974 | 0.038263 | -0.14957 | -0.038154 | 0.00017148 | 0.0001087 | 0.22494 | 0.22494 | 0.22494 | 0.99172 | -0.15727 | 0.99048 | -0.18098 | 20.5987
56 | 0.075343 | 0.019048 | -0.075251 | -0.01899 | 9.1021e-05 | 5.8009e-05 | 0.11311 | 0.11311 | 0.11311 | 0.99172 | -0.15727 | 0.99041 | -0.1825 | 31.0731
57 | -0.23125 | -0.059091 | 0.23159 | 0.059308 | 0.00034121 | 0.00021749 | 0.34637 | 0.34637 | 0.34637 | 0.99462 | -0.10181 | 0.99623 | -0.071347 | 31.7185
58 | 0.14957 | 0.038154 | -0.14949 | -0.038107 | 7.4345e-05 | 4.7127e-05 | 0.22494 | 0.22494 | 0.22494 | 0.99048 | -0.18098 | 0.98994 | -0.19128 | 20.5987
59 | 0.071598 | 0.018074 | -0.07157 | -0.018056 | 2.8332e-05 | 1.8049e-05 | 0.10762 | 0.10762 | 0.10762 | 0.99041 | -0.1825 | 0.98998 | -0.19076 | 29.5651
60 | -0.23356 | -0.059802 | 0.23374 | 0.059917 | 0.00017984 | 0.00011464 | 0.34931 | 0.34931 | 0.34931 | 0.99623 | -0.071347 | 0.99706 | -0.055463 | 31.9879
61 | 0.00197 | 0.00049358 | -0.00197 | -0.00049372 | 4.011e-08 | -1.3518e-07 | 0.0029424 | 0.0029425 | 0.0029425 | 0.99623 | -0.071347 | 0.9962 | -0.071774 | 0.80838
62 | 0.14749 | 0.037606 | -0.14733 | -0.0375 | 0.0001664 | 0.00010545 | 0.22193 | 0.22193 | 0.22193 | 0.98994 | -0.19128 | 0.98872 | -0.21468 | 20.3233
63 | 0.068836 | 0.017371 | -0.06877 | -0.017329 | 6.569e-05 | 4.1832e-05 | 0.10351 | 0.10351 | 0.10351 | 0.98998 | -0.19076 | 0.98895 | -0.21071 | 28.4362
64 | -0.2356 | -0.060384 | 0.23624 | 0.060788 | 0.00063528 | 0.00040497 | 0.35209 | 0.35209 | 0.35209 | 0.99706 | -0.055463 | 1 | 0 | 32.2424
65 | 0.039753 | 0.010007 | -0.03972 | -0.009986 | 3.3166e-05 | 2.092e-05 | 0.060359 | 0.060359 | 0.060359 | 0.98027 | -0.37804 | 0.97938 | -0.39551 | 16.5821
66 | -0.10381 | -0.026227 | 0.10398 | 0.026335 | 0.0001695 | 0.00010825 | 0.15766 | 0.15766 | 0.15766 | 0.98027 | -0.37804 | 0.98202 | -0.34403 | 43.3127
67 | 0.06406 | 0.01622 | -0.063908 | -0.016123 | 0.00015144 | 9.6388e-05 | 0.097299 | 0.0973 | 0.0973 | 0.98027 | -0.37804 | 0.97774 | -0.4274 | 26.7306
68 | 0.035945 | 0.00904 | -0.03591 | -0.0090178 | 3.5227e-05 | 2.2149e-05 | 0.054624 | 0.054624 | 0.054624 | 0.97938 | -0.39551 | 0.97833 | -0.41604 | 15.0066
69 | -0.10546 | -0.026706 | 0.10559 | 0.026788 | 0.00012945 | 8.2164e-05 | 0.1599 | 0.1599 | 0.1599 | 0.98202 | -0.34403 | 0.98334 | -0.3185 | 21.9643
70 | 0.063908 | 0.016123 | -0.063788 | -0.016047 | 0.0001204 | 7.663e-05 | 0.0973 | 0.0973 | 0.0973 | 0.97774 | -0.4274 | 0.97573 | -0.46683 | 26.7307
71 | 0.059115 | 0.014875 | -0.05901 | -0.014809 | 0.00010475 | 6.6612e-05 | 0.090173 | 0.090173 | 0.090173 | 0.97573 | -0.46683 | 0.97384 | -0.50398 | 24.7728
72 | -0.018021 | -0.0045183 | 0.018025 | 0.0045209 | 4.3262e-06 | 2.5772e-06 | 0.027456 | 0.027456 | 0.027456 | 0.97669 | -0.44825 | 0.97695 | -0.44321 | 7.5429
73 | 0.018021 | 0.0045183 | -0.018017 | -0.0045158 | 4.1526e-06 | 2.4738e-06 | 0.027456 | 0.027456 | 0.027456 | 0.97669 | -0.44825 | 0.97645 | -0.45308 | 7.5429
74 | 0.0078564 | 0.0019692 | -0.007855 | -0.0019686 | 1.386e-06 | 5.6391e-07 | 0.011966 | 0.011966 | 0.011966 | 0.97695 | -0.44321 | 0.97676 | -0.44691 | 3.2875
75 | -0.025882 | -0.0064901 | 0.025889 | 0.0064948 | 7.5957e-06 | 4.698e-06 | 0.039422 | 0.039422 | 0.039422 | 0.97695 | -0.44321 | 0.97726 | -0.43705 | 10.8303
76 | 0.013323 | 0.0033396 | -0.013322 | -0.003339 | 1.0383e-06 | 5.8051e-07 | 0.020304 | 0.020304 | 0.020304 | 0.97645 | -0.45308 | 0.97636 | -0.45472 | 5.578
77 | 0.13609 | 0.034585 | -0.13601 | -0.034535 | 7.8221e-05 | 4.9493e-05 | 0.20539 | 0.20539 | 0.20539 | 0.98675 | -0.25254 | 0.98613 | -0.26448 | 18.8087
78 | 0.0060101 | 0.001506 | -0.0060099 | -0.0015059 | 2.3959e-07 | 5.3985e-08 | 0.0090632 | 0.0090632 | 0.0090632 | 0.98675 | -0.25254 | 0.98671 | -0.25338 | 2.4899
79 | -0.1421 | -0.036091 | 0.14229 | 0.036213 | 0.00019307 | 0.00012228 | 0.21445 | 0.21445 | 0.21445 | 0.98675 | -0.25254 | 0.98821 | -0.22435 | 19.6386
80 | 0.13441 | 0.034136 | -0.13429 | -0.034059 | 0.0001207 | 7.6354e-05 | 0.20298 | 0.20298 | 0.20298 | 0.98613 | -0.26448 | 0.98516 | -0.28316 | 18.5884
81 | 0.0044764 | 0.0011216 | -0.0044761 | -0.0011216 | 2.435e-07 | -2.6151e-08 | 0.0067505 | 0.0067506 | 0.0067506 | 0.98671 | -0.25338 | 0.98665 | -0.25452 | 1.8546
82 | -0.14229 | -0.036213 | 0.14236 | 0.036255 | 6.6393e-05 | 4.2048e-05 | 0.21445 | 0.21445 | 0.21445 | 0.98821 | -0.22435 | 0.98872 | -0.21468 | 19.6386
83 | 0.020215 | 0.0050689 | -0.020211 | -0.0050668 | 3.4972e-06 | 2.1166e-06 | 0.030889 | 0.030889 | 0.030889 | 0.97384 | -0.50398 | 0.97366 | -0.50761 | 8.4859
84 | 0.038795 | 0.0097398 | -0.038778 | -0.0097291 | 1.6947e-05 | 1.0686e-05 | 0.059285 | 0.059285 | 0.059285 | 0.97384 | -0.50398 | 0.97338 | -0.51314 | 16.287
85 | 0.015326 | 0.0038425 | -0.015322 | -0.00384 | 4.3e-06 | 2.4921e-06 | 0.023423 | 0.023423 | 0.023423 | 0.97366 | -0.50761 | 0.97336 | -0.5135 | 6.4348
86 | 0.030601 | 0.0076798 | -0.030584 | -0.0076691 | 1.7168e-05 | 1.0728e-05 | 0.046784 | 0.046785 | 0.046785 | 0.97338 | -0.51314 | 0.97278 | -0.52491 | 12.8529
87 | 0.067414 | 0.016989 | -0.067405 | -0.016983 | 9.3313e-06 | 5.941e-06 | 0.10147 | 0.10147 | 0.10147 | 0.98895 | -0.21071 | 0.9888 | -0.2136 | 27.8758
88 | 0.032843 | 0.0082557 | -0.032828 | -0.0082459 | 1.5647e-05 | 9.7998e-06 | 0.0497 | 0.0497 | 0.0497 | 0.9835 | -0.31666 | 0.98299 | -0.32665 | 13.6538
89 | 0.031343 | 0.0078738 | -0.031333 | -0.0078675 | 1.0086e-05 | 6.304e-06 | 0.047452 | 0.047452 | 0.047452 | 0.98299 | -0.32665 | 0.98265 | -0.33339 | 13.0363
90 | -0.019649 | -0.0049333 | 0.019656 | 0.0049371 | 6.3131e-06 | 3.8002e-06 | 0.029781 | 0.029781 | 0.029781 | 0.9819 | -0.34806 | 0.98224 | -0.34133 | 8.1816
91 | 0.0017223 | 0.00043142 | -0.0017223 | -0.00043165 | 5.1152e-08 | -2.2344e-07 | 0.0026025 | 0.0026026 | 0.0026026 | 0.98472 | -0.2929 | 0.98469 | -0.29352 | 0.71501
92 | -0.0094752 | -0.0023754 | 0.0094755 | 0.0023755 | 3.2814e-07 | 1.5621e-07 | 0.014351 | 0.014351 | 0.014351 | 0.98245 | -0.33727 | 0.98249 | -0.33654 | 3.9427
93 | 0.01077 | 0.0027003 | -0.010768 | -0.0026995 | 1.6146e-06 | 8.283e-07 | 0.016309 | 0.016309 | 0.016309 | 0.98265 | -0.33339 | 0.98249 | -0.33654 | 4.4805
94 | 0.020563 | 0.0051672 | -0.020555 | -0.0051625 | 7.7873e-06 | 4.7127e-06 | 0.031143 | 0.031143 | 0.031143 | 0.98265 | -0.33339 | 0.98224 | -0.34133 | 8.5559
95 | 0.27082 | 0.069355 | -0.27054 | -0.069177 | 0.00027862 | 0.00017778 | 0.40351 | 0.40351 | 0.40351 | 1 | 0 | 0.99888 | -0.021261 | 36.9515
96 | 0.0059427 | 0.0014892 | -0.0059421 | -0.001489 | 6.4781e-07 | 1.4226e-07 | 0.0089813 | 0.0089814 | 0.0089814 | 0.98458 | -0.29553 | 0.98447 | -0.29781 | 2.4674
97 | -0.043904 | -0.011012 | 0.043942 | 0.011036 | 3.8048e-05 | 2.4057e-05 | 0.066355 | 0.066355 | 0.066355 | 0.98458 | -0.29553 | 0.98552 | -0.27736 | 18.2295
98 | 0.012814 | 0.0032122 | -0.012811 | -0.0032107 | 2.7187e-06 | 1.4942e-06 | 0.019366 | 0.019366 | 0.019366 | 0.98458 | -0.29553 | 0.98436 | -0.29998 | 5.3203
99 | 0.0031986 | 0.00080146 | -0.0031984 | -0.00080161 | 1.8329e-07 | -1.4855e-07 | 0.0048346 | 0.0048347 | 0.0048347 | 0.98447 | -0.29781 | 0.98441 | -0.29902 | 1.3282
100 | -0.046151 | -0.01159 | 0.046164 | 0.011598 | 1.3044e-05 | 8.2569e-06 | 0.069691 | 0.069691 | 0.069691 | 0.98552 | -0.27736 | 0.98582 | -0.27144 | 19.146
101 | 0.007185 | 0.0018007 | -0.0071842 | -0.0018004 | 8.1202e-07 | 2.8639e-07 | 0.010861 | 0.010861 | 0.010861 | 0.98436 | -0.29998 | 0.98423 | -0.30235 | 2.9839
102 | -0.048963 | -0.0123 | 0.048983 | 0.012313 | 2.0444e-05 | 1.2957e-05 | 0.073916 | 0.073916 | 0.073916 | 0.98582 | -0.27144 | 0.98627 | -0.26269 | 20.3065
103 | 0.0023201 | 0.00058132 | -0.00232 | -0.00058145 | 5.9289e-08 | -1.2537e-07 | 0.0035075 | 0.0035076 | 0.0035076 | 0.98423 | -0.30235 | 0.98421 | -0.30289 | 0.96362
104 | -0.050945 | -0.012804 | 0.05097 | 0.01282 | 2.5206e-05 | 1.5986e-05 | 0.076875 | 0.076875 | 0.076875 | 0.98627 | -0.26269 | 0.9868 | -0.25234 | 21.1194
105 | -0.056611 | -0.014234 | 0.05662 | 0.01424 | 9.0161e-06 | 5.7281e-06 | 0.085381 | 0.085381 | 0.085381 | 0.9868 | -0.25234 | 0.98697 | -0.249 | 23.4564
106 | -0.058047 | -0.014597 | 0.05809 | 0.014625 | 4.3205e-05 | 2.7459e-05 | 0.087533 | 0.087532 | 0.087533 | 0.98697 | -0.249 | 0.98778 | -0.23343 | 24.0474
107 | -0.059755 | -0.015042 | 0.059759 | 0.015044 | 3.8881e-06 | 2.472e-06 | 0.09004 | 0.09004 | 0.09004 | 0.98778 | -0.23343 | 0.98785 | -0.23207 | 24.7362
108 | -0.0018703 | -0.00046874 | 0.0018704 | 0.00046844 | 7.8394e-08 | -2.9714e-07 | 0.0027966 | 0.0027965 | 0.0027966 | 0.99515 | -0.092124 | 0.99519 | -0.091244 | 0.76829
109 | -0.25906 | -0.066045 | 0.25924 | 0.066161 | 0.00018112 | 0.00011554 | 0.38737 | 0.38737 | 0.38737 | 0.99616 | -0.072755 | 0.99693 | -0.058283 | 35.4732
110 | -0.019262 | -0.0048275 | 0.019273 | 0.0048343 | 1.1273e-05 | 6.7859e-06 | 0.029483 | 0.029483 | 0.029483 | 0.97216 | -0.53719 | 0.97278 | -0.52491 | 8.0996
111 | -0.0018612 | -0.00046646 | 0.0018613 | 0.00046627 | 5.1805e-08 | -1.9075e-07 | 0.0028071 | 0.002807 | 0.0028071 | 0.98662 | -0.2551 | 0.98665 | -0.25452 | 0.77117
112 | 0.1229 | 0.031204 | -0.12279 | -0.031135 | 0.00010884 | 6.8693e-05 | 0.18578 | 0.18578 | 0.18578 | 0.98516 | -0.28316 | 0.98421 | -0.30158 | 17.0124
113 | 0.034011 | 0.008542 | -0.034006 | -0.0085387 | 5.254e-06 | 3.2969e-06 | 0.051736 | 0.051736 | 0.051736 | 0.97833 | -0.41604 | 0.97817 | -0.41928 | 14.2133
114 | -0.11764 | -0.029808 | 0.11774 | 0.029868 | 9.5711e-05 | 6.0336e-05 | 0.17813 | 0.17813 | 0.17813 | 0.98334 | -0.3185 | 0.98421 | -0.30158 | 16.3126
115 | 0.0060505 | 0.0015164 | -0.0060504 | -0.0015164 | 9.8258e-08 | 2.4819e-08 | 0.0092496 | 0.0092496 | 0.0092496 | 0.97336 | -0.5135 | 0.97334 | -0.51384 | 2.5411
116 | -0.027143 | -0.0068089 | 0.027144 | 0.0068097 | 1.3152e-06 | 8.16e-07 | 0.041331 | 0.041331 | 0.041331 | 0.97726 | -0.43705 | 0.97731 | -0.43604 | 11.3546
117 | 0.0071034 | 0.0017804 | -0.0071026 | -0.0017801 | 7.3162e-07 | 2.6007e-07 | 0.010826 | 0.010826 | 0.010826 | 0.97636 | -0.45472 | 0.97626 | -0.45688 | 2.9742
118 | 0.26551 | 0.067915 | -0.26541 | -0.06785 | 0.00010277 | 6.5569e-05 | 0.39601 | 0.39601 | 0.39601 | 0.99888 | -0.021261 | 0.99845 | -0.029262 | 36.2649
119 | 0.26541 | 0.06785 | -0.26503 | -0.067612 | 0.00037205 | 0.00023737 | 0.39601 | 0.39601 | 0.39601 | 0.99845 | -0.029262 | 0.99693 | -0.058283 | 36.2649
120 | 0.06592 | 0.016611 | -0.065862 | -0.016574 | 5.8182e-05 | 3.7035e-05 | 0.099233 | 0.099233 | 0.099233 | 0.9888 | -0.2136 | 0.98785 | -0.23207 | 27.2618
121 | 0.03263 | 0.008194 | -0.032619 | -0.0081867 | 1.1654e-05 | 7.3002e-06 | 0.049644 | 0.049644 | 0.049644 | 0.97817 | -0.41928 | 0.97779 | -0.42677 | 13.6385
122 | -0.029117 | -0.0073042 | 0.029128 | 0.0073109 | 1.0809e-05 | 6.734e-06 | 0.044334 | 0.044334 | 0.044334 | 0.97731 | -0.43604 | 0.97771 | -0.42825 | 12.1798
123 | -0.030585 | -0.0076761 | 0.030587 | 0.0076774 | 2.1606e-06 | 1.3495e-06 | 0.046552 | 0.046552 | 0.046552 | 0.97771 | -0.42825 | 0.97779 | -0.42677 | 12.789

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50871 | 0.13014

## res_load
| p_mw | q_mvar
0 | 0.083996 | 0.021051
1 | 0.018119 | 0.0045411
2 | 0.025545 | 0.0064021
3 | 0.0032673 | 0.00081886
4 | 0.0034721 | 0.00087019
5 | 0.036094 | 0.009046
6 | 0.0074585 | 0.0018693
7 | 0.000975 | 0.00024436
8 | 0.0013206 | 0.00033097
9 | 0.0014693 | 0.00036824
10 | 0.002259 | 0.00056617
11 | 0.0072047 | 0.0018057
12 | 0.0038343 | 0.00096096
13 | 0.010892 | 0.0027297
14 | 0.0053292 | 0.0013356
15 | 0.0081961 | 0.0020541
16 | 0.0012315 | 0.00030864
17 | 0.017801 | 0.0044613
18 | 0.0029936 | 0.00075027
19 | 0.0028533 | 0.00071511
20 | 0.0036921 | 0.00092533
21 | 0.0093334 | 0.0023392
22 | 0.0023966 | 0.00060065
23 | 0.0018588 | 0.00046587
24 | 0.0033895 | 0.00084949
25 | 0.0031295 | 0.00078433
26 | 0.00162 | 0.00040602
27 | 0.0020426 | 0.00051193
28 | 0.0018971 | 0.00047545
29 | 0.0036536 | 0.00091567
30 | 0.0020008 | 0.00050145
31 | 0.0027339 | 0.00068518
32 | 0.0018628 | 0.00046686
33 | 0.00197 | 0.00049372
34 | 0.0037746 | 0.00094601
35 | 0.0014796 | 0.00037081
36 | 0.0046731 | 0.0011712
37 | 0.0046934 | 0.0011763
38 | 0.0015946 | 0.00039965
39 | 0.0015335 | 0.00038434
40 | 0.0049684 | 0.0012452
41 | 0.0048853 | 0.0012244
42 | 0.0081769 | 0.0020493
43 | 0.0013556 | 0.00033973
44 | 0.0011279 | 0.00028267
45 | 0.0014848 | 0.00037213
46 | 0.0028799 | 0.00072176
47 | 0.00057116 | 0.00014315
48 | 0.00129 | 0.00032332
49 | 0.00089934 | 0.0002254
50 | 0.0012926 | 0.00032395
51 | 0.0027435 | 0.00068757
52 | 0.0022095 | 0.00055376
53 | 0.005626 | 0.00141
54 | 0.0031984 | 0.00080161
55 | 0.0027987 | 0.00070143
56 | 0.0048642 | 0.0012191
57 | 0.0019612 | 0.00049152
58 | 0.0056414 | 0.0014139
59 | 0.0014269 | 0.0003576
60 | 0.0016644 | 0.00041713
61 | 0.0018703 | 0.00046874
62 | 0.019262 | 0.0048275
63 | 0.011311 | 0.0028348
64 | 0.0018612 | 0.00046646
65 | 0.0026149 | 0.00065535
66 | 0.011394 | 0.0028556
67 | 0.0018985 | 0.00047582
68 | 0.01205 | 0.0030199
69 | 0.0092712 | 0.0023236
70 | 0.007855 | 0.0019686
71 | 0.0012534 | 0.00031412
72 | 0.006219 | 0.0015586
73 | 0.00232 | 0.00058145
74 | 0.0050331 | 0.0012614
75 | 0.0057926 | 0.0014518
76 | 0.0060504 | 0.0015164
77 | 0.0014853 | 0.00037224
78 | 0.0061031 | 0.0015296
79 | 0.0017223 | 0.00043165
80 | 0.0050548 | 0.0012669
81 | 0.0013756 | 0.00034475
82 | 0.0019729 | 0.00049447
83 | 0.0014571 | 0.00036517
84 | 0.0020318 | 0.00050922
85 | 0.0071026 | 0.0017801

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1