## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_198-48_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_198-48_0_7_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_198-48_0_7_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_198-48_0_7_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_198-48_0_7_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_198-48_0_7_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_198-48_0_7_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_198-48_0_7_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_198-48_0_7_node_117 | 0.4 | n |  | TRUE
9 | bus_LV_198-48_0_7_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_198-48_0_7_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_198-48_0_7_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_198-48_0_7_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_198-48_0_7_node_154 | 0.4 | n |  | TRUE
14 | bus_LV_198-48_0_7_node_50 | 0.4 | n |  | TRUE
15 | bus_LV_198-48_0_7_node_78 | 0.4 | n |  | TRUE
16 | bus_LV_198-48_0_7_node_114 | 0.4 | n |  | TRUE
17 | bus_LV_198-48_0_7_node_142 | 0.4 | n |  | TRUE
18 | bus_LV_198-48_0_7_node_63 | 0.4 | n |  | TRUE
19 | bus_LV_198-48_0_7_node_51 | 0.4 | n |  | TRUE
20 | bus_LV_198-48_0_7_node_75 | 0.4 | n |  | TRUE
21 | bus_LV_198-48_0_7_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_198-48_0_7_node_116 | 0.4 | n |  | TRUE
23 | bus_LV_198-48_0_7_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_198-48_0_7_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_198-48_0_7_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_198-48_0_7_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_198-48_0_7_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_198-48_0_7_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_198-48_0_7_node_149 | 0.4 | n |  | TRUE
30 | bus_LV_198-48_0_7_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_198-48_0_7_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_198-48_0_7_node_82 | 0.4 | n |  | TRUE
33 | bus_LV_198-48_0_7_node_84 | 0.4 | n |  | TRUE
34 | bus_LV_198-48_0_7_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_198-48_0_7_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_198-48_0_7_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_198-48_0_7_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_198-48_0_7_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_198-48_0_7_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_198-48_0_7_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_198-48_0_7_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_198-48_0_7_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_198-48_0_7_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_198-48_0_7_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_198-48_0_7_node_72 | 0.4 | n |  | TRUE
46 | bus_LV_198-48_0_7_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_198-48_0_7_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_198-48_0_7_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_198-48_0_7_node_108 | 0.4 | n |  | TRUE
50 | bus_LV_198-48_0_7_node_109 | 0.4 | n |  | TRUE
51 | bus_LV_198-48_0_7_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_198-48_0_7_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_198-48_0_7_node_73 | 0.4 | n |  | TRUE
54 | bus_LV_198-48_0_7_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_198-48_0_7_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_198-48_0_7_node_64 | 0.4 | n |  | TRUE
57 | bus_LV_198-48_0_7_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_198-48_0_7_node_129 | 0.4 | n |  | TRUE
59 | bus_LV_198-48_0_7_node_127 | 0.4 | n |  | TRUE
60 | bus_LV_198-48_0_7_node_106 | 0.4 | n |  | TRUE
61 | bus_LV_198-48_0_7_node_107 | 0.4 | n |  | TRUE
62 | bus_LV_198-48_0_7_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_198-48_0_7_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_198-48_0_7_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_198-48_0_7_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_198-48_0_7_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_198-48_0_7_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_198-48_0_7_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_198-48_0_7_node_105 | 0.4 | n |  | TRUE
70 | bus_LV_198-48_0_7_node_79 | 0.4 | n |  | TRUE
71 | bus_LV_198-48_0_7_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_198-48_0_7_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_198-48_0_7_node_86 | 0.4 | n |  | TRUE
74 | bus_LV_198-48_0_7_node_94 | 0.4 | n |  | TRUE
75 | bus_LV_198-48_0_7_node_95 | 0.4 | n |  | TRUE
76 | bus_LV_198-48_0_7_node_113 | 0.4 | n |  | TRUE
77 | bus_LV_198-48_0_7_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_198-48_0_7_node_111 | 0.4 | n |  | TRUE
79 | bus_LV_198-48_0_7_node_59 | 0.4 | n |  | TRUE
80 | bus_LV_198-48_0_7_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_198-48_0_7_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_198-48_0_7_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_198-48_0_7_node_112 | 0.4 | n |  | TRUE
84 | bus_LV_198-48_0_7_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_198-48_0_7_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_198-48_0_7_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_198-48_0_7_node_98 | 0.4 | n |  | TRUE
88 | bus_LV_198-48_0_7_node_99 | 0.4 | n |  | TRUE
89 | bus_LV_198-48_0_7_node_100 | 0.4 | n |  | TRUE
90 | bus_LV_198-48_0_7_node_104 | 0.4 | n |  | TRUE
91 | bus_LV_198-48_0_7_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_198-48_0_7_node_66 | 0.4 | n |  | TRUE
93 | bus_LV_198-48_0_7_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_198-48_0_7_node_150 | 0.4 | n |  | TRUE
95 | bus_LV_198-48_0_7_node_68 | 0.4 | n |  | TRUE
96 | bus_LV_198-48_0_7_node_69 | 0.4 | n |  | TRUE
97 | bus_LV_198-48_0_7_node_71 | 0.4 | n |  | TRUE
98 | bus_LV_198-48_0_7_node_124 | 0.4 | n |  | TRUE
99 | bus_LV_198-48_0_7_node_137 | 0.4 | n |  | TRUE
100 | bus_LV_198-48_0_7_node_119 | 0.4 | n |  | TRUE
101 | bus_LV_198-48_0_7_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_198-48_0_7_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_198-48_0_7_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_198-48_0_7_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_198-48_0_7_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_198-48_0_7_node_77 | 0.4 | n |  | TRUE
107 | bus_LV_198-48_0_7_node_122 | 0.4 | n |  | TRUE
108 | bus_LV_198-48_0_7_node_83 | 0.4 | n |  | TRUE
109 | bus_LV_198-48_0_7_node_85 | 0.4 | n |  | TRUE
110 | bus_LV_198-48_0_7_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_198-48_0_7_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_198-48_0_7_node_120 | 0.4 | n |  | TRUE
113 | bus_LV_198-48_0_7_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_198-48_0_7_node_141 | 0.4 | n |  | TRUE
115 | bus_LV_198-48_0_7_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_198-48_0_7_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_198-48_0_7_node_139 | 0.4 | n |  | TRUE
118 | bus_LV_198-48_0_7_node_96 | 0.4 | n |  | TRUE
119 | bus_LV_198-48_0_7_node_97 | 0.4 | n |  | TRUE
120 | bus_LV_198-48_0_7_node_118 | 0.4 | n |  | TRUE
121 | bus_LV_198-48_0_7_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_198-48_0_7_node_144 | 0.4 | n |  | TRUE
123 | bus_LV_198-48_0_7_node_145 | 0.4 | n |  | TRUE
124 | bus_LV_198-48_0_7_node_110 | 0.4 | n |  | TRUE
125 | bus_LV_198-48_0_7_node_123 | 0.4 | n |  | TRUE
126 | bus_LV_198-48_0_7_node_115 | 0.4 | n |  | TRUE
127 | bus_LV_198-48_0_7_node_136 | 0.4 | n |  | TRUE
128 | bus_LV_198-48_0_7_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_198-48_0_7_node_126 | 0.4 | n |  | TRUE
130 | bus_LV_198-48_0_7_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_198-48_0_7_node_130 | 0.4 | n |  | TRUE
132 | bus_LV_198-48_0_7_node_133 | 0.4 | n |  | TRUE
133 | bus_LV_198-48_0_7_node_131 | 0.4 | n |  | TRUE
134 | bus_LV_198-48_0_7_node_132 | 0.4 | n |  | TRUE
135 | bus_LV_198-48_0_7_node_134 | 0.4 | n |  | TRUE
136 | bus_LV_198-48_0_7_node_140 | 0.4 | n |  | TRUE
137 | bus_LV_198-48_0_7_node_135 | 0.4 | n |  | TRUE
138 | bus_LV_198-48_0_7_node_147 | 0.4 | n |  | TRUE
139 | bus_LV_198-48_0_7_node_146 | 0.4 | n |  | TRUE
140 | bus_LV_198-48_0_7_node_138 | 0.4 | n |  | TRUE
141 | bus_LV_198-48_0_7_node_148 | 0.4 | n |  | TRUE
142 | bus_LV_198-48_0_7_node_152 | 0.4 | n |  | TRUE
143 | bus_MV_362_0_node_182 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_198-48_0_7_load_0 | 0 | 0.0070489 | 0.0017666 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_198-48_0_7_load_7 | 3 | 0.0031746 | 0.00079564 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_198-48_0_7_load_9 | 6 | 0.0086127 | 0.0021585 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_198-48_0_7_load_117 | 8 | 0.0021293 | 0.00053366 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_198-48_0_7_load_26 | 9 | 0.008323 | 0.0020859 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_198-48_0_7_load_20 | 10 | 0.0083888 | 0.0021024 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_198-48_0_7_load_8 | 11 | 0.0083214 | 0.0020855 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_198-48_0_7_load_154 | 13 | 0.0073422 | 0.0018401 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_198-48_0_7_load_142 | 17 | 0.0021059 | 0.00052778 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_198-48_0_7_load_75 | 20 | 0.0018035 | 0.00045199 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_198-48_0_7_load_10 | 21 | 0.0065779 | 0.0016486 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_198-48_0_7_load_116 | 22 | 0.0046352 | 0.0011617 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_198-48_0_7_load_11 | 23 | 0.0058108 | 0.0014563 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_198-48_0_7_load_17 | 25 | 0.0083893 | 0.0021026 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_198-48_0_7_load_149 | 29 | 0.0075622 | 0.0018953 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_198-48_0_7_load_15 | 30 | 0.0081819 | 0.0020506 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_198-48_0_7_load_27 | 31 | 0.0094249 | 0.0023621 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_198-48_0_7_load_82 | 32 | 0.0078935 | 0.0019783 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_198-48_0_7_load_16 | 34 | 0.0083161 | 0.0020842 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_198-48_0_7_load_18 | 35 | 0.0081791 | 0.0020499 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_198-48_0_7_load_21 | 36 | 0.0019826 | 0.00049688 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_198-48_0_7_load_22 | 37 | 0.0024541 | 0.00061506 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_198-48_0_7_load_23 | 38 | 0.001123 | 0.00028145 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_198-48_0_7_load_24 | 39 | 0.0021668 | 0.00054306 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_198-48_0_7_load_25 | 40 | 0.001196 | 0.00029974 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_198-48_0_7_load_41 | 41 | 0.002349 | 0.00058871 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_198-48_0_7_load_42 | 43 | 0.0018541 | 0.00046469 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_198-48_0_7_load_40 | 44 | 0.0010336 | 0.00025905 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_198-48_0_7_load_72 | 45 | 0.0013071 | 0.0003276 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_198-48_0_7_load_31 | 47 | 0.003629 | 0.00090951 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_198-48_0_7_load_34 | 48 | 0.0044175 | 0.0011071 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_198-48_0_7_load_108 | 49 | 0.0049136 | 0.0012315 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_198-48_0_7_load_109 | 50 | 0.0043826 | 0.0010984 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_198-48_0_7_load_39 | 52 | 0.00098917 | 0.00024791 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_198-48_0_7_load_73 | 53 | 0.0012923 | 0.00032387 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_198-48_0_7_load_56 | 54 | 0.001587 | 0.00039774 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_198-48_0_7_load_38 | 55 | 0.0013236 | 0.00033172 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_198-48_0_7_load_37 | 57 | 0.0054551 | 0.0013672 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_198-48_0_7_load_129 | 58 | 0.0051983 | 0.0013028 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_198-48_0_7_load_127 | 59 | 0.0026325 | 0.00065976 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_198-48_0_7_load_106 | 60 | 0.0032672 | 0.00081885 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_198-48_0_7_load_107 | 61 | 0.0024795 | 0.00062143 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_198-48_0_7_load_43 | 62 | 0.0066556 | 0.001668 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_198-48_0_7_load_55 | 65 | 0.0087637 | 0.0021964 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_198-48_0_7_load_46 | 66 | 0.0058772 | 0.001473 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_198-48_0_7_load_105 | 69 | 0.0097057 | 0.0024325 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_198-48_0_7_load_79 | 70 | 0.011381 | 0.0028522 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_198-48_0_7_load_58 | 72 | 0.0087308 | 0.0021881 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_198-48_0_7_load_94 | 74 | 0.0053923 | 0.0013514 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_198-48_0_7_load_113 | 76 | 0.0029469 | 0.00073857 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_198-48_0_7_load_111 | 78 | 0.0069814 | 0.0017497 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_198-48_0_7_load_60 | 80 | 0.0058499 | 0.0014661 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_198-48_0_7_load_57 | 81 | 0.0085573 | 0.0021447 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_198-48_0_7_load_65 | 82 | 0.0049093 | 0.0012304 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_198-48_0_7_load_112 | 83 | 0.018225 | 0.0045677 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_198-48_0_7_load_80 | 84 | 0.0084897 | 0.0021277 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_198-48_0_7_load_87 | 85 | 0.034077 | 0.0085406 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_198-48_0_7_load_100 | 89 | 0.0058478 | 0.0014656 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_198-48_0_7_load_104 | 90 | 0.0026447 | 0.00066282 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_198-48_0_7_load_76 | 91 | 0.0035431 | 0.00088798 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_198-48_0_7_load_66 | 92 | 0.0058475 | 0.0014655 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_198-48_0_7_load_150 | 94 | 0.0094765 | 0.002375 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_198-48_0_7_load_68 | 95 | 0.004862 | 0.0012185 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_198-48_0_7_load_69 | 96 | 0.00082078 | 0.00020571 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_198-48_0_7_load_137 | 99 | 0.00061996 | 0.00015538 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_198-48_0_7_load_74 | 101 | 0.0013195 | 0.00033071 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_198-48_0_7_load_92 | 103 | 0.00090274 | 0.00022625 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_198-48_0_7_load_93 | 104 | 0.00074033 | 0.00018554 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_198-48_0_7_load_88 | 105 | 0.0016362 | 0.00041007 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_198-48_0_7_load_122 | 107 | 0.019598 | 0.0049118 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_198-48_0_7_load_85 | 109 | 0.008456 | 0.0021193 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_198-48_0_7_load_89 | 110 | 0.0010398 | 0.0002606 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_198-48_0_7_load_91 | 111 | 0.0012591 | 0.00031556 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_198-48_0_7_load_120 | 112 | 0.0020955 | 0.00052518 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_198-48_0_7_load_102 | 113 | 0.0083134 | 0.0020835 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_198-48_0_7_load_141 | 114 | 0.0017106 | 0.00042871 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_198-48_0_7_load_121 | 115 | 0.0053815 | 0.0013487 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_198-48_0_7_load_101 | 116 | 0.0061611 | 0.0015441 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_198-48_0_7_load_139 | 117 | 0.0029119 | 0.00072978 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_198-48_0_7_load_96 | 118 | 0.0064051 | 0.0016053 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_198-48_0_7_load_97 | 119 | 0.0040353 | 0.0010113 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_198-48_0_7_load_118 | 120 | 0.0069059 | 0.0017308 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_198-48_0_7_load_144 | 122 | 0.0075589 | 0.0018944 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_198-48_0_7_load_123 | 125 | 0.0021047 | 0.00052748 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_198-48_0_7_load_115 | 126 | 0.0022258 | 0.00055783 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_198-48_0_7_load_136 | 127 | 0.0069605 | 0.0017445 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_198-48_0_7_load_125 | 128 | 0.0030965 | 0.00077607 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_198-48_0_7_load_126 | 129 | 0.0042002 | 0.0010527 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_198-48_0_7_load_128 | 130 | 0.0020829 | 0.00052203 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_198-48_0_7_load_130 | 131 | 0.0019722 | 0.00049427 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_198-48_0_7_load_131 | 133 | 0.0027979 | 0.00070121 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_198-48_0_7_load_134 | 135 | 0.0031474 | 0.00078882 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_198-48_0_7_load_140 | 136 | 0.0026543 | 0.00066523 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_198-48_0_7_load_135 | 137 | 0.0068292 | 0.0017116 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_198-48_0_7_load_147 | 138 | 0.0053576 | 0.0013427 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_198-48_0_7_load_138 | 140 | 0.0073141 | 0.0018331 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_198-48_0_7_load_148 | 141 | 0.0068305 | 0.0017119 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_198-48_0_7_load_152 | 142 | 0.0079384 | 0.0019896 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_198-48_0_7_line_0 |  | 0 | 1 | 0.049887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_198-48_0_7_line_1 |  | 1 | 2 | 0.022665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_198-48_0_7_line_2 |  | 1 | 3 | 0.0033042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_198-48_0_7_line_3 |  | 2 | 7 | 0.007005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_198-48_0_7_line_4 |  | 2 | 8 | 0.016045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_198-48_0_7_line_5 |  | 4 | 5 | 0.02889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_198-48_0_7_line_6 |  | 4 | 6 | 0.018786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_198-48_0_7_line_7 |  | 5 | 9 | 0.014884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_198-48_0_7_line_8 |  | 5 | 10 | 0.0038962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_198-48_0_7_line_9 |  | 6 | 11 | 0.023437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_198-48_0_7_line_10 |  | 7 | 21 | 0.0038059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_198-48_0_7_line_11 |  | 8 | 22 | 0.013506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_198-48_0_7_line_12 |  | 10 | 35 | 0.019588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_198-48_0_7_line_13 |  | 12 | 13 | 0.004186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_198-48_0_7_line_14 |  | 12 | 14 | 0.093614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_198-48_0_7_line_15 |  | 14 | 19 | 0.064464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_198-48_0_7_line_16 |  | 15 | 16 | 0.0289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_198-48_0_7_line_17 |  | 15 | 17 | 0.0103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_198-48_0_7_line_18 |  | 15 | 18 | 0.028994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_198-48_0_7_line_19 |  | 16 | 94 | 0.036809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_198-48_0_7_line_20 |  | 16 | 93 | 0.004542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_198-48_0_7_line_21 |  | 18 | 20 | 0.074141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_198-48_0_7_line_22 |  | 19 | 70 | 0.058479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_198-48_0_7_line_23 |  | 20 | 91 | 0.010767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_198-48_0_7_line_24 |  | 21 | 23 | 0.031728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_198-48_0_7_line_25 |  | 22 | 126 | 0.0023187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_198-48_0_7_line_26 |  | 23 | 24 | 0.0050843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_198-48_0_7_line_27 |  | 24 | 25 | 0.052407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_198-48_0_7_line_28 |  | 24 | 26 | 0.011135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_198-48_0_7_line_29 |  | 25 | 30 | 0.0090014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_198-48_0_7_line_30 |  | 26 | 28 | 0.026376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_198-48_0_7_line_31 |  | 26 | 31 | 0.018018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_198-48_0_7_line_32 |  | 27 | 28 | 0.031585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_198-48_0_7_line_33 |  | 27 | 29 | 0.017124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_198-48_0_7_line_34 |  | 28 | 32 | 0.0038642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_198-48_0_7_line_35 |  | 29 | 33 | 0.027042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_198-48_0_7_line_36 |  | 30 | 34 | 0.0071539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_198-48_0_7_line_37 |  | 31 | 46 | 0.023437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_198-48_0_7_line_38 |  | 33 | 108 | 0.021266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_198-48_0_7_line_39 |  | 34 | 35 | 0.010817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_198-48_0_7_line_40 |  | 36 | 37 | 0.0030054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_198-48_0_7_line_41 |  | 36 | 38 | 0.020611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_198-48_0_7_line_42 |  | 37 | 39 | 0.011906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_198-48_0_7_line_43 |  | 38 | 40 | 0.0031277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_198-48_0_7_line_44 |  | 39 | 41 | 0.016736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_198-48_0_7_line_45 |  | 40 | 42 | 0.034893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_198-48_0_7_line_46 |  | 41 | 43 | 0.0032341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_198-48_0_7_line_47 |  | 42 | 44 | 0.014347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_198-48_0_7_line_48 |  | 42 | 45 | 0.0035221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_198-48_0_7_line_49 |  | 43 | 60 | 0.019683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_198-48_0_7_line_50 |  | 44 | 52 | 0.0057217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_198-48_0_7_line_51 |  | 45 | 53 | 0.014454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_198-48_0_7_line_52 |  | 46 | 47 | 0.018869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_198-48_0_7_line_53 |  | 47 | 48 | 0.00052402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_198-48_0_7_line_54 |  | 48 | 51 | 0.016226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_198-48_0_7_line_55 |  | 49 | 50 | 0.041388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_198-48_0_7_line_56 |  | 50 | 93 | 0.016243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_198-48_0_7_line_57 |  | 51 | 54 | 0.0084252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_198-48_0_7_line_58 |  | 51 | 55 | 0.023599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_198-48_0_7_line_59 |  | 52 | 57 | 0.019293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_198-48_0_7_line_60 |  | 53 | 101 | 0.0053413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_198-48_0_7_line_61 |  | 54 | 56 | 0.044701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_198-48_0_7_line_62 |  | 55 | 57 | 0.0029746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_198-48_0_7_line_63 |  | 56 | 82 | 0.031968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_198-48_0_7_line_64 |  | 56 | 77 | 0.018135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_198-48_0_7_line_65 |  | 58 | 59 | 0.0014028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_198-48_0_7_line_66 |  | 59 | 128 | 0.028089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_198-48_0_7_line_67 |  | 60 | 61 | 0.0020079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_198-48_0_7_line_68 |  | 61 | 124 | 0.018667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_198-48_0_7_line_69 |  | 62 | 63 | 0.046501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_198-48_0_7_line_70 |  | 63 | 64 | 0.032248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_198-48_0_7_line_71 |  | 63 | 65 | 0.021874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_198-48_0_7_line_72 |  | 64 | 71 | 0.02004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_198-48_0_7_line_73 |  | 64 | 72 | 0.020698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_198-48_0_7_line_74 |  | 65 | 73 | 0.018203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_198-48_0_7_line_75 |  | 66 | 67 | 0.01905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_198-48_0_7_line_76 |  | 67 | 68 | 0.010242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_198-48_0_7_line_77 |  | 68 | 69 | 0.037213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_198-48_0_7_line_78 |  | 69 | 73 | 0.046705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_198-48_0_7_line_79 |  | 70 | 84 | 0.01703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_198-48_0_7_line_80 |  | 71 | 76 | 0.02346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_198-48_0_7_line_81 |  | 72 | 81 | 0.022783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_198-48_0_7_line_82 |  | 73 | 86 | 0.031169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_198-48_0_7_line_83 |  | 74 | 75 | 0.010483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_198-48_0_7_line_84 |  | 75 | 118 | 0.029709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_198-48_0_7_line_85 |  | 75 | 119 | 0.029479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_198-48_0_7_line_86 |  | 76 | 83 | 0.036386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_198-48_0_7_line_87 |  | 77 | 78 | 0.020451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_198-48_0_7_line_88 |  | 78 | 90 | 0.038992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_198-48_0_7_line_89 |  | 79 | 80 | 0.018627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_198-48_0_7_line_90 |  | 79 | 81 | 0.02878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_198-48_0_7_line_91 |  | 80 | 87 | 0.0026818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_198-48_0_7_line_92 |  | 82 | 92 | 0.026964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_198-48_0_7_line_93 |  | 84 | 86 | 0.02063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_198-48_0_7_line_94 |  | 85 | 86 | 0.010807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_198-48_0_7_line_95 |  | 87 | 88 | 0.025029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_198-48_0_7_line_96 |  | 87 | 89 | 0.019237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_198-48_0_7_line_97 |  | 88 | 121 | 0.01393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_198-48_0_7_line_98 |  | 88 | 122 | 0.048717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_198-48_0_7_line_99 |  | 89 | 100 | 0.025291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_198-48_0_7_line_100 |  | 91 | 106 | 0.033276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_198-48_0_7_line_101 |  | 92 | 93 | 0.042124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_198-48_0_7_line_102 |  | 95 | 96 | 0.018879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_198-48_0_7_line_103 |  | 96 | 97 | 0.023878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_198-48_0_7_line_104 |  | 97 | 98 | 0.019067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_198-48_0_7_line_105 |  | 98 | 99 | 0.020149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_198-48_0_7_line_106 |  | 98 | 100 | 0.021635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_198-48_0_7_line_107 |  | 99 | 127 | 0.010558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_198-48_0_7_line_108 |  | 100 | 120 | 0.025671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_198-48_0_7_line_109 |  | 101 | 102 | 0.031466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_198-48_0_7_line_110 |  | 102 | 103 | 0.011542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_198-48_0_7_line_111 |  | 102 | 104 | 0.0093052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_198-48_0_7_line_112 |  | 102 | 105 | 0.016425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_198-48_0_7_line_113 |  | 103 | 113 | 0.027136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_198-48_0_7_line_114 |  | 104 | 114 | 0.0084818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_198-48_0_7_line_115 |  | 105 | 110 | 0.013899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_198-48_0_7_line_116 |  | 106 | 107 | 0.022669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_198-48_0_7_line_117 |  | 108 | 109 | 0.0050555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_198-48_0_7_line_118 |  | 110 | 111 | 0.0041159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_198-48_0_7_line_119 |  | 111 | 112 | 0.0014624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_198-48_0_7_line_120 |  | 112 | 115 | 0.036549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_198-48_0_7_line_121 |  | 113 | 116 | 0.0050542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_198-48_0_7_line_122 |  | 114 | 117 | 0.014895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_198-48_0_7_line_123 |  | 116 | 121 | 0.014286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_198-48_0_7_line_124 |  | 117 | 136 | 0.023842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_198-48_0_7_line_125 |  | 118 | 120 | 0.020274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_198-48_0_7_line_126 |  | 122 | 123 | 0.043095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_198-48_0_7_line_127 |  | 123 | 139 | 0.01341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_198-48_0_7_line_128 |  | 124 | 125 | 0.024116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_198-48_0_7_line_129 |  | 127 | 140 | 0.004225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_198-48_0_7_line_130 |  | 128 | 129 | 0.0025457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_198-48_0_7_line_131 |  | 129 | 130 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_198-48_0_7_line_132 |  | 130 | 131 | 0.0083399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_198-48_0_7_line_133 |  | 131 | 132 | 0.0067543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_198-48_0_7_line_134 |  | 132 | 133 | 0.018902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_198-48_0_7_line_135 |  | 133 | 134 | 0.017312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_198-48_0_7_line_136 |  | 134 | 135 | 0.028565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_198-48_0_7_line_137 |  | 135 | 136 | 0.020516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_198-48_0_7_line_138 |  | 137 | 138 | 0.0036191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_198-48_0_7_line_139 |  | 138 | 139 | 0.020633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_198-48_0_7_line_140 |  | 139 | 141 | 0.048105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_198-48_0_7_line_141 |  | 141 | 142 | 0.019399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_198-48_0_7_trafo_33 | 0.63 MVA 20/0.4 kV | 143 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2696317.2942 | 1246156.5176 | 2696347.2623 | 1246134.0761 | 2696349.8565 | 1246127.4131 | 2696354.4935 | 1246124.8514
1 | 2696317.2942 | 1246156.5176 | 2696312.4349 | 1246139.8371 | 2696310.9535 | 1246134.7536
2 | 2696317.2942 | 1246156.5176 | 2696318.6739 | 1246159.52
3 | 2696308.9925 | 1246128.0277 | 2696310.9535 | 1246134.7536
4 | 2696310.9535 | 1246134.7536 | 2696296.3496 | 1246141.3991
5 | 2696393.6315 | 1246066.7445 | 2696378.9627 | 1246041.8315
6 | 2696393.6315 | 1246066.7445 | 2696410.6025 | 1246058.6888
7 | 2696378.9627 | 1246041.8315 | 2696388.4697 | 1246036.6154 | 2696392.0112 | 1246034.6717
8 | 2696378.9627 | 1246041.8315 | 2696375.5457 | 1246043.7035
9 | 2696431.1771 | 1246055.9653 | 2696430.3384 | 1246054.6319 | 2696427.5095 | 1246052.4954 | 2696423.7779 | 1246052.4347 | 2696410.6025 | 1246058.6888
10 | 2696308.9925 | 1246128.0277 | 2696307.9261 | 1246124.3743 | 2696307.9261 | 1246124.3743
11 | 2696296.3496 | 1246141.3991 | 2696284.0566 | 1246146.993
12 | 2696358.367 | 1246053.1158 | 2696366.6427 | 1246048.581 | 2696375.5457 | 1246043.7035
13 | 2696040.8268 | 1246074.6721 | 2696043.888 | 1246071.8084
14 | 2696044.5753 | 1246038.7164 | 2696043.6787 | 1246039.4914 | 2696046.5172 | 1246046.6428 | 2696043.4069 | 1246049.2722 | 2696012.6256 | 1246075.316 | 2696015.6767 | 1246079.135 | 2696021.6905 | 1246086.6381 | 2696023.8159 | 1246089.2968 | 2696040.8268 | 1246074.6721
15 | 2696002.8774 | 1245989.5593 | 2696030.5837 | 1246022.7443 | 2696033.2619 | 1246025.8011 | 2696036.4889 | 1246029.4895 | 2696044.5753 | 1246038.7164
16 | 2696162.0928 | 1246088.0137 | 2696156.4422 | 1246116.3549
17 | 2696156.4422 | 1246116.3549 | 2696166.5645 | 1246118.2585
18 | 2696156.2728 | 1246092.3338 | 2696151.0726 | 1246115.267 | 2696156.4422 | 1246116.3549
19 | 2696162.0928 | 1246088.0137 | 2696186.4359 | 1246093.2457 | 2696184.2044 | 1246104.1067 | 2696183.323 | 1246103.9479
20 | 2696162.0928 | 1246088.0137 | 2696163.0339 | 1246083.57
21 | 2696156.2728 | 1246092.3338 | 2696135.4689 | 1246087.3816 | 2696126.6071 | 1246083.1125 | 2696119.0082 | 1246077.385 | 2696107.2267 | 1246060.2699 | 2696103.6624 | 1246048.9591 | 2696104.167 | 1246048.3824
22 | 2696002.8774 | 1245989.5593 | 2696047.6621 | 1245951.954
23 | 2696104.167 | 1246048.3824 | 2696111.2571 | 1246040.28
24 | 2696307.9261 | 1246124.3743 | 2696294.9175 | 1246099.1104 | 2696292.8222 | 1246096.5455
25 | 2696281.9461 | 1246147.9534 | 2696284.0566 | 1246146.993
26 | 2696289.6056 | 1246092.608 | 2696292.8222 | 1246096.5455
27 | 2696289.6056 | 1246092.608 | 2696299.996 | 1246085.0932 | 2696334.7125 | 1246066.0768
28 | 2696289.6056 | 1246092.608 | 2696282.7441 | 1246083.8233
29 | 2696334.7125 | 1246066.0768 | 2696338.9531 | 1246063.7539 | 2696342.6068 | 1246061.7518
30 | 2696282.7441 | 1246083.8233 | 2696273.1184 | 1246090.7724 | 2696261.6839 | 1246099.7714
31 | 2696282.7441 | 1246083.8233 | 2696270.4294 | 1246070.6705
32 | 2696261.6839 | 1246099.7714 | 2696259.5175 | 1246101.5043 | 2696257.1651 | 1246105.8472 | 2696260.565 | 1246112.374 | 2696270.3216 | 1246125.7315
33 | 2696270.3216 | 1246125.7315 | 2696256.8242 | 1246136.2689
34 | 2696261.6839 | 1246099.7714 | 2696258.2163 | 1246101.4767
35 | 2696235.5092 | 1246152.9096 | 2696256.8242 | 1246136.2689
36 | 2696348.8805 | 1246058.314 | 2696342.6068 | 1246061.7518
37 | 2696254.4101 | 1246053.5625 | 2696255.9549 | 1246055.211 | 2696270.4294 | 1246070.6705
38 | 2696225.6267 | 1246134.7354 | 2696233.5436 | 1246144.1377 | 2696235.5092 | 1246152.9096
39 | 2696348.8805 | 1246058.314 | 2696358.367 | 1246053.1158
40 | 2696307.6052 | 1245976.2729 | 2696308.457 | 1245976.3807 | 2696310.5913 | 1245976.1498
41 | 2696307.6052 | 1245976.2729 | 2696292.2299 | 1245974.3268 | 2696287.2438 | 1245973.1929
42 | 2696322.4087 | 1245974.7621 | 2696321.6805 | 1245974.9499 | 2696310.5913 | 1245976.1498
43 | 2696284.194 | 1245972.4994 | 2696287.2438 | 1245973.1929
44 | 2696322.4087 | 1245974.7621 | 2696335.0273 | 1245971.5084 | 2696338.208 | 1245969.6092
45 | 2696250.0475 | 1245965.3353 | 2696270.7973 | 1245969.4529 | 2696284.194 | 1245972.4994
46 | 2696340.9847 | 1245967.9511 | 2696338.208 | 1245969.6092
47 | 2696250.0475 | 1245965.3353 | 2696247.4342 | 1245979.4425
48 | 2696250.0475 | 1245965.3353 | 2696250.5297 | 1245961.8464
49 | 2696340.9847 | 1245967.9511 | 2696345.2516 | 1245965.4032 | 2696352.8023 | 1245958.7541 | 2696356.1525 | 1245955.5261
50 | 2696246.3921 | 1245985.0685 | 2696247.4342 | 1245979.4425
51 | 2696250.5297 | 1245961.8464 | 2696251.1776 | 1245957.1585 | 2696254.6047 | 1245948.0612
52 | 2696254.4101 | 1246053.5625 | 2696241.8381 | 1246039.4921
53 | 2696241.8381 | 1246039.4921 | 2696241.4889 | 1246039.1013
54 | 2696230.6777 | 1246027.0015 | 2696241.4889 | 1246039.1013
55 | 2696216.2022 | 1246084.1549 | 2696209.9174 | 1246090.569 | 2696178.1845 | 1246083.9867
56 | 2696163.0339 | 1246083.57 | 2696166.7296 | 1246083.9747 | 2696168.5676 | 1246081.9918 | 2696178.1845 | 1246083.9867
57 | 2696230.6777 | 1246027.0015 | 2696224.6941 | 1246021.0702
58 | 2696230.6777 | 1246027.0015 | 2696237.1857 | 1246018.9454 | 2696242.6752 | 1246006.8945
59 | 2696243.9083 | 1246004.1876 | 2696243.9083 | 1246004.1876 | 2696245.2605 | 1245991.1774 | 2696246.3921 | 1245985.0685
60 | 2696254.6047 | 1245948.0612 | 2696256.4876 | 1245943.0628
61 | 2696192.9538 | 1245989.5943 | 2696207.2758 | 1246003.8042 | 2696224.6941 | 1246021.0702
62 | 2696243.9083 | 1246004.1876 | 2696242.6752 | 1246006.8945
63 | 2696192.9538 | 1245989.5943 | 2696191.1639 | 1245998.8502 | 2696185.4294 | 1246001.6149 | 2696179.3994 | 1246013.7486 | 2696178.8003 | 1246016.3045
64 | 2696191.6465 | 1245972.3711 | 2696195.0105 | 1245980.1872 | 2696192.9538 | 1245989.5943
65 | 2696441.0895 | 1245801.3385 | 2696439.9259 | 1245802.1222
66 | 2696416.1575 | 1245817.0229 | 2696423.522 | 1245813.1696 | 2696439.9259 | 1245802.1222
67 | 2696356.1525 | 1245955.5261 | 2696357.5985 | 1245954.133
68 | 2696371.041 | 1245941.1813 | 2696357.5985 | 1245954.133
69 | 2696125.2001 | 1245908.5006 | 2696095.9102 | 1245872.3835
70 | 2696125.2001 | 1245908.5006 | 2696144.4252 | 1245934.432
71 | 2696125.2001 | 1245908.5006 | 2696107.4733 | 1245921.3163
72 | 2696158.5279 | 1245948.2045 | 2696153.8422 | 1245945.4709 | 2696150.0551 | 1245942.3071 | 2696144.4252 | 1245934.432
73 | 2696144.4252 | 1245934.432 | 2696160.0604 | 1245920.8692
74 | 2696092.7214 | 1245931.9812 | 2696107.4733 | 1245921.3163
75 | 2696033.7728 | 1245858.5593 | 2696048.9073 | 1245846.9902
76 | 2696033.7728 | 1245858.5593 | 2696035.7825 | 1245860.9048 | 2696040.2483 | 1245866.4925
77 | 2696040.2483 | 1245866.4925 | 2696063.5174 | 1245895.5333
78 | 2696092.7214 | 1245931.9812 | 2696063.5174 | 1245895.5333
79 | 2696047.6621 | 1245951.954 | 2696060.704 | 1245941.0029
80 | 2696158.5279 | 1245948.2045 | 2696139.335 | 1245961.6949
81 | 2696177.2705 | 1245905.9404 | 2696177.104 | 1245906.0846 | 2696160.0604 | 1245920.8692
82 | 2696092.7214 | 1245931.9812 | 2696074.959 | 1245946.3267 | 2696076.2012 | 1245948.9377 | 2696076.1787 | 1245950.3273 | 2696076.1313 | 1245953.251 | 2696075.339 | 1245954.1166
83 | 2696143.3748 | 1245808.6633 | 2696134.2551 | 1245803.4933
84 | 2696143.3748 | 1245808.6633 | 2696144.4497 | 1245812.7394 | 2696151.1503 | 1245815.1721 | 2696162.8331 | 1245813.2489 | 2696169.1923 | 1245814.7115
85 | 2696143.3748 | 1245808.6633 | 2696165.4711 | 1245789.1495
86 | 2696110.4255 | 1245983.7516 | 2696125.7925 | 1245971.2137 | 2696139.335 | 1245961.6949
87 | 2696191.6465 | 1245972.3711 | 2696195.303 | 1245952.2496
88 | 2696195.303 | 1245952.2496 | 2696199.6449 | 1245928.356 | 2696201.4486 | 1245913.7597
89 | 2696199.0299 | 1245887.1034 | 2696202.9977 | 1245868.9036
90 | 2696199.0299 | 1245887.1034 | 2696177.2705 | 1245905.9404
91 | 2696203.569 | 1245866.2833 | 2696202.9977 | 1245868.9036
92 | 2696178.8003 | 1246016.3045 | 2696172.6469 | 1246042.5572
93 | 2696075.339 | 1245954.1166 | 2696074.6852 | 1245954.8288 | 2696060.704 | 1245941.0029 | 2696060.704 | 1245941.0029
94 | 2696075.339 | 1245954.1166 | 2696078.3405 | 1245957.7346 | 2696082.2349 | 1245962.4376
95 | 2696203.569 | 1245866.2833 | 2696210.504 | 1245867.3077 | 2696216.9841 | 1245867.4907 | 2696223.1312 | 1245866.7788 | 2696228.3747 | 1245865.4072
96 | 2696203.569 | 1245866.2833 | 2696207.6974 | 1245847.4948
97 | 2696228.3747 | 1245865.4072 | 2696227.9786 | 1245873.0511 | 2696227.4024 | 1245875.9662 | 2696225.754 | 1245878.8305
98 | 2696228.3747 | 1245865.4072 | 2696232.9977 | 1245862.7024 | 2696239.1148 | 1245858.2538 | 2696254.6906 | 1245844.129 | 2696259.9514 | 1245839.3663 | 2696265.2271 | 1245834.1591 | 2696265.4143 | 1245833.9757
99 | 2696213.1834 | 1245822.806 | 2696208.0074 | 1245846.0843 | 2696207.6974 | 1245847.4948
100 | 2696132.5145 | 1246014.7115 | 2696126.6502 | 1246022.6892 | 2696111.2571 | 1246040.28
101 | 2696163.0339 | 1246083.57 | 2696172.6469 | 1246042.5572
102 | 2696180.0154 | 1245774.4902 | 2696198.5118 | 1245778.2699
103 | 2696221.9063 | 1245783.0504 | 2696198.5118 | 1245778.2699
104 | 2696217.8861 | 1245801.6884 | 2696221.9063 | 1245783.0504
105 | 2696217.8861 | 1245801.6884 | 2696237.4347 | 1245806.5696
106 | 2696217.8861 | 1245801.6884 | 2696213.1834 | 1245822.806
107 | 2696245.1366 | 1245813.3948 | 2696239.3191 | 1245807.0401 | 2696237.4347 | 1245806.5696
108 | 2696213.1834 | 1245822.806 | 2696188.0651 | 1245817.5059
109 | 2696269.7989 | 1245914.617 | 2696264.6719 | 1245923.7074 | 2696260.0374 | 1245933.6398 | 2696256.4876 | 1245943.0628
110 | 2696269.7989 | 1245914.617 | 2696259.8504 | 1245908.7643
111 | 2696269.7989 | 1245914.617 | 2696275.6082 | 1245907.348
112 | 2696269.7989 | 1245914.617 | 2696283.3809 | 1245923.8533
113 | 2696259.8504 | 1245908.7643 | 2696255.0843 | 1245905.9605 | 2696251.1023 | 1245900.3805 | 2696240.609 | 1245890.0134
114 | 2696275.6082 | 1245907.348 | 2696280.9034 | 1245900.7222
115 | 2696283.3809 | 1245923.8533 | 2696288.946 | 1245927.6378 | 2696296.0821 | 1245928.3212
116 | 2696132.5145 | 1246014.7115 | 2696137.4042 | 1246006.2621 | 2696143.0781 | 1245994.6563
117 | 2696225.6267 | 1246134.7354 | 2696221.447 | 1246137.5795
118 | 2696300.1792 | 1245928.7136 | 2696296.0821 | 1245928.3212
119 | 2696300.1792 | 1245928.7136 | 2696301.635 | 1245928.853
120 | 2696331.5238 | 1245911.8503 | 2696312.5434 | 1245929.033 | 2696307.2635 | 1245929.392 | 2696301.635 | 1245928.853
121 | 2696235.6284 | 1245889.1542 | 2696240.609 | 1245890.0134 | 2696240.609 | 1245890.0134
122 | 2696291.9716 | 1245890.8066 | 2696282.2474 | 1245899.0405 | 2696280.9034 | 1245900.7222
123 | 2696225.754 | 1245878.8305 | 2696235.6284 | 1245889.1542
124 | 2696291.9716 | 1245890.8066 | 2696310.1668 | 1245875.4
125 | 2696169.1923 | 1245814.7115 | 2696180.0498 | 1245817.2088 | 2696180.4715 | 1245815.9036 | 2696188.0651 | 1245817.5059
126 | 2696296.2089 | 1245803.8276 | 2696274.1415 | 1245825.4304 | 2696265.4143 | 1245833.9757
127 | 2696306.5119 | 1245795.2105 | 2696296.2089 | 1245803.8276
128 | 2696371.041 | 1245941.1813 | 2696388.1537 | 1245958.1738
129 | 2696245.1366 | 1245813.3948 | 2696247.9895 | 1245816.5111
130 | 2696416.1575 | 1245817.0229 | 2696413.9019 | 1245818.2031
131 | 2696413.9019 | 1245818.2031 | 2696397.7068 | 1245826.6768
132 | 2696390.3173 | 1245830.5432 | 2696397.7068 | 1245826.6768
133 | 2696384.5257 | 1245834.0184 | 2696390.3173 | 1245830.5432 | 2696390.3173 | 1245830.5432
134 | 2696384.5257 | 1245834.0184 | 2696383.5146 | 1245834.8582 | 2696368.3807 | 1245843.8192
135 | 2696353.4846 | 1245852.6395 | 2696368.3807 | 1245843.8192
136 | 2696353.4846 | 1245852.6395 | 2696353.1219 | 1245853.1006 | 2696328.0873 | 1245865.5935
137 | 2696310.1668 | 1245875.4 | 2696312.9009 | 1245873.0849 | 2696320.6012 | 1245869.3293 | 2696328.0873 | 1245865.5935
138 | 2696321.0785 | 1245809.8239 | 2696323.6335 | 1245812.3871
139 | 2696306.5119 | 1245795.2105 | 2696321.0785 | 1245809.8239
140 | 2696306.5119 | 1245795.2105 | 2696313.5845 | 1245788.6982 | 2696331.6913 | 1245771.3678 | 2696341.3929 | 1245762.0857
141 | 2696341.3929 | 1245762.0857 | 2696358.5861 | 1245753.1018

## bus_geodata
| x | y | coords
0 | 2696354.4935 | 1246124.8514
1 | 2696317.2942 | 1246156.5176
2 | 2696310.9535 | 1246134.7536
3 | 2696318.6739 | 1246159.52
4 | 2696393.6315 | 1246066.7445
5 | 2696378.9627 | 1246041.8315
6 | 2696410.6025 | 1246058.6888
7 | 2696308.9925 | 1246128.0277
8 | 2696296.3496 | 1246141.3991
9 | 2696392.0112 | 1246034.6717
10 | 2696375.5457 | 1246043.7035
11 | 2696431.1771 | 1246055.9653
12 | 2696040.8268 | 1246074.6721
13 | 2696043.888 | 1246071.8084
14 | 2696044.5753 | 1246038.7164
15 | 2696156.4422 | 1246116.3549
16 | 2696162.0928 | 1246088.0137
17 | 2696166.5645 | 1246118.2585
18 | 2696156.2728 | 1246092.3338
19 | 2696002.8774 | 1245989.5593
20 | 2696104.167 | 1246048.3824
21 | 2696307.9261 | 1246124.3743
22 | 2696284.0566 | 1246146.993
23 | 2696292.8222 | 1246096.5455
24 | 2696289.6056 | 1246092.6081
25 | 2696334.7125 | 1246066.0768
26 | 2696282.7441 | 1246083.8233
27 | 2696270.3216 | 1246125.7315
28 | 2696261.6839 | 1246099.7714
29 | 2696256.8242 | 1246136.2689
30 | 2696342.6068 | 1246061.7518
31 | 2696270.4294 | 1246070.6705
32 | 2696258.2163 | 1246101.4767
33 | 2696235.5092 | 1246152.9096
34 | 2696348.8805 | 1246058.314
35 | 2696358.367 | 1246053.1158
36 | 2696307.6052 | 1245976.2729
37 | 2696310.5913 | 1245976.1498
38 | 2696287.2438 | 1245973.1929
39 | 2696322.4087 | 1245974.7621
40 | 2696284.194 | 1245972.4994
41 | 2696338.208 | 1245969.6092
42 | 2696250.0475 | 1245965.3353
43 | 2696340.9847 | 1245967.9511
44 | 2696247.4342 | 1245979.4425
45 | 2696250.5297 | 1245961.8464
46 | 2696254.4101 | 1246053.5625
47 | 2696241.8381 | 1246039.4921
48 | 2696241.4889 | 1246039.1013
49 | 2696216.2022 | 1246084.1549
50 | 2696178.1845 | 1246083.9867
51 | 2696230.6777 | 1246027.0015
52 | 2696246.3921 | 1245985.0685
53 | 2696254.6047 | 1245948.0612
54 | 2696224.6941 | 1246021.0702
55 | 2696242.6752 | 1246006.8945
56 | 2696192.9538 | 1245989.5943
57 | 2696243.9083 | 1246004.1876
58 | 2696441.0895 | 1245801.3385
59 | 2696439.9259 | 1245802.1222
60 | 2696356.1525 | 1245955.5261
61 | 2696357.5985 | 1245954.133
62 | 2696095.9102 | 1245872.3835
63 | 2696125.2001 | 1245908.5006
64 | 2696144.4252 | 1245934.432
65 | 2696107.4733 | 1245921.3163
66 | 2696048.9073 | 1245846.9902
67 | 2696033.7728 | 1245858.5593
68 | 2696040.2483 | 1245866.4925
69 | 2696063.5174 | 1245895.5333
70 | 2696047.6621 | 1245951.954
71 | 2696158.5279 | 1245948.2045
72 | 2696160.0604 | 1245920.8692
73 | 2696092.7214 | 1245931.9812
74 | 2696134.2551 | 1245803.4933
75 | 2696143.3748 | 1245808.6633
76 | 2696139.335 | 1245961.6949
77 | 2696191.6465 | 1245972.3711
78 | 2696195.303 | 1245952.2496
79 | 2696199.0299 | 1245887.1034
80 | 2696202.9977 | 1245868.9036
81 | 2696177.2705 | 1245905.9404
82 | 2696178.8003 | 1246016.3045
83 | 2696110.4255 | 1245983.7516
84 | 2696060.704 | 1245941.0029
85 | 2696082.2349 | 1245962.4376
86 | 2696075.339 | 1245954.1166
87 | 2696203.569 | 1245866.2833
88 | 2696228.3747 | 1245865.4072
89 | 2696207.6974 | 1245847.4948
90 | 2696201.4486 | 1245913.7597
91 | 2696111.2571 | 1246040.28
92 | 2696172.6469 | 1246042.5572
93 | 2696163.0339 | 1246083.57
94 | 2696183.323 | 1246103.9479
95 | 2696180.0154 | 1245774.4902
96 | 2696198.5118 | 1245778.2699
97 | 2696221.9063 | 1245783.0504
98 | 2696217.8861 | 1245801.6884
99 | 2696237.4347 | 1245806.5696
100 | 2696213.1834 | 1245822.806
101 | 2696256.4876 | 1245943.0628
102 | 2696269.7989 | 1245914.617
103 | 2696259.8504 | 1245908.7643
104 | 2696275.6082 | 1245907.348
105 | 2696283.3809 | 1245923.8533
106 | 2696132.5145 | 1246014.7115
107 | 2696143.0781 | 1245994.6563
108 | 2696225.6267 | 1246134.7354
109 | 2696221.447 | 1246137.5795
110 | 2696296.0821 | 1245928.3212
111 | 2696300.1792 | 1245928.7136
112 | 2696301.635 | 1245928.853
113 | 2696240.609 | 1245890.0134
114 | 2696280.9034 | 1245900.7222
115 | 2696331.5238 | 1245911.8503
116 | 2696235.6284 | 1245889.1542
117 | 2696291.9716 | 1245890.8066
118 | 2696169.1923 | 1245814.7115
119 | 2696165.4711 | 1245789.1495
120 | 2696188.0651 | 1245817.5059
121 | 2696225.754 | 1245878.8305
122 | 2696265.4143 | 1245833.9757
123 | 2696296.2088 | 1245803.8276
124 | 2696371.041 | 1245941.1813
125 | 2696388.1537 | 1245958.1738
126 | 2696281.9461 | 1246147.9534
127 | 2696245.1366 | 1245813.3948
128 | 2696416.1575 | 1245817.0229
129 | 2696413.9019 | 1245818.2031
130 | 2696397.7068 | 1245826.6768
131 | 2696390.3173 | 1245830.5432
132 | 2696384.5257 | 1245834.0184
133 | 2696368.3807 | 1245843.8192
134 | 2696353.4846 | 1245852.6395
135 | 2696328.0873 | 1245865.5935
136 | 2696310.1668 | 1245875.4
137 | 2696323.6335 | 1245812.3871
138 | 2696321.0785 | 1245809.8239
139 | 2696306.5119 | 1245795.2105
140 | 2696247.9895 | 1245816.5111
141 | 2696341.3929 | 1245762.0857
142 | 2696358.5861 | 1245753.1018
143 | 2696269.7989 | 1245914.617

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98403 | -0.30681 | 0.0070489 | 0.0017666
1 | 0.98435 | -0.30048 | 0 | 0
2 | 0.98456 | -0.29631 | 0 | 0
3 | 0.98434 | -0.30067 | 0.0031746 | 0.00079564
4 | 0.98003 | -0.38469 | 0 | 0
5 | 0.98049 | -0.37582 | 0 | 0
6 | 0.97974 | -0.39047 | 0.0086127 | 0.0021585
7 | 0.98469 | -0.29389 | 0 | 0
8 | 0.98443 | -0.29891 | 0.0021293 | 0.00053366
9 | 0.98037 | -0.37806 | 0.008323 | 0.0020859
10 | 0.98058 | -0.37403 | 0.0083888 | 0.0021024
11 | 0.97956 | -0.39401 | 0.0083214 | 0.0020855
12 | 0.97027 | -0.57472 | 0 | 0
13 | 0.97024 | -0.57529 | 0.0073422 | 0.0018401
14 | 0.97091 | -0.562 | 0 | 0
15 | 0.9861 | -0.26676 | 0 | 0
16 | 0.98682 | -0.25275 | 0 | 0
17 | 0.98608 | -0.26714 | 0.0021059 | 0.00052778
18 | 0.98544 | -0.27973 | 0 | 0
19 | 0.97135 | -0.55325 | 0 | 0
20 | 0.98373 | -0.31299 | 0.0018035 | 0.00045199
21 | 0.98475 | -0.29258 | 0.0065779 | 0.0016486
22 | 0.98434 | -0.30057 | 0.0046352 | 0.0011617
23 | 0.98551 | -0.27788 | 0.0058108 | 0.0014563
24 | 0.98566 | -0.275 | 0 | 0
25 | 0.98242 | -0.33793 | 0.0083893 | 0.0021026
26 | 0.98667 | -0.25537 | 0 | 0
27 | 0.98562 | -0.27575 | 0 | 0
28 | 0.98609 | -0.26667 | 0 | 0
29 | 0.98537 | -0.28067 | 0.0075622 | 0.0018953
30 | 0.98194 | -0.34742 | 0.0081819 | 0.0020506
31 | 0.9887 | -0.21602 | 0.0094249 | 0.0023621
32 | 0.98606 | -0.26722 | 0.0078935 | 0.0019783
33 | 0.98516 | -0.28478 | 0 | 0
34 | 0.98161 | -0.3539 | 0.0083161 | 0.0020842
35 | 0.98119 | -0.36209 | 0.0081791 | 0.0020499
36 | 0.99893 | -0.020565 | 0.0019826 | 0.00049688
37 | 0.99888 | -0.021441 | 0.0024541 | 0.00061506
38 | 0.99928 | -0.013849 | 0.001123 | 0.00028145
39 | 0.99873 | -0.024399 | 0.0021668 | 0.00054306
40 | 0.99934 | -0.012769 | 0.001196 | 0.00029974
41 | 0.99855 | -0.027926 | 0.002349 | 0.00058871
42 | 1 | 0 | -0.53063 | -0.13548
43 | 0.99852 | -0.028475 | 0.0018541 | 0.00046469
44 | 0.99905 | -0.01805 | 0.0010336 | 0.00025905
45 | 0.99969 | -0.0058172 | 0.0013071 | 0.0003276
46 | 0.99155 | -0.16116 | 0 | 0
47 | 0.99384 | -0.11721 | 0.003629 | 0.00090951
48 | 0.9939 | -0.11596 | 0.0044175 | 0.0011071
49 | 0.98665 | -0.25612 | 0.0049136 | 0.0012315
50 | 0.98684 | -0.25248 | 0.0043826 | 0.0010984
51 | 0.99495 | -0.095985 | 0 | 0
52 | 0.99867 | -0.025223 | 0.00098917 | 0.00024791
53 | 0.99843 | -0.029617 | 0.0012923 | 0.00032387
54 | 0.99443 | -0.10605 | 0.001587 | 0.00039774
55 | 0.99721 | -0.052968 | 0.0013236 | 0.00033172
56 | 0.9917 | -0.15837 | 0 | 0
57 | 0.9974 | -0.04934 | 0.0054551 | 0.0013672
58 | 0.99124 | -0.16762 | 0.0051983 | 0.0013028
59 | 0.99124 | -0.16749 | 0.0026325 | 0.00065976
60 | 0.99838 | -0.031177 | 0.0032672 | 0.00081885
61 | 0.99837 | -0.031338 | 0.0024795 | 0.00062143
62 | 0.97712 | -0.43968 | 0.0066556 | 0.001668
63 | 0.97741 | -0.43403 | 0 | 0
64 | 0.98018 | -0.37987 | 0 | 0
65 | 0.97566 | -0.46827 | 0.0087637 | 0.0021964
66 | 0.97331 | -0.51449 | 0.0058772 | 0.001473
67 | 0.97342 | -0.51243 | 0 | 0
68 | 0.97347 | -0.51133 | 0 | 0
69 | 0.97368 | -0.5073 | 0.0097057 | 0.0024325
70 | 0.97175 | -0.54531 | 0.011381 | 0.0028522
71 | 0.97979 | -0.38757 | 0 | 0
72 | 0.98237 | -0.33735 | 0.0087308 | 0.0021881
73 | 0.97436 | -0.49393 | 0 | 0
74 | 0.985 | -0.2872 | 0.0053923 | 0.0013514
75 | 0.98505 | -0.28618 | 0 | 0
76 | 0.97933 | -0.3966 | 0.0029469 | 0.00073857
77 | 0.99154 | -0.16146 | 0 | 0
78 | 0.99136 | -0.16495 | 0.0069814 | 0.0017497
79 | 0.98671 | -0.25345 | 0 | 0
80 | 0.98785 | -0.23167 | 0.0058499 | 0.0014661
81 | 0.98496 | -0.2872 | 0.0085573 | 0.0021447
82 | 0.99004 | -0.19048 | 0.0049093 | 0.0012304
83 | 0.97872 | -0.40866 | 0.018225 | 0.0045677
84 | 0.97205 | -0.53942 | 0.0084897 | 0.0021277
85 | 0.97223 | -0.53586 | 0.034077 | 0.0085406
86 | 0.97257 | -0.52907 | 0 | 0
87 | 0.98802 | -0.2284 | 0 | 0
88 | 0.99017 | -0.18697 | 0 | 0
89 | 0.98715 | -0.2453 | 0.0058478 | 0.0014656
90 | 0.99127 | -0.16678 | 0.0026447 | 0.00066282
91 | 0.9835 | -0.31748 | 0.0035431 | 0.00088798
92 | 0.98875 | -0.2153 | 0.0058475 | 0.0014655
93 | 0.98698 | -0.24978 | 0 | 0
94 | 0.9865 | -0.259 | 0.0094765 | 0.002375
95 | 0.98542 | -0.27893 | 0.004862 | 0.0012185
96 | 0.98551 | -0.27728 | 0.00082078 | 0.00020571
97 | 0.98563 | -0.27485 | 0 | 0
98 | 0.98573 | -0.27291 | 0 | 0
99 | 0.98545 | -0.27829 | 0.00061996 | 0.00015538
100 | 0.98614 | -0.26492 | 0 | 0
101 | 0.99797 | -0.038387 | 0.0013195 | 0.00033071
102 | 0.99525 | -0.089974 | 0 | 0
103 | 0.99441 | -0.10595 | 0.00090274 | 0.00022625
104 | 0.99497 | -0.095404 | 0.00074033 | 0.00018554
105 | 0.99508 | -0.093274 | 0.0016362 | 0.00041007
106 | 0.9829 | -0.32924 | 0 | 0
107 | 0.98249 | -0.33725 | 0.019598 | 0.0049118
108 | 0.98499 | -0.28801 | 0 | 0
109 | 0.98495 | -0.28878 | 0.008456 | 0.0021193
110 | 0.99496 | -0.095666 | 0.0010398 | 0.0002606
111 | 0.99493 | -0.096299 | 0.0012591 | 0.00031556
112 | 0.99492 | -0.096492 | 0.0020955 | 0.00052518
113 | 0.99245 | -0.14345 | 0.0083134 | 0.0020835
114 | 0.99472 | -0.10025 | 0.0017106 | 0.00042871
115 | 0.99474 | -0.099956 | 0.0053815 | 0.0013487
116 | 0.99209 | -0.15021 | 0.0061611 | 0.0015441
117 | 0.9943 | -0.1083 | 0.0029119 | 0.00072978
118 | 0.98531 | -0.28115 | 0.0064051 | 0.0016053
119 | 0.98494 | -0.28832 | 0.0040353 | 0.0010113
120 | 0.9856 | -0.27539 | 0.0069059 | 0.0017308
121 | 0.99112 | -0.1688 | 0 | 0
122 | 0.98863 | -0.21692 | 0.0075589 | 0.0018944
123 | 0.98756 | -0.23766 | 0 | 0
124 | 0.99833 | -0.032026 | 0 | 0
125 | 0.99829 | -0.032914 | 0.0021047 | 0.00052748
126 | 0.98434 | -0.30067 | 0.0022258 | 0.00055783
127 | 0.98532 | -0.281 | 0.0069605 | 0.0017445
128 | 0.99144 | -0.16359 | 0.0030965 | 0.00077607
129 | 0.99147 | -0.16309 | 0.0042002 | 0.0010527
130 | 0.99172 | -0.15819 | 0.0020829 | 0.00052203
131 | 0.99185 | -0.15565 | 0.0019722 | 0.00049427
132 | 0.99197 | -0.15335 | 0 | 0
133 | 0.9923 | -0.14693 | 0.0027979 | 0.00070121
134 | 0.99265 | -0.1402 | 0 | 0
135 | 0.99323 | -0.1291 | 0.0031474 | 0.00078882
136 | 0.9937 | -0.11999 | 0.0026543 | 0.00066523
137 | 0.98698 | -0.24906 | 0.0068292 | 0.0017116
138 | 0.987 | -0.24862 | 0.0053576 | 0.0013427
139 | 0.98723 | -0.24412 | 0 | 0
140 | 0.98529 | -0.28155 | 0.0073141 | 0.0018331
141 | 0.98658 | -0.25684 | 0.0068305 | 0.0017119
142 | 0.98644 | -0.25959 | 0.0079384 | 0.0019896
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0070489 | -0.0017666 | 0.007051 | 0.0017673 | 2.1255e-06 | 7.2636e-07 | 0.010659 | 0.010659 | 0.010659 | 0.98403 | -0.30681 | 0.98435 | -0.30048 | 2.9283
1 | -0.010226 | -0.002563 | 0.010228 | 0.002564 | 2.0309e-06 | 1.0116e-06 | 0.015458 | 0.015458 | 0.015458 | 0.98435 | -0.30048 | 0.98456 | -0.29631 | 4.2467
2 | 0.0031747 | 0.00079561 | -0.0031746 | -0.00079564 | 2.8537e-08 | -2.3738e-08 | 0.004799 | 0.0047991 | 0.0047991 | 0.98435 | -0.30048 | 0.98434 | -0.30067 | 1.3184
3 | -0.01922 | -0.0048178 | 0.019222 | 0.0048191 | 2.2165e-06 | 1.3295e-06 | 0.029048 | 0.029048 | 0.029048 | 0.98456 | -0.29631 | 0.98469 | -0.29389 | 7.9802
4 | 0.0089919 | 0.0022538 | -0.0089908 | -0.0022533 | 1.1112e-06 | 5.0718e-07 | 0.01359 | 0.01359 | 0.01359 | 0.98456 | -0.29631 | 0.98443 | -0.29891 | 3.7335
5 | -0.01694 | -0.0042474 | 0.016947 | 0.0042517 | 7.1675e-06 | 4.223e-06 | 0.025721 | 0.025721 | 0.025721 | 0.98003 | -0.38469 | 0.98049 | -0.37582 | 7.0663
6 | 0.01694 | 0.0042474 | -0.016936 | -0.0042447 | 4.6608e-06 | 2.7462e-06 | 0.025721 | 0.025722 | 0.025722 | 0.98003 | -0.38469 | 0.97974 | -0.39047 | 7.0664
7 | 0.0083239 | 0.0020863 | -0.008323 | -0.0020859 | 8.9071e-07 | 3.8236e-07 | 0.012633 | 0.012633 | 0.012633 | 0.98049 | -0.37582 | 0.98037 | -0.37806 | 3.4705
8 | -0.025271 | -0.006338 | 0.025273 | 0.0063393 | 2.1493e-06 | 1.3264e-06 | 0.038354 | 0.038354 | 0.038354 | 0.98049 | -0.37582 | 0.98058 | -0.37403 | 10.5368
9 | 0.0083228 | 0.0020862 | -0.0083214 | -0.0020855 | 1.4043e-06 | 6.037e-07 | 0.012641 | 0.012641 | 0.012641 | 0.97974 | -0.39047 | 0.97956 | -0.39401 | 3.4728
10 | -0.019222 | -0.0048191 | 0.019223 | 0.0048199 | 1.2043e-06 | 7.2231e-07 | 0.029048 | 0.029048 | 0.029048 | 0.98469 | -0.29389 | 0.98475 | -0.29258 | 7.9802
11 | 0.0068615 | 0.0017197 | -0.006861 | -0.0017195 | 5.448e-07 | 1.7698e-07 | 0.010372 | 0.010372 | 0.010372 | 0.98443 | -0.29891 | 0.98434 | -0.30057 | 2.8493
12 | -0.033662 | -0.0084418 | 0.033681 | 0.0084538 | 1.9169e-05 | 1.2021e-05 | 0.051084 | 0.051084 | 0.051084 | 0.98058 | -0.37403 | 0.98119 | -0.36209 | 14.0341
13 | 0.0073424 | 0.0018402 | -0.0073422 | -0.0018401 | 1.9904e-07 | 7.5689e-08 | 0.01126 | 0.011261 | 0.011261 | 0.97027 | -0.57472 | 0.97024 | -0.57529 | 3.0935
14 | -0.0073424 | -0.0018402 | 0.0073469 | 0.0018419 | 4.4511e-06 | 1.6918e-06 | 0.01126 | 0.01126 | 0.01126 | 0.97027 | -0.57472 | 0.97091 | -0.562 | 3.0935
15 | -0.0073469 | -0.0018419 | 0.0073499 | 0.0018431 | 3.0649e-06 | 1.164e-06 | 0.01126 | 0.01126 | 0.01126 | 0.97091 | -0.562 | 0.97135 | -0.55325 | 3.0934
16 | -0.027129 | -0.0068276 | 0.027148 | 0.0068389 | 1.8172e-05 | 1.1261e-05 | 0.040948 | 0.040948 | 0.040948 | 0.9861 | -0.26676 | 0.98682 | -0.25275 | 11.2495
17 | 0.0021059 | 0.00052768 | -0.0021059 | -0.00052778 | 3.9004e-08 | -1.0643e-07 | 0.0031778 | 0.0031778 | 0.0031778 | 0.9861 | -0.26676 | 0.98608 | -0.26714 | 0.87302
18 | 0.025024 | 0.0062999 | -0.025008 | -0.0062904 | 1.5511e-05 | 9.5575e-06 | 0.03777 | 0.03777 | 0.03777 | 0.9861 | -0.26676 | 0.98544 | -0.27973 | 10.3765
19 | 0.0094793 | 0.0023764 | -0.0094765 | -0.002375 | 2.8203e-06 | 1.3349e-06 | 0.014294 | 0.014294 | 0.014294 | 0.98682 | -0.25275 | 0.9865 | -0.259 | 3.927
20 | -0.036627 | -0.0092153 | 0.036632 | 0.0092185 | 5.1978e-06 | 3.2685e-06 | 0.055242 | 0.055242 | 0.055242 | 0.98682 | -0.25275 | 0.98698 | -0.24978 | 15.1764
21 | 0.025008 | 0.0062904 | -0.024968 | -0.0062659 | 3.9664e-05 | 2.4442e-05 | 0.03777 | 0.037771 | 0.037771 | 0.98544 | -0.27973 | 0.98373 | -0.31299 | 10.3766
22 | -0.0073499 | -0.0018431 | 0.0073527 | 0.0018441 | 2.7802e-06 | 1.0552e-06 | 0.01126 | 0.01126 | 0.01126 | 0.97135 | -0.55325 | 0.97175 | -0.54531 | 3.0933
23 | 0.023165 | 0.0058139 | -0.02316 | -0.0058109 | 4.958e-06 | 3.0365e-06 | 0.035043 | 0.035043 | 0.035043 | 0.98373 | -0.31299 | 0.9835 | -0.31748 | 9.6272
24 | -0.025801 | -0.0064685 | 0.025819 | 0.0064796 | 1.8085e-05 | 1.1171e-05 | 0.038987 | 0.038987 | 0.038987 | 0.98475 | -0.29258 | 0.98551 | -0.27788 | 10.7108
25 | 0.0022258 | 0.00055781 | -0.0022258 | -0.00055783 | 9.844e-09 | -2.3175e-08 | 0.0033647 | 0.0033647 | 0.0033647 | 0.98434 | -0.30057 | 0.98434 | -0.30067 | 0.92436
26 | -0.03163 | -0.0079359 | 0.031634 | 0.0079387 | 4.3492e-06 | 2.7187e-06 | 0.047761 | 0.047761 | 0.047761 | 0.98551 | -0.27788 | 0.98566 | -0.275 | 13.1212
27 | 0.067007 | 0.016906 | -0.066806 | -0.016778 | 0.00020127 | 0.00012815 | 0.1012 | 0.1012 | 0.1012 | 0.98566 | -0.275 | 0.98242 | -0.33793 | 27.8021
28 | -0.098642 | -0.024845 | 0.098734 | 0.024904 | 9.2654e-05 | 5.9156e-05 | 0.14896 | 0.14896 | 0.14896 | 0.98566 | -0.275 | 0.98667 | -0.25537 | 40.9232
29 | 0.058417 | 0.014675 | -0.05839 | -0.014659 | 2.6434e-05 | 1.6804e-05 | 0.088493 | 0.088493 | 0.088493 | 0.98242 | -0.33793 | 0.98194 | -0.34742 | 24.3112
30 | 0.023939 | 0.0060085 | -0.023926 | -0.0060006 | 1.2894e-05 | 7.9156e-06 | 0.036106 | 0.036106 | 0.036106 | 0.98667 | -0.25537 | 0.98609 | -0.26667 | 9.9192
31 | -0.12267 | -0.030912 | 0.1229 | 0.03106 | 0.00023141 | 0.00014787 | 0.18507 | 0.18507 | 0.18507 | 0.98667 | -0.25537 | 0.9887 | -0.21602 | 50.8423
32 | -0.016025 | -0.0040181 | 0.016032 | 0.0040222 | 6.9332e-06 | 4.0345e-06 | 0.024194 | 0.024194 | 0.024194 | 0.98562 | -0.27575 | 0.98609 | -0.26667 | 6.6468
33 | 0.016025 | 0.0040181 | -0.016021 | -0.0040159 | 3.7588e-06 | 2.1875e-06 | 0.024194 | 0.024194 | 0.024194 | 0.98562 | -0.27575 | 0.98537 | -0.28067 | 6.6468
34 | 0.0078937 | 0.0019784 | -0.0078935 | -0.0019783 | 2.0561e-07 | 8.2296e-08 | 0.011912 | 0.011912 | 0.011912 | 0.98609 | -0.26667 | 0.98606 | -0.26722 | 3.2725
35 | 0.0084592 | 0.0021207 | -0.0084576 | -0.00212 | 1.6549e-06 | 7.1473e-07 | 0.012775 | 0.012775 | 0.012775 | 0.98537 | -0.28067 | 0.98516 | -0.28478 | 3.5095
36 | 0.050209 | 0.012608 | -0.050193 | -0.012598 | 1.5534e-05 | 9.8512e-06 | 0.076094 | 0.076094 | 0.076094 | 0.98194 | -0.34742 | 0.98161 | -0.3539 | 20.905
37 | -0.13233 | -0.033422 | 0.13268 | 0.033645 | 0.00034893 | 0.00022301 | 0.19925 | 0.19925 | 0.19925 | 0.9887 | -0.21602 | 0.99155 | -0.16116 | 54.7392
38 | 0.0084576 | 0.00212 | -0.0084563 | -0.0021194 | 1.3014e-06 | 5.6219e-07 | 0.012775 | 0.012775 | 0.012775 | 0.98516 | -0.28478 | 0.98499 | -0.28801 | 3.5096
39 | 0.041877 | 0.010514 | -0.041861 | -0.010504 | 1.6351e-05 | 1.0328e-05 | 0.063488 | 0.063488 | 0.063488 | 0.98161 | -0.3539 | 0.98119 | -0.36209 | 17.4417
40 | 0.016682 | 0.0041819 | -0.016681 | -0.0041815 | 6.9594e-07 | 4.0606e-07 | 0.02485 | 0.02485 | 0.02485 | 0.99893 | -0.020565 | 0.99888 | -0.021441 | 6.8268
41 | -0.018664 | -0.0046788 | 0.01867 | 0.0046824 | 5.9747e-06 | 3.5539e-06 | 0.027803 | 0.027803 | 0.027803 | 0.99893 | -0.020565 | 0.99928 | -0.013849 | 7.6381
42 | 0.014227 | 0.0035665 | -0.014225 | -0.0035653 | 2.0054e-06 | 1.1277e-06 | 0.021194 | 0.021194 | 0.021194 | 0.99888 | -0.021441 | 0.99873 | -0.024399 | 5.8225
43 | -0.019793 | -0.0049638 | 0.019794 | 0.0049644 | 1.019e-06 | 6.1116e-07 | 0.029475 | 0.029475 | 0.029475 | 0.99928 | -0.013849 | 0.99934 | -0.012769 | 8.0975
44 | 0.012058 | 0.0030223 | -0.012056 | -0.0030212 | 2.0256e-06 | 1.0774e-06 | 0.017965 | 0.017965 | 0.017965 | 0.99873 | -0.024399 | 0.99855 | -0.027926 | 4.9356
45 | -0.02099 | -0.0052642 | 0.021003 | 0.0052719 | 1.2783e-05 | 7.7236e-06 | 0.031256 | 0.031256 | 0.031256 | 0.99934 | -0.012769 | 1 | 0 | 8.5868
46 | 0.009707 | 0.0024325 | -0.0097068 | -0.0024324 | 2.5376e-07 | 1.201e-07 | 0.014465 | 0.014465 | 0.014465 | 0.99855 | -0.027926 | 0.99852 | -0.028475 | 3.9739
47 | 0.21927 | 0.056098 | -0.21908 | -0.055976 | 0.0001914 | 0.00012193 | 0.32668 | 0.32669 | 0.32669 | 1 | 0 | 0.99905 | -0.01805 | 29.9162
48 | 0.28871 | 0.074112 | -0.28862 | -0.07406 | 8.1489e-05 | 5.2014e-05 | 0.43022 | 0.43022 | 0.43022 | 1 | 0 | 0.99969 | -0.0058172 | 39.3977
49 | 0.0078526 | 0.0019677 | -0.0078516 | -0.0019673 | 1.0108e-06 | 3.8946e-07 | 0.011702 | 0.011702 | 0.011702 | 0.99852 | -0.028475 | 0.99838 | -0.031177 | 3.2149
50 | 0.21805 | 0.055717 | -0.21797 | -0.055669 | 7.5612e-05 | 4.8167e-05 | 0.32515 | 0.32515 | 0.32515 | 0.99905 | -0.01805 | 0.99867 | -0.025223 | 29.7753
51 | 0.28732 | 0.073733 | -0.28699 | -0.073521 | 0.00033139 | 0.00021152 | 0.42828 | 0.42828 | 0.42828 | 0.99969 | -0.0058172 | 0.99843 | -0.029617 | 39.2196
52 | -0.13268 | -0.033645 | 0.13296 | 0.033825 | 0.00028091 | 0.00017954 | 0.19925 | 0.19925 | 0.19925 | 0.99155 | -0.16116 | 0.99384 | -0.11721 | 54.7392
53 | -0.13659 | -0.034734 | 0.1366 | 0.03474 | 8.2329e-06 | 5.2622e-06 | 0.20468 | 0.20468 | 0.20468 | 0.99384 | -0.11721 | 0.9939 | -0.11596 | 56.2318
54 | -0.14101 | -0.035847 | 0.14115 | 0.035933 | 0.00013583 | 8.6512e-05 | 0.2113 | 0.2113 | 0.2113 | 0.9939 | -0.11596 | 0.99495 | -0.095985 | 29.0244
55 | -0.0049136 | -0.0012315 | 0.0049144 | 0.0012315 | 8.5228e-07 | 1.6773e-08 | 0.0074104 | 0.0074102 | 0.0074104 | 0.98665 | -0.25612 | 0.98684 | -0.25248 | 2.0358
56 | -0.009297 | -0.0023299 | 0.0092982 | 0.0023304 | 1.197e-06 | 5.5855e-07 | 0.014019 | 0.014018 | 0.014019 | 0.98684 | -0.25248 | 0.98698 | -0.24978 | 3.8513
57 | 0.068329 | 0.017326 | -0.068296 | -0.017305 | 3.304e-05 | 2.1036e-05 | 0.10226 | 0.10226 | 0.10226 | 0.99495 | -0.095985 | 0.99443 | -0.10605 | 28.0939
58 | -0.20948 | -0.05326 | 0.20991 | 0.053538 | 0.00043504 | 0.00027781 | 0.31356 | 0.31356 | 0.31356 | 0.99495 | -0.095985 | 0.99721 | -0.052968 | 43.0713
59 | 0.21698 | 0.055421 | -0.21673 | -0.05526 | 0.00025265 | 0.00016094 | 0.32367 | 0.32367 | 0.32367 | 0.99867 | -0.025223 | 0.9974 | -0.04934 | 29.6403
60 | 0.28569 | 0.073197 | -0.28557 | -0.07312 | 0.00012136 | 7.7464e-05 | 0.42635 | 0.42635 | 0.42635 | 0.99843 | -0.029617 | 0.99797 | -0.038387 | 39.0432
61 | 0.066709 | 0.016908 | -0.066541 | -0.016801 | 0.00016725 | 0.00010646 | 0.099887 | 0.099887 | 0.099887 | 0.99443 | -0.10605 | 0.9917 | -0.15837 | 27.4416
62 | -0.21124 | -0.053869 | 0.21127 | 0.053893 | 3.7019e-05 | 2.3576e-05 | 0.31553 | 0.31553 | 0.31553 | 0.99721 | -0.052968 | 0.9974 | -0.04934 | 28.895
63 | 0.056912 | 0.014387 | -0.056825 | -0.014332 | 8.751e-05 | 5.5595e-05 | 0.085439 | 0.085439 | 0.085439 | 0.9917 | -0.15837 | 0.99004 | -0.19048 | 23.4722
64 | 0.0096293 | 0.0024136 | -0.0096279 | -0.0024129 | 1.4197e-06 | 6.7467e-07 | 0.014449 | 0.014449 | 0.014449 | 0.9917 | -0.15837 | 0.99154 | -0.16146 | 3.9694
65 | -0.0051983 | -0.0013028 | 0.0051984 | 0.0013028 | 3.2035e-08 | 2.4195e-09 | 0.0078036 | 0.0078036 | 0.0078036 | 0.99124 | -0.16762 | 0.99124 | -0.16749 | 2.1438
66 | -0.0078308 | -0.0019626 | 0.0078323 | 0.0019632 | 1.4556e-06 | 5.6941e-07 | 0.011755 | 0.011755 | 0.011755 | 0.99124 | -0.16749 | 0.99144 | -0.16359 | 3.2295
67 | 0.0045844 | 0.0011484 | -0.0045843 | -0.0011484 | 3.5151e-08 | -3.7603e-09 | 0.0068325 | 0.0068325 | 0.0068325 | 0.99838 | -0.031177 | 0.99837 | -0.031338 | 1.8771
68 | 0.0021048 | 0.00052702 | -0.0021047 | -0.00052722 | 6.8884e-08 | -2e-07 | 0.0031369 | 0.003137 | 0.003137 | 0.99837 | -0.031338 | 0.99833 | -0.032026 | 0.86182
69 | -0.0066556 | -0.001668 | 0.0066573 | 0.0016686 | 1.7913e-06 | 5.6381e-07 | 0.010135 | 0.010135 | 0.010135 | 0.97712 | -0.43968 | 0.97741 | -0.43403 | 2.7845
70 | -0.092684 | -0.023375 | 0.092925 | 0.023529 | 0.00024095 | 0.0001538 | 0.14116 | 0.14116 | 0.14116 | 0.97741 | -0.43403 | 0.98018 | -0.37987 | 38.7791
71 | 0.086027 | 0.021707 | -0.085886 | -0.021617 | 0.00014081 | 8.9847e-05 | 0.13102 | 0.13102 | 0.13102 | 0.97741 | -0.43403 | 0.97566 | -0.46827 | 35.9947
72 | 0.0212 | 0.0053228 | -0.021192 | -0.005318 | 7.7854e-06 | 4.7302e-06 | 0.032187 | 0.032187 | 0.032187 | 0.98018 | -0.37987 | 0.97979 | -0.38757 | 8.8425
73 | -0.11412 | -0.028852 | 0.11436 | 0.029001 | 0.00023322 | 0.000149 | 0.17334 | 0.17334 | 0.17334 | 0.98018 | -0.37987 | 0.98237 | -0.33735 | 47.6215
74 | 0.077122 | 0.01942 | -0.077028 | -0.01936 | 9.4493e-05 | 6.0249e-05 | 0.11766 | 0.11766 | 0.11766 | 0.97566 | -0.46827 | 0.97436 | -0.49393 | 32.3228
75 | -0.0058772 | -0.001473 | 0.0058777 | 0.0014731 | 5.7672e-07 | 1.3232e-07 | 0.0089851 | 0.008985 | 0.0089851 | 0.97331 | -0.51449 | 0.97342 | -0.51243 | 2.4684
76 | -0.0058777 | -0.0014731 | 0.0058781 | 0.0014732 | 3.1005e-07 | 7.1112e-08 | 0.008985 | 0.008985 | 0.008985 | 0.97342 | -0.51243 | 0.97347 | -0.51133 | 2.4684
77 | -0.0058781 | -0.0014732 | 0.0058792 | 0.0014734 | 1.1266e-06 | 2.5825e-07 | 0.008985 | 0.0089848 | 0.008985 | 0.97347 | -0.51133 | 0.97368 | -0.5073 | 2.4684
78 | -0.015585 | -0.0039059 | 0.015595 | 0.0039117 | 9.9353e-06 | 5.7773e-06 | 0.023818 | 0.023817 | 0.023818 | 0.97368 | -0.5073 | 0.97436 | -0.49393 | 6.5433
79 | -0.018733 | -0.0046964 | 0.018739 | 0.0046995 | 5.2552e-06 | 3.1523e-06 | 0.028686 | 0.028686 | 0.028686 | 0.97175 | -0.54531 | 0.97205 | -0.53942 | 7.8808
80 | 0.021192 | 0.005318 | -0.021183 | -0.0053125 | 9.114e-06 | 5.5376e-06 | 0.032187 | 0.032187 | 0.032187 | 0.97979 | -0.38757 | 0.97933 | -0.3966 | 8.8425
81 | -0.12309 | -0.031189 | 0.12339 | 0.031379 | 0.00029738 | 0.00019003 | 0.18657 | 0.18657 | 0.18657 | 0.98237 | -0.33735 | 0.98496 | -0.2872 | 51.2547
82 | 0.061433 | 0.015449 | -0.06133 | -0.015383 | 0.00010292 | 6.5483e-05 | 0.093838 | 0.093838 | 0.093838 | 0.97436 | -0.49393 | 0.97257 | -0.52907 | 25.7796
83 | -0.0053923 | -0.0013514 | 0.0053925 | 0.0013515 | 2.6086e-07 | 3.3509e-08 | 0.008146 | 0.008146 | 0.008146 | 0.985 | -0.2872 | 0.98505 | -0.28618 | 2.2379
84 | -0.0094282 | -0.0023627 | 0.0094305 | 0.0023638 | 2.2598e-06 | 1.068e-06 | 0.014242 | 0.014242 | 0.014242 | 0.98505 | -0.28618 | 0.98531 | -0.28115 | 3.9127
85 | 0.0040357 | 0.0010112 | -0.0040353 | -0.0010113 | 4.1085e-07 | -1.1228e-07 | 0.0060963 | 0.0060964 | 0.0060964 | 0.98505 | -0.28618 | 0.98494 | -0.28832 | 1.6748
86 | 0.018236 | 0.0045739 | -0.018225 | -0.0045677 | 1.0476e-05 | 6.2474e-06 | 0.027709 | 0.027709 | 0.027709 | 0.97933 | -0.3966 | 0.97872 | -0.40866 | 7.6125
87 | 0.0096279 | 0.0024129 | -0.0096263 | -0.0024122 | 1.6011e-06 | 7.6094e-07 | 0.014449 | 0.014449 | 0.014449 | 0.99154 | -0.16146 | 0.99136 | -0.16495 | 3.9694
88 | 0.0026449 | 0.00066246 | -0.0026447 | -0.00066282 | 2.3045e-07 | -3.5522e-07 | 0.0039698 | 0.00397 | 0.00397 | 0.99136 | -0.16495 | 0.99127 | -0.16678 | 1.0907
89 | -0.13216 | -0.03366 | 0.1323 | 0.033749 | 0.000139 | 8.8483e-05 | 0.19949 | 0.19949 | 0.19949 | 0.98671 | -0.25345 | 0.98785 | -0.23167 | 27.4031
90 | 0.13216 | 0.03366 | -0.13194 | -0.033524 | 0.00021476 | 0.00013671 | 0.19949 | 0.19949 | 0.19949 | 0.98671 | -0.25345 | 0.98496 | -0.2872 | 27.4031
91 | -0.13815 | -0.035215 | 0.13817 | 0.035229 | 2.1819e-05 | 1.3895e-05 | 0.20831 | 0.20831 | 0.20831 | 0.98785 | -0.23167 | 0.98802 | -0.2284 | 28.6134
92 | 0.051915 | 0.013102 | -0.051854 | -0.013062 | 6.1614e-05 | 3.9087e-05 | 0.07806 | 0.07806 | 0.07806 | 0.99004 | -0.19048 | 0.98875 | -0.2153 | 21.4451
93 | -0.027228 | -0.0068272 | 0.027242 | 0.0068356 | 1.3441e-05 | 8.3462e-06 | 0.041682 | 0.041682 | 0.041682 | 0.97205 | -0.53942 | 0.97257 | -0.52907 | 11.4511
94 | -0.034077 | -0.0085406 | 0.034088 | 0.0085475 | 1.1024e-05 | 6.9214e-06 | 0.052156 | 0.052156 | 0.052156 | 0.97223 | -0.53586 | 0.97257 | -0.52907 | 14.3285
95 | -0.18745 | -0.04762 | 0.18782 | 0.047859 | 0.00037462 | 0.00023911 | 0.28254 | 0.28254 | 0.28254 | 0.98802 | -0.2284 | 0.99017 | -0.18697 | 38.8099
96 | 0.049278 | 0.012391 | -0.049238 | -0.012366 | 3.9749e-05 | 2.5193e-05 | 0.07423 | 0.07423 | 0.07423 | 0.98802 | -0.2284 | 0.98715 | -0.2453 | 20.393
97 | -0.22243 | -0.056569 | 0.22263 | 0.056693 | 0.0001949 | 0.0001242 | 0.33456 | 0.33456 | 0.33456 | 0.99017 | -0.18697 | 0.99112 | -0.1688 | 30.6376
98 | 0.034612 | 0.0087099 | -0.034562 | -0.0086789 | 4.945e-05 | 3.1023e-05 | 0.052027 | 0.052027 | 0.052027 | 0.99017 | -0.18697 | 0.98863 | -0.21692 | 14.2931
99 | 0.04339 | 0.0109 | -0.04335 | -0.010875 | 4.0584e-05 | 2.5651e-05 | 0.065416 | 0.065416 | 0.065416 | 0.98715 | -0.2453 | 0.98614 | -0.26492 | 17.9713
100 | 0.019617 | 0.0049229 | -0.019606 | -0.0049163 | 1.0994e-05 | 6.6142e-06 | 0.029682 | 0.029682 | 0.029682 | 0.9835 | -0.31748 | 0.9829 | -0.32924 | 8.1545
101 | 0.046006 | 0.011597 | -0.04593 | -0.011549 | 7.5776e-05 | 4.7957e-05 | 0.06926 | 0.06926 | 0.06926 | 0.98875 | -0.2153 | 0.98698 | -0.24978 | 19.0276
102 | -0.004862 | -0.0012185 | 0.0048624 | 0.0012185 | 3.8159e-07 | 3.6942e-09 | 0.0073418 | 0.0073417 | 0.0073418 | 0.98542 | -0.27893 | 0.98551 | -0.27728 | 2.017
103 | -0.0056832 | -0.0014242 | 0.0056838 | 0.0014244 | 6.5932e-07 | 1.1768e-07 | 0.008581 | 0.0085809 | 0.008581 | 0.98551 | -0.27728 | 0.98563 | -0.27485 | 2.3574
104 | -0.0056838 | -0.0014244 | 0.0056844 | 0.0014245 | 5.2647e-07 | 9.3909e-08 | 0.0085809 | 0.0085808 | 0.0085809 | 0.98563 | -0.27485 | 0.98573 | -0.27291 | 2.3574
105 | 0.0149 | 0.0037362 | -0.014897 | -0.0037341 | 3.823e-06 | 2.19e-06 | 0.022494 | 0.022494 | 0.022494 | 0.98573 | -0.27291 | 0.98545 | -0.27829 | 6.1796
106 | -0.020585 | -0.0051607 | 0.020593 | 0.0051654 | 7.8343e-06 | 4.738e-06 | 0.031075 | 0.031075 | 0.031075 | 0.98573 | -0.27291 | 0.98614 | -0.26492 | 8.537
107 | 0.014277 | 0.0035787 | -0.014275 | -0.0035776 | 1.84e-06 | 1.0431e-06 | 0.021558 | 0.021558 | 0.021558 | 0.98545 | -0.27829 | 0.98532 | -0.281 | 5.9225
108 | 0.022757 | 0.0057093 | -0.022746 | -0.0057023 | 1.1353e-05 | 6.9386e-06 | 0.034341 | 0.034341 | 0.034341 | 0.98614 | -0.26492 | 0.9856 | -0.27539 | 9.4344
109 | 0.28425 | 0.072789 | -0.28354 | -0.072337 | 0.0007084 | 0.00045214 | 0.42438 | 0.42438 | 0.42438 | 0.99797 | -0.038387 | 0.99525 | -0.089974 | 38.8631
110 | 0.2389 | 0.061114 | -0.23871 | -0.060997 | 0.00018452 | 0.00011764 | 0.35762 | 0.35762 | 0.35762 | 0.99525 | -0.089974 | 0.99441 | -0.10595 | 32.7488
111 | 0.033233 | 0.0083609 | -0.033225 | -0.0083555 | 8.6189e-06 | 5.3952e-06 | 0.049699 | 0.049699 | 0.049699 | 0.99525 | -0.089974 | 0.99497 | -0.095404 | 13.6536
112 | 0.011416 | 0.0028619 | -0.011414 | -0.0028609 | 1.7945e-06 | 9.3508e-07 | 0.017069 | 0.017069 | 0.017069 | 0.99525 | -0.089974 | 0.99508 | -0.093274 | 4.6893
113 | 0.23781 | 0.06077 | -0.23738 | -0.060496 | 0.00043053 | 0.00027448 | 0.35627 | 0.35627 | 0.35627 | 0.99441 | -0.10595 | 0.99245 | -0.14345 | 32.6252
114 | 0.032485 | 0.0081699 | -0.032477 | -0.0081652 | 7.5101e-06 | 4.6963e-06 | 0.048592 | 0.048592 | 0.048592 | 0.99497 | -0.095404 | 0.99472 | -0.10025 | 13.3494
115 | 0.0097783 | 0.0024509 | -0.0097772 | -0.0024503 | 1.1144e-06 | 5.3268e-07 | 0.014622 | 0.014622 | 0.014622 | 0.99508 | -0.093274 | 0.99496 | -0.095666 | 4.0171
116 | 0.019606 | 0.0049163 | -0.019598 | -0.0049118 | 7.4897e-06 | 4.5062e-06 | 0.029682 | 0.029682 | 0.029682 | 0.9829 | -0.32924 | 0.98249 | -0.33725 | 8.1545
117 | 0.0084563 | 0.0021194 | -0.008456 | -0.0021193 | 3.0939e-07 | 1.3366e-07 | 0.012775 | 0.012775 | 0.012775 | 0.98499 | -0.28801 | 0.98495 | -0.28878 | 3.5096
118 | 0.0087374 | 0.0021897 | -0.0087371 | -0.0021896 | 2.6355e-07 | 1.1522e-07 | 0.013067 | 0.013067 | 0.013067 | 0.99496 | -0.095666 | 0.99493 | -0.096299 | 3.5899
119 | 0.007478 | 0.001874 | -0.0074779 | -0.001874 | 6.8597e-08 | 2.491e-08 | 0.011184 | 0.011184 | 0.011184 | 0.99493 | -0.096299 | 0.99492 | -0.096492 | 3.0726
120 | 0.0053824 | 0.0013488 | -0.0053815 | -0.0013487 | 8.882e-07 | 9.3897e-08 | 0.00805 | 0.0080502 | 0.0080502 | 0.99492 | -0.096492 | 0.99474 | -0.099956 | 2.2116
121 | 0.22906 | 0.058412 | -0.22899 | -0.058365 | 7.4676e-05 | 4.7597e-05 | 0.3438 | 0.3438 | 0.3438 | 0.99245 | -0.14345 | 0.99209 | -0.15021 | 31.4837
122 | 0.030766 | 0.0077365 | -0.030755 | -0.0077291 | 1.1836e-05 | 7.3818e-06 | 0.046033 | 0.046033 | 0.046033 | 0.99472 | -0.10025 | 0.9943 | -0.1083 | 12.6465
123 | 0.22283 | 0.056821 | -0.22263 | -0.056693 | 0.00019988 | 0.00012737 | 0.33456 | 0.33456 | 0.33456 | 0.99209 | -0.15021 | 0.99112 | -0.1688 | 30.6375
124 | 0.027843 | 0.0069994 | -0.027827 | -0.0069897 | 1.5529e-05 | 9.6292e-06 | 0.041675 | 0.041676 | 0.041676 | 0.9943 | -0.1083 | 0.9937 | -0.11999 | 11.4493
125 | -0.015836 | -0.003969 | 0.01584 | 0.0039716 | 4.3482e-06 | 2.5245e-06 | 0.023915 | 0.023915 | 0.023915 | 0.98531 | -0.28115 | 0.9856 | -0.27539 | 6.5701
126 | 0.027004 | 0.0067844 | -0.026977 | -0.0067679 | 2.6704e-05 | 1.6539e-05 | 0.04065 | 0.04065 | 0.04065 | 0.98863 | -0.21692 | 0.98756 | -0.23766 | 11.1676
127 | 0.026977 | 0.0067679 | -0.026969 | -0.0067627 | 8.3096e-06 | 5.1466e-06 | 0.04065 | 0.04065 | 0.04065 | 0.98756 | -0.23766 | 0.98723 | -0.24412 | 11.1676
128 | 0.0021047 | 0.00052722 | -0.0021047 | -0.00052748 | 8.8999e-08 | -2.5836e-07 | 0.003137 | 0.0031371 | 0.0031371 | 0.99833 | -0.032026 | 0.99829 | -0.032914 | 0.86185
129 | 0.0073143 | 0.0018332 | -0.0073141 | -0.0018331 | 1.9332e-07 | 6.9911e-08 | 0.011046 | 0.011046 | 0.011046 | 0.98532 | -0.281 | 0.98529 | -0.28155 | 3.0346
130 | -0.010929 | -0.0027392 | 0.010929 | 0.0027394 | 2.5684e-07 | 1.3155e-07 | 0.016403 | 0.016403 | 0.016403 | 0.99144 | -0.16359 | 0.99147 | -0.16309 | 4.5062
131 | -0.015129 | -0.003792 | 0.015133 | 0.003794 | 3.5339e-06 | 2.0259e-06 | 0.022706 | 0.022706 | 0.022706 | 0.99147 | -0.16309 | 0.99172 | -0.15819 | 6.238
132 | -0.017216 | -0.0043161 | 0.017218 | 0.0043173 | 2.0869e-06 | 1.228e-06 | 0.025832 | 0.025832 | 0.025832 | 0.99172 | -0.15819 | 0.99185 | -0.15565 | 7.0966
133 | -0.01919 | -0.0048116 | 0.019192 | 0.0048128 | 2.0994e-06 | 1.2565e-06 | 0.02879 | 0.02879 | 0.02879 | 0.99185 | -0.15565 | 0.99197 | -0.15335 | 7.9094
134 | -0.019192 | -0.0048128 | 0.019198 | 0.0048163 | 5.8754e-06 | 3.5161e-06 | 0.02879 | 0.02879 | 0.02879 | 0.99197 | -0.15335 | 0.9923 | -0.14693 | 7.9094
135 | -0.021996 | -0.0055176 | 0.022003 | 0.0055219 | 7.0635e-06 | 4.2969e-06 | 0.032986 | 0.032986 | 0.032986 | 0.9923 | -0.14693 | 0.99265 | -0.1402 | 9.062
136 | -0.022003 | -0.0055219 | 0.022015 | 0.005529 | 1.1655e-05 | 7.0898e-06 | 0.032986 | 0.032986 | 0.032986 | 0.99265 | -0.1402 | 0.99323 | -0.1291 | 9.062
137 | -0.025162 | -0.0063178 | 0.025173 | 0.0063245 | 1.0935e-05 | 6.733e-06 | 0.037701 | 0.037701 | 0.037701 | 0.99323 | -0.1291 | 0.9937 | -0.11999 | 10.3574
138 | -0.0068292 | -0.0017116 | 0.0068293 | 0.0017116 | 1.4387e-07 | 4.5825e-08 | 0.010296 | 0.010296 | 0.010296 | 0.98698 | -0.24906 | 0.987 | -0.24862 | 2.8286
139 | -0.012187 | -0.0030544 | 0.01219 | 0.0030558 | 2.612e-06 | 1.4079e-06 | 0.018373 | 0.018373 | 0.018373 | 0.987 | -0.24862 | 0.98723 | -0.24412 | 5.0476
140 | 0.014779 | 0.003707 | -0.01477 | -0.0037019 | 8.9522e-06 | 5.1147e-06 | 0.022277 | 0.022277 | 0.022277 | 0.98723 | -0.24412 | 0.98658 | -0.25684 | 6.1201
141 | 0.0079395 | 0.00199 | -0.0079384 | -0.0019896 | 1.0432e-06 | 4.1994e-07 | 0.011975 | 0.011975 | 0.011975 | 0.98658 | -0.25684 | 0.98644 | -0.25959 | 3.2898

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53063 | 0.13548

## res_load
| p_mw | q_mvar
0 | 0.0070489 | 0.0017666
1 | 0.0031746 | 0.00079564
2 | 0.0086127 | 0.0021585
3 | 0.0021293 | 0.00053366
4 | 0.008323 | 0.0020859
5 | 0.0083888 | 0.0021024
6 | 0.0083214 | 0.0020855
7 | 0.0073422 | 0.0018401
8 | 0.0021059 | 0.00052778
9 | 0.0018035 | 0.00045199
10 | 0.0065779 | 0.0016486
11 | 0.0046352 | 0.0011617
12 | 0.0058108 | 0.0014563
13 | 0.0083893 | 0.0021026
14 | 0.0075622 | 0.0018953
15 | 0.0081819 | 0.0020506
16 | 0.0094249 | 0.0023621
17 | 0.0078935 | 0.0019783
18 | 0.0083161 | 0.0020842
19 | 0.0081791 | 0.0020499
20 | 0.0019826 | 0.00049688
21 | 0.0024541 | 0.00061506
22 | 0.001123 | 0.00028145
23 | 0.0021668 | 0.00054306
24 | 0.001196 | 0.00029974
25 | 0.002349 | 0.00058871
26 | 0.0018541 | 0.00046469
27 | 0.0010336 | 0.00025905
28 | 0.0013071 | 0.0003276
29 | 0.003629 | 0.00090951
30 | 0.0044175 | 0.0011071
31 | 0.0049136 | 0.0012315
32 | 0.0043826 | 0.0010984
33 | 0.00098917 | 0.00024791
34 | 0.0012923 | 0.00032387
35 | 0.001587 | 0.00039774
36 | 0.0013236 | 0.00033172
37 | 0.0054551 | 0.0013672
38 | 0.0051983 | 0.0013028
39 | 0.0026325 | 0.00065976
40 | 0.0032672 | 0.00081885
41 | 0.0024795 | 0.00062143
42 | 0.0066556 | 0.001668
43 | 0.0087637 | 0.0021964
44 | 0.0058772 | 0.001473
45 | 0.0097057 | 0.0024325
46 | 0.011381 | 0.0028522
47 | 0.0087308 | 0.0021881
48 | 0.0053923 | 0.0013514
49 | 0.0029469 | 0.00073857
50 | 0.0069814 | 0.0017497
51 | 0.0058499 | 0.0014661
52 | 0.0085573 | 0.0021447
53 | 0.0049093 | 0.0012304
54 | 0.018225 | 0.0045677
55 | 0.0084897 | 0.0021277
56 | 0.034077 | 0.0085406
57 | 0.0058478 | 0.0014656
58 | 0.0026447 | 0.00066282
59 | 0.0035431 | 0.00088798
60 | 0.0058475 | 0.0014655
61 | 0.0094765 | 0.002375
62 | 0.004862 | 0.0012185
63 | 0.00082078 | 0.00020571
64 | 0.00061996 | 0.00015538
65 | 0.0013195 | 0.00033071
66 | 0.00090274 | 0.00022625
67 | 0.00074033 | 0.00018554
68 | 0.0016362 | 0.00041007
69 | 0.019598 | 0.0049118
70 | 0.008456 | 0.0021193
71 | 0.0010398 | 0.0002606
72 | 0.0012591 | 0.00031556
73 | 0.0020955 | 0.00052518
74 | 0.0083134 | 0.0020835
75 | 0.0017106 | 0.00042871
76 | 0.0053815 | 0.0013487
77 | 0.0061611 | 0.0015441
78 | 0.0029119 | 0.00072978
79 | 0.0064051 | 0.0016053
80 | 0.0040353 | 0.0010113
81 | 0.0069059 | 0.0017308
82 | 0.0075589 | 0.0018944
83 | 0.0021047 | 0.00052748
84 | 0.0022258 | 0.00055783
85 | 0.0069605 | 0.0017445
86 | 0.0030965 | 0.00077607
87 | 0.0042002 | 0.0010527
88 | 0.0020829 | 0.00052203
89 | 0.0019722 | 0.00049427
90 | 0.0027979 | 0.00070121
91 | 0.0031474 | 0.00078882
92 | 0.0026543 | 0.00066523
93 | 0.0068292 | 0.0017116
94 | 0.0053576 | 0.0013427
95 | 0.0073141 | 0.0018331
96 | 0.0068305 | 0.0017119
97 | 0.0079384 | 0.0019896

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1