## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_198-66_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_198-66_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_198-66_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_198-66_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_198-66_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_198-66_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_198-66_0_3_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_198-66_0_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_198-66_0_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_198-66_0_3_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_198-66_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_198-66_0_3_node_49 | 0.4 | n |  | TRUE
12 | bus_LV_198-66_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_198-66_0_3_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_198-66_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_198-66_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_198-66_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_198-66_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_198-66_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_198-66_0_3_node_84 | 0.4 | n |  | TRUE
20 | bus_LV_198-66_0_3_node_85 | 0.4 | n |  | TRUE
21 | bus_LV_198-66_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_198-66_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_198-66_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_198-66_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_198-66_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_198-66_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_198-66_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_198-66_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_198-66_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_198-66_0_3_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_198-66_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_198-66_0_3_node_74 | 0.4 | n |  | TRUE
33 | bus_LV_198-66_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_198-66_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_198-66_0_3_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_198-66_0_3_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_198-66_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_198-66_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_198-66_0_3_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_198-66_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_198-66_0_3_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_198-66_0_3_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_198-66_0_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_198-66_0_3_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_198-66_0_3_node_110 | 0.4 | n |  | TRUE
46 | bus_LV_198-66_0_3_node_125 | 0.4 | n |  | TRUE
47 | bus_LV_198-66_0_3_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_198-66_0_3_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_198-66_0_3_node_111 | 0.4 | n |  | TRUE
50 | bus_LV_198-66_0_3_node_126 | 0.4 | n |  | TRUE
51 | bus_LV_198-66_0_3_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_198-66_0_3_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_198-66_0_3_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_198-66_0_3_node_71 | 0.4 | n |  | TRUE
55 | bus_LV_198-66_0_3_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_198-66_0_3_node_70 | 0.4 | n |  | TRUE
57 | bus_LV_198-66_0_3_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_198-66_0_3_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_198-66_0_3_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_198-66_0_3_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_198-66_0_3_node_124 | 0.4 | n |  | TRUE
62 | bus_LV_198-66_0_3_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_198-66_0_3_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_198-66_0_3_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_198-66_0_3_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_198-66_0_3_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_198-66_0_3_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_198-66_0_3_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_198-66_0_3_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_198-66_0_3_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_198-66_0_3_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_198-66_0_3_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_198-66_0_3_node_83 | 0.4 | n |  | TRUE
74 | bus_LV_198-66_0_3_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_198-66_0_3_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_198-66_0_3_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_198-66_0_3_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_198-66_0_3_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_198-66_0_3_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_198-66_0_3_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_198-66_0_3_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_198-66_0_3_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_198-66_0_3_node_118 | 0.4 | n |  | TRUE
84 | bus_LV_198-66_0_3_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_198-66_0_3_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_198-66_0_3_node_119 | 0.4 | n |  | TRUE
87 | bus_LV_198-66_0_3_node_116 | 0.4 | n |  | TRUE
88 | bus_LV_198-66_0_3_node_72 | 0.4 | n |  | TRUE
89 | bus_LV_198-66_0_3_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_198-66_0_3_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_198-66_0_3_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_198-66_0_3_node_115 | 0.4 | n |  | TRUE
93 | bus_LV_198-66_0_3_node_93 | 0.4 | n |  | TRUE
94 | bus_LV_198-66_0_3_node_127 | 0.4 | n |  | TRUE
95 | bus_LV_198-66_0_3_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_198-66_0_3_node_86 | 0.4 | n |  | TRUE
97 | bus_LV_198-66_0_3_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_198-66_0_3_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_198-66_0_3_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_198-66_0_3_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_198-66_0_3_node_105 | 0.4 | n |  | TRUE
102 | bus_LV_198-66_0_3_node_107 | 0.4 | n |  | TRUE
103 | bus_LV_198-66_0_3_node_104 | 0.4 | n |  | TRUE
104 | bus_LV_198-66_0_3_node_106 | 0.4 | n |  | TRUE
105 | bus_LV_198-66_0_3_node_92 | 0.4 | n |  | TRUE
106 | bus_LV_198-66_0_3_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_198-66_0_3_node_99 | 0.4 | n |  | TRUE
108 | bus_LV_198-66_0_3_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_198-66_0_3_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_198-66_0_3_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_198-66_0_3_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_198-66_0_3_node_98 | 0.4 | n |  | TRUE
113 | bus_LV_198-66_0_3_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_198-66_0_3_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_198-66_0_3_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_198-66_0_3_node_133 | 0.4 | n |  | TRUE
117 | bus_LV_198-66_0_3_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_198-66_0_3_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_198-66_0_3_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_198-66_0_3_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_198-66_0_3_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_198-66_0_3_node_117 | 0.4 | n |  | TRUE
123 | bus_LV_198-66_0_3_node_120 | 0.4 | n |  | TRUE
124 | bus_LV_198-66_0_3_node_122 | 0.4 | n |  | TRUE
125 | bus_LV_198-66_0_3_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_198-66_0_3_node_128 | 0.4 | n |  | TRUE
127 | bus_LV_198-66_0_3_node_129 | 0.4 | n |  | TRUE
128 | bus_LV_198-66_0_3_node_130 | 0.4 | n |  | TRUE
129 | bus_LV_198-66_0_3_node_131 | 0.4 | n |  | TRUE
130 | bus_MV_501_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_198-66_0_3_load_0 | 0 | 0.0041632 | 0.0010434 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_198-66_0_3_load_1 | 1 | 0.0037024 | 0.00092792 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_198-66_0_3_load_3 | 3 | 0.0041607 | 0.0010428 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_198-66_0_3_load_4 | 4 | 0.0031677 | 0.0007939 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_198-66_0_3_load_15 | 6 | 0.0070032 | 0.0017552 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_198-66_0_3_load_50 | 7 | 0.0073379 | 0.001839 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_198-66_0_3_load_51 | 9 | 0.0050281 | 0.0012602 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_198-66_0_3_load_49 | 11 | 0.012549 | 0.0031451 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_198-66_0_3_load_23 | 12 | 0.0068823 | 0.0017249 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_198-66_0_3_load_43 | 13 | 0.0045536 | 0.0011412 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_198-66_0_3_load_6 | 14 | 0.0021774 | 0.00054572 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_198-66_0_3_load_7 | 15 | 0.0017061 | 0.00042758 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_198-66_0_3_load_8 | 16 | 0.0015476 | 0.00038786 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_198-66_0_3_load_9 | 17 | 0.0023124 | 0.00057954 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_198-66_0_3_load_10 | 18 | 0.0020231 | 0.00050704 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_198-66_0_3_load_11 | 21 | 0.0037753 | 0.00094619 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_198-66_0_3_load_12 | 22 | 0.0016243 | 0.0004071 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_198-66_0_3_load_14 | 23 | 0.0013816 | 0.00034626 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_198-66_0_3_load_16 | 24 | 0.0015018 | 0.00037638 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_198-66_0_3_load_18 | 25 | 0.0044362 | 0.0011118 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_198-66_0_3_load_19 | 26 | 0.0026206 | 0.00065679 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_198-66_0_3_load_20 | 27 | 0.0040349 | 0.0010112 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_198-66_0_3_load_21 | 28 | 0.0025103 | 0.00062913 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_198-66_0_3_load_22 | 29 | 0.0045176 | 0.0011322 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_198-66_0_3_load_73 | 30 | 0.0025639 | 0.00064257 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_198-66_0_3_load_25 | 31 | 0.0066502 | 0.0016667 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_198-66_0_3_load_74 | 32 | 0.00242 | 0.00060651 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_198-66_0_3_load_26 | 33 | 0.0060046 | 0.0015049 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_198-66_0_3_load_27 | 34 | 0.01195 | 0.0029948 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_198-66_0_3_load_40 | 35 | 0.0083003 | 0.0020803 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_198-66_0_3_load_48 | 36 | 0.007183 | 0.0018002 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_198-66_0_3_load_28 | 37 | 0.012622 | 0.0031633 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_198-66_0_3_load_29 | 38 | 0.0045733 | 0.0011462 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_198-66_0_3_load_31 | 40 | 0.0055027 | 0.0013791 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_198-66_0_3_load_32 | 41 | 0.0075926 | 0.0019029 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_198-66_0_3_load_33 | 42 | 0.0054675 | 0.0013703 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_198-66_0_3_load_34 | 43 | 0.0034896 | 0.00087458 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_198-66_0_3_load_110 | 45 | 0.0028136 | 0.00070514 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_198-66_0_3_load_125 | 46 | 0.0023591 | 0.00059125 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_198-66_0_3_load_44 | 47 | 0.007323 | 0.0018353 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_198-66_0_3_load_36 | 48 | 0.0027097 | 0.00067911 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_198-66_0_3_load_111 | 49 | 0.0022023 | 0.00055194 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_198-66_0_3_load_126 | 50 | 0.0021183 | 0.00053091 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_198-66_0_3_load_35 | 51 | 0.0068705 | 0.0017219 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_198-66_0_3_load_71 | 54 | 0.00092313 | 0.00023136 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_198-66_0_3_load_70 | 56 | 0.00090326 | 0.00022638 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_198-66_0_3_load_46 | 57 | 0.0084668 | 0.002122 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_198-66_0_3_load_41 | 58 | 0.0051118 | 0.0012811 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_198-66_0_3_load_42 | 59 | 0.0071078 | 0.0017814 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_198-66_0_3_load_47 | 60 | 0.00099145 | 0.00024848 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_198-66_0_3_load_124 | 61 | 0.0082713 | 0.002073 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_198-66_0_3_load_52 | 62 | 0.0022237 | 0.00055731 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_198-66_0_3_load_53 | 63 | 0.0019909 | 0.00049897 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_198-66_0_3_load_54 | 64 | 0.0026367 | 0.00066083 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_198-66_0_3_load_55 | 65 | 0.0019635 | 0.00049211 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_198-66_0_3_load_56 | 66 | 0.0021525 | 0.00053947 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_198-66_0_3_load_60 | 67 | 0.0016554 | 0.00041489 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_198-66_0_3_load_57 | 68 | 0.0022894 | 0.00057378 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_198-66_0_3_load_61 | 69 | 0.0024924 | 0.00062467 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_198-66_0_3_load_58 | 70 | 0.0017469 | 0.00043782 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_198-66_0_3_load_81 | 72 | 0.0015564 | 0.00039008 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_198-66_0_3_load_83 | 73 | 0.0016684 | 0.00041813 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_198-66_0_3_load_68 | 74 | 0.0035747 | 0.00089591 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_198-66_0_3_load_69 | 75 | 0.0048015 | 0.0012034 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_198-66_0_3_load_62 | 76 | 0.003311 | 0.00082982 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_198-66_0_3_load_63 | 77 | 0.0021866 | 0.00054802 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_198-66_0_3_load_67 | 80 | 0.0021704 | 0.00054396 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_198-66_0_3_load_79 | 81 | 0.0051707 | 0.0012959 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_198-66_0_3_load_76 | 82 | 0.00088672 | 0.00022223 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_198-66_0_3_load_80 | 84 | 0.0051519 | 0.0012912 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_198-66_0_3_load_75 | 85 | 0.010355 | 0.0025953 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_198-66_0_3_load_119 | 86 | 0.00096188 | 0.00024107 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_198-66_0_3_load_116 | 87 | 0.0043632 | 0.0010935 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_198-66_0_3_load_72 | 88 | 0.0021037 | 0.00052723 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_198-66_0_3_load_82 | 89 | 0.0024636 | 0.00061743 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_198-66_0_3_load_77 | 90 | 0.00087096 | 0.00021828 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_198-66_0_3_load_78 | 91 | 0.01053 | 0.0026391 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_198-66_0_3_load_115 | 92 | 0.0025693 | 0.00064392 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_198-66_0_3_load_93 | 93 | 0.00063244 | 0.00015851 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_198-66_0_3_load_127 | 94 | 0.0018383 | 0.00046071 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_198-66_0_3_load_91 | 95 | 0.0009384 | 0.00023518 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_198-66_0_3_load_86 | 96 | 0.0015413 | 0.00038628 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_198-66_0_3_load_87 | 97 | 0.0014705 | 0.00036855 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_198-66_0_3_load_89 | 99 | 0.0013014 | 0.00032615 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_198-66_0_3_load_90 | 100 | 0.0020917 | 0.00052422 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_198-66_0_3_load_105 | 101 | 0.0021265 | 0.00053295 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_198-66_0_3_load_107 | 102 | 0.00194 | 0.00048621 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_198-66_0_3_load_104 | 103 | 0.0013496 | 0.00033825 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_198-66_0_3_load_106 | 104 | 0.0033906 | 0.00084976 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_198-66_0_3_load_92 | 105 | 0.00055967 | 0.00014027 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_198-66_0_3_load_94 | 106 | 0.0021201 | 0.00053134 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_198-66_0_3_load_99 | 107 | 0.0062565 | 0.001568 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_198-66_0_3_load_95 | 109 | 0.00061365 | 0.0001538 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_198-66_0_3_load_96 | 110 | 0.0014829 | 0.00037166 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_198-66_0_3_load_97 | 111 | 0.00067752 | 0.0001698 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_198-66_0_3_load_98 | 112 | 0.0013575 | 0.00034022 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_198-66_0_3_load_101 | 113 | 0.0014863 | 0.00037251 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_198-66_0_3_load_133 | 116 | 0.0022857 | 0.00057284 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_198-66_0_3_load_114 | 118 | 0.0018203 | 0.00045621 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_198-66_0_3_load_112 | 119 | 0.0021518 | 0.00053929 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_198-66_0_3_load_113 | 120 | 0.0037301 | 0.00093485 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_198-66_0_3_load_108 | 121 | 0.0039788 | 0.00099719 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_198-66_0_3_load_117 | 122 | 0.0025074 | 0.00062841 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_198-66_0_3_load_120 | 123 | 0.0036178 | 0.0009067 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_198-66_0_3_load_122 | 124 | 0.00023667 | 5.9314e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_198-66_0_3_load_121 | 125 | 0.0015691 | 0.00039325 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_198-66_0_3_load_128 | 126 | 0.0046228 | 0.0011586 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_198-66_0_3_load_129 | 127 | 0.0021382 | 0.00053589 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_198-66_0_3_load_130 | 128 | 0.0029842 | 0.0007479 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_198-66_0_3_load_131 | 129 | 0.003317 | 0.00083132 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_198-66_0_3_line_0 |  | 0 | 1 | 0.00075433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_198-66_0_3_line_1 |  | 0 | 2 | 0.028536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_198-66_0_3_line_2 |  | 1 | 3 | 0.01662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_198-66_0_3_line_3 |  | 2 | 4 | 0.011513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_198-66_0_3_line_4 |  | 2 | 5 | 0.02543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_198-66_0_3_line_5 |  | 3 | 6 | 0.034497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_198-66_0_3_line_6 |  | 4 | 7 | 0.042793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_198-66_0_3_line_7 |  | 5 | 8 | 0.044379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_198-66_0_3_line_8 |  | 5 | 9 | 0.020663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_198-66_0_3_line_9 |  | 6 | 10 | 0.012817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_198-66_0_3_line_10 |  | 7 | 11 | 0.010393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_198-66_0_3_line_11 |  | 8 | 12 | 0.05261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_198-66_0_3_line_12 |  | 9 | 13 | 0.015153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_198-66_0_3_line_13 |  | 10 | 24 | 0.024483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_198-66_0_3_line_14 |  | 10 | 21 | 0.02025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_198-66_0_3_line_15 |  | 11 | 41 | 0.03225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_198-66_0_3_line_16 |  | 13 | 59 | 0.013432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_198-66_0_3_line_17 |  | 14 | 15 | 0.007625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_198-66_0_3_line_18 |  | 14 | 16 | 0.015464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_198-66_0_3_line_19 |  | 15 | 17 | 0.021603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_198-66_0_3_line_20 |  | 16 | 18 | 0.014209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_198-66_0_3_line_21 |  | 18 | 19 | 0.018328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_198-66_0_3_line_22 |  | 19 | 20 | 0.00906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_198-66_0_3_line_23 |  | 20 | 92 | 0.0027093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_198-66_0_3_line_24 |  | 20 | 93 | 0.01412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_198-66_0_3_line_25 |  | 21 | 22 | 0.02362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_198-66_0_3_line_26 |  | 22 | 23 | 0.020904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_198-66_0_3_line_27 |  | 25 | 26 | 0.017708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_198-66_0_3_line_28 |  | 25 | 27 | 0.0017027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_198-66_0_3_line_29 |  | 26 | 28 | 0.0078946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_198-66_0_3_line_30 |  | 27 | 29 | 0.0080145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_198-66_0_3_line_31 |  | 28 | 30 | 0.016963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_198-66_0_3_line_32 |  | 29 | 31 | 0.01397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_198-66_0_3_line_33 |  | 30 | 32 | 0.0077116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_198-66_0_3_line_34 |  | 31 | 33 | 0.0049597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_198-66_0_3_line_35 |  | 32 | 89 | 0.017986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_198-66_0_3_line_36 |  | 33 | 34 | 0.0080621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_198-66_0_3_line_37 |  | 34 | 35 | 0.013758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_198-66_0_3_line_38 |  | 35 | 36 | 0.02157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_198-66_0_3_line_39 |  | 36 | 57 | 0.0047499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_198-66_0_3_line_40 |  | 37 | 38 | 0.013746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_198-66_0_3_line_41 |  | 37 | 39 | 0.013141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_198-66_0_3_line_42 |  | 38 | 40 | 0.011207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_198-66_0_3_line_43 |  | 39 | 41 | 0.027272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_198-66_0_3_line_44 |  | 39 | 42 | 0.043332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_198-66_0_3_line_45 |  | 39 | 43 | 0.01548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_198-66_0_3_line_46 |  | 40 | 44 | 0.021261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_198-66_0_3_line_47 |  | 42 | 45 | 0.0056839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_198-66_0_3_line_48 |  | 43 | 46 | 0.0001719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_198-66_0_3_line_49 |  | 44 | 47 | 0.016126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_198-66_0_3_line_50 |  | 44 | 48 | 0.0084185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_198-66_0_3_line_51 |  | 45 | 49 | 0.017481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_198-66_0_3_line_52 |  | 46 | 50 | 0.010181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_198-66_0_3_line_53 |  | 47 | 55 | 0.023384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_198-66_0_3_line_54 |  | 48 | 51 | 0.034375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_198-66_0_3_line_55 |  | 49 | 120 | 0.0093927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_198-66_0_3_line_56 |  | 50 | 126 | 2.738e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_198-66_0_3_line_57 |  | 51 | 52 | 0.050141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_198-66_0_3_line_58 |  | 52 | 53 | 0.003576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_198-66_0_3_line_59 |  | 53 | 54 | 0.063459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_198-66_0_3_line_60 |  | 54 | 56 | 0.0097785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_198-66_0_3_line_61 |  | 55 | 57 | 0.025952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_198-66_0_3_line_62 |  | 55 | 60 | 0.01986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_198-66_0_3_line_63 |  | 56 | 88 | 0.0028951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_198-66_0_3_line_64 |  | 58 | 59 | 0.0015868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_198-66_0_3_line_65 |  | 60 | 61 | 0.0028582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_198-66_0_3_line_66 |  | 62 | 63 | 0.01286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_198-66_0_3_line_67 |  | 62 | 64 | 0.021589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_198-66_0_3_line_68 |  | 63 | 65 | 0.011406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_198-66_0_3_line_69 |  | 64 | 66 | 0.006022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_198-66_0_3_line_70 |  | 65 | 67 | 0.013097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_198-66_0_3_line_71 |  | 66 | 68 | 0.0078491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_198-66_0_3_line_72 |  | 67 | 69 | 0.012476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_198-66_0_3_line_73 |  | 68 | 70 | 0.032198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_198-66_0_3_line_74 |  | 69 | 74 | 0.010004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_198-66_0_3_line_75 |  | 70 | 71 | 0.018869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_198-66_0_3_line_76 |  | 71 | 72 | 0.022534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_198-66_0_3_line_77 |  | 72 | 73 | 0.017524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_198-66_0_3_line_78 |  | 73 | 89 | 0.0078971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_198-66_0_3_line_79 |  | 74 | 75 | 0.016261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_198-66_0_3_line_80 |  | 75 | 84 | 0.014608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_198-66_0_3_line_81 |  | 76 | 77 | 0.039311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_198-66_0_3_line_82 |  | 77 | 78 | 0.028526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_198-66_0_3_line_83 |  | 78 | 79 | 0.005599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_198-66_0_3_line_84 |  | 78 | 80 | 0.020954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_198-66_0_3_line_85 |  | 79 | 81 | 0.028237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_198-66_0_3_line_86 |  | 79 | 82 | 0.030613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_198-66_0_3_line_87 |  | 80 | 83 | 0.010947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_198-66_0_3_line_88 |  | 81 | 84 | 0.0083413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_198-66_0_3_line_89 |  | 82 | 85 | 0.0011538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_198-66_0_3_line_90 |  | 83 | 86 | 0.027081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_198-66_0_3_line_91 |  | 83 | 87 | 0.013727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_198-66_0_3_line_92 |  | 85 | 90 | 0.0022894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_198-66_0_3_line_93 |  | 86 | 123 | 0.0011954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_198-66_0_3_line_94 |  | 87 | 122 | 0.00093546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_198-66_0_3_line_95 |  | 90 | 91 | 0.014641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_198-66_0_3_line_96 |  | 92 | 94 | 0.038984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_198-66_0_3_line_97 |  | 93 | 95 | 0.022089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_198-66_0_3_line_98 |  | 94 | 118 | 0.00090585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_198-66_0_3_line_99 |  | 95 | 105 | 0.024268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_198-66_0_3_line_100 |  | 96 | 97 | 0.0061003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_198-66_0_3_line_101 |  | 96 | 98 | 0.00035458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_198-66_0_3_line_102 |  | 98 | 99 | 0.015099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_198-66_0_3_line_103 |  | 98 | 100 | 0.014937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_198-66_0_3_line_104 |  | 99 | 101 | 0.0021906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_198-66_0_3_line_105 |  | 100 | 102 | 0.020458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_198-66_0_3_line_106 |  | 101 | 103 | 0.0056173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_198-66_0_3_line_107 |  | 102 | 104 | 0.009117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_198-66_0_3_line_108 |  | 103 | 114 | 0.012469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_198-66_0_3_line_109 |  | 104 | 121 | 0.0088743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_198-66_0_3_line_110 |  | 105 | 106 | 0.0052277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_198-66_0_3_line_111 |  | 106 | 107 | 0.019713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_198-66_0_3_line_112 |  | 107 | 108 | 0.035762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_198-66_0_3_line_113 |  | 108 | 115 | 0.064853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_198-66_0_3_line_114 |  | 109 | 110 | 0.016517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_198-66_0_3_line_115 |  | 109 | 111 | 0.0059427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_198-66_0_3_line_116 |  | 110 | 112 | 0.0055556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_198-66_0_3_line_117 |  | 112 | 113 | 0.0025849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_198-66_0_3_line_118 |  | 113 | 114 | 0.026548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_198-66_0_3_line_119 |  | 114 | 117 | 0.015351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_198-66_0_3_line_120 |  | 115 | 116 | 0.031865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_198-66_0_3_line_121 |  | 117 | 118 | 0.0044423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_198-66_0_3_line_122 |  | 117 | 119 | 0.017996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_198-66_0_3_line_123 |  | 119 | 120 | 0.0018796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_198-66_0_3_line_124 |  | 123 | 124 | 0.083897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_198-66_0_3_line_125 |  | 124 | 125 | 0.037668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_198-66_0_3_line_126 |  | 126 | 127 | 0.0096355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_198-66_0_3_line_127 |  | 127 | 128 | 0.00071549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_198-66_0_3_line_128 |  | 128 | 129 | 0.008065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_198-66_0_3_trafo_40 | 0.63 MVA 20/0.4 kV | 130 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2697218.0637 | 1244155.2534 | 2697217.7418 | 1244154.5712
1 | 2697232.0104 | 1244179.8618 | 2697228.3806 | 1244176.2885 | 2697226.4098 | 1244172.9425 | 2697224.0578 | 1244167.9558 | 2697218.0637 | 1244155.2534
2 | 2697217.7418 | 1244154.5712 | 2697210.6489 | 1244139.5404
3 | 2697232.0104 | 1244179.8618 | 2697235.1141 | 1244177.2663 | 2697241.0838 | 1244172.7807
4 | 2697213.8441 | 1244197.611 | 2697217.823 | 1244193.2618 | 2697221.4557 | 1244189.2849 | 2697232.0104 | 1244179.8618
5 | 2697195.9268 | 1244108.3425 | 2697210.6489 | 1244139.5404
6 | 2697241.0838 | 1244172.7807 | 2697244.0064 | 1244170.5847 | 2697250.2069 | 1244166.2719 | 2697261.2681 | 1244159.1589 | 2697267.0488 | 1244156.0179 | 2697277.5132 | 1244150.4482
7 | 2697182.7895 | 1244229.282 | 2697198.6993 | 1244214.0866 | 2697202.016 | 1244210.4826 | 2697213.8441 | 1244197.611
8 | 2697213.8441 | 1244197.611 | 2697228.8331 | 1244211.8342 | 2697228.8331 | 1244211.8342
9 | 2697190.4569 | 1244096.751 | 2697195.9268 | 1244108.3425
10 | 2697286.6879 | 1244145.565 | 2697277.5132 | 1244150.4482
11 | 2697182.7895 | 1244229.282 | 2697191.2969 | 1244238.6952 | 2697189.8296 | 1244278.59
12 | 2697228.1579 | 1244226.9723 | 2697228.8331 | 1244211.8342
13 | 2697190.4569 | 1244096.751 | 2697171.5497 | 1244112.3046
14 | 2697190.4569 | 1244096.751 | 2697181.822 | 1244078.4344
15 | 2697286.6879 | 1244145.565 | 2697296.5572 | 1244140.312 | 2697315.1579 | 1244130.4155
16 | 2697227.5593 | 1244240.391 | 2697228.1579 | 1244226.9723
17 | 2697200.7307 | 1244011.2904 | 2697197.7458 | 1244012.217 | 2697194.2994 | 1244015.11
18 | 2697200.7307 | 1244011.2904 | 2697205.6393 | 1244009.7667 | 2697210.6573 | 1244005.668 | 2697213.8149 | 1244003.4736
19 | 2697202.9296 | 1244030.7383 | 2697200.0666 | 1244028.334 | 2697192.3261 | 1244021.4575 | 2697191.8599 | 1244017.1577 | 2697194.2994 | 1244015.11
20 | 2697227.7735 | 1244004.1658 | 2697225.0815 | 1244005.0483 | 2697213.8149 | 1244003.4736 | 2697213.8149 | 1244003.4736
21 | 2697245.6292 | 1244000.2147 | 2697233.19 | 1244002.3903 | 2697227.7735 | 1244004.1658
22 | 2697250.3167 | 1244007.9752 | 2697245.6292 | 1244000.2147
23 | 2697250.3167 | 1244007.9752 | 2697251.7623 | 1244010.2666
24 | 2697250.3167 | 1244007.9752 | 2697261.4139 | 1243999.2452
25 | 2697181.822 | 1244078.4344 | 2697171.7502 | 1244057.0699 | 2697171.7502 | 1244057.0699
26 | 2697171.7502 | 1244057.0699 | 2697160.2666 | 1244044.7613 | 2697156.8145 | 1244042.6053
27 | 2697291.9314 | 1244242.2048 | 2697288.1217 | 1244244.8979 | 2697277.9671 | 1244253.0832
28 | 2697293.3218 | 1244241.222 | 2697291.9314 | 1244242.2048
29 | 2697271.8207 | 1244258.0377 | 2697277.9671 | 1244253.0832
30 | 2697293.3218 | 1244241.222 | 2697299.8662 | 1244236.5957
31 | 2697271.8207 | 1244258.0377 | 2697258.6143 | 1244268.683
32 | 2697311.2741 | 1244228.5316 | 2697299.8662 | 1244236.5957
33 | 2697252.6104 | 1244273.5226 | 2697258.6143 | 1244268.683
34 | 2697315.3241 | 1244225.6687 | 2697311.2741 | 1244228.5316
35 | 2697252.6104 | 1244273.5226 | 2697238.6075 | 1244284.81
36 | 2697315.3241 | 1244225.6687 | 2697321.9074 | 1244221.0149
37 | 2697333.1418 | 1244213.0735 | 2697321.9074 | 1244221.0149
38 | 2697333.1418 | 1244213.0735 | 2697339.9757 | 1244208.2426 | 2697351.9903 | 1244202.7726
39 | 2697356.3133 | 1244200.8044 | 2697351.9903 | 1244202.7726
40 | 2697360.0529 | 1244134.6193 | 2697349.4081 | 1244125.9223
41 | 2697339.234 | 1244117.6057 | 2697342.6872 | 1244120.4312 | 2697349.4081 | 1244125.9223
42 | 2697369.1686 | 1244141.1252 | 2697362.1459 | 1244136.3293 | 2697360.0529 | 1244134.6193
43 | 2697339.234 | 1244117.6057 | 2697315.1579 | 1244130.4155
44 | 2697339.234 | 1244117.6057 | 2697336.4015 | 1244115.1907 | 2697331.624 | 1244111.5429 | 2697305.351 | 1244090.6006
45 | 2697339.234 | 1244117.6057 | 2697348.4077 | 1244112.6747 | 2697352.3614 | 1244109.5083
46 | 2697386.9544 | 1244152.7712 | 2697374.9422 | 1244145.0681 | 2697369.1686 | 1244141.1252
47 | 2697305.351 | 1244090.6006 | 2697303.8923 | 1244089.4379 | 2697301.4363 | 1244086.5141
48 | 2697352.4956 | 1244109.4008 | 2697352.3614 | 1244109.5083
49 | 2697386.9544 | 1244152.7712 | 2697384.9351 | 1244156.0628 | 2697381.8106 | 1244161.3044 | 2697379.415 | 1244166.9821
50 | 2697386.9544 | 1244152.7712 | 2697393.9767 | 1244157.4143
51 | 2697301.4363 | 1244086.5141 | 2697295.1221 | 1244078.9972 | 2697291.0325 | 1244072.515
52 | 2697352.4956 | 1244109.4008 | 2697360.4418 | 1244103.0368
53 | 2697379.9326 | 1244190.051 | 2697378.3753 | 1244182.7088 | 2697378.1571 | 1244175.7443 | 2697378.8378 | 1244168.3498 | 2697379.415 | 1244166.9821
54 | 2697422.6511 | 1244176.3733 | 2697393.9767 | 1244157.4143
55 | 2697286.0208 | 1244064.5711 | 2697291.0325 | 1244072.515
56 | 2697360.444 | 1244103.0351 | 2697360.4418 | 1244103.0368
57 | 2697464.4765 | 1244204.0277 | 2697422.6511 | 1244176.3733
58 | 2697467.545 | 1244205.8795 | 2697464.4765 | 1244204.0277
59 | 2697467.545 | 1244205.8795 | 2697462.2785 | 1244209.9183 | 2697438.9543 | 1244219.5425 | 2697449.0563 | 1244246.8738 | 2697446.6806 | 1244247.4796 | 2697446.6806 | 1244247.4796
60 | 2697451.0212 | 1244256.242 | 2697446.6806 | 1244247.4796
61 | 2697379.9326 | 1244190.051 | 2697356.3133 | 1244200.8044
62 | 2697379.9326 | 1244190.051 | 2697386.4197 | 1244208.8218
63 | 2697452.3062 | 1244258.8363 | 2697451.0212 | 1244256.242
64 | 2697227.4886 | 1244241.9763 | 2697227.5593 | 1244240.391
65 | 2697386.4197 | 1244208.8218 | 2697387.3533 | 1244211.5232
66 | 2697266.4662 | 1244336.1958 | 2697268.4792 | 1244335.1114 | 2697276.8701 | 1244328.6771
67 | 2697266.4662 | 1244336.1958 | 2697247.4593 | 1244346.435
68 | 2697285.9213 | 1244321.7364 | 2697276.8701 | 1244328.6771
69 | 2697242.1576 | 1244349.2911 | 2697247.4593 | 1244346.435
70 | 2697285.9213 | 1244321.7364 | 2697296.3147 | 1244313.7666
71 | 2697242.1576 | 1244349.2911 | 2697235.2475 | 1244353.0137
72 | 2697306.3277 | 1244306.3306 | 2697303.3757 | 1244308.352 | 2697296.3147 | 1244313.7666
73 | 2697235.2475 | 1244353.0137 | 2697235.2475 | 1244353.0137 | 2697214.1502 | 1244328.691
74 | 2697306.3277 | 1244306.3306 | 2697312.0976 | 1244302.3794 | 2697314.7748 | 1244301.0026
75 | 2697201.2714 | 1244314.9057 | 2697211.1098 | 1244325.1858 | 2697214.1502 | 1244328.691
76 | 2697201.2714 | 1244314.9057 | 2697218.8156 | 1244300.7637
77 | 2697232.4592 | 1244289.766 | 2697218.8156 | 1244300.7637
78 | 2697232.4592 | 1244289.766 | 2697238.6075 | 1244284.81
79 | 2697314.7748 | 1244301.0026 | 2697322.1974 | 1244297.1855 | 2697329.6763 | 1244294.5971
80 | 2697329.6763 | 1244294.5971 | 2697330.8781 | 1244294.1812 | 2697340.8188 | 1244292.2317 | 2697344.0203 | 1244292.0496
81 | 2697338.2053 | 1244354.9816 | 2697343.8777 | 1244348.5248 | 2697353.1169 | 1244334.0543 | 2697360.8779 | 1244322.9497
82 | 2697377.2193 | 1244299.5679 | 2697360.8779 | 1244322.9497
83 | 2697380.3416 | 1244294.9156 | 2697377.2193 | 1244299.5679
84 | 2697377.2193 | 1244299.5679 | 2697379.6423 | 1244307.5805 | 2697381.3498 | 1244312.2231 | 2697384.0103 | 1244316.3589 | 2697385.9476 | 1244318.2663
85 | 2697380.3416 | 1244294.9156 | 2697363.7969 | 1244292.1531 | 2697352.3482 | 1244291.5759
86 | 2697380.3416 | 1244294.9156 | 2697391.6256 | 1244277.4541 | 2697394.7919 | 1244269.6668 | 2697395.0763 | 1244268.2792
87 | 2697395.3044 | 1244323.5831 | 2697392.8661 | 1244322.9426 | 2697388.0416 | 1244320.3281 | 2697385.9476 | 1244318.2663
88 | 2697344.0203 | 1244292.0496 | 2697352.3482 | 1244291.5759 | 2697352.3482 | 1244291.5759
89 | 2697395.308 | 1244267.1489 | 2697395.0763 | 1244268.2792
90 | 2697395.3044 | 1244323.5831 | 2697397.5545 | 1244324.176 | 2697404.3534 | 1244324.3878 | 2697410.6515 | 1244322.4119 | 2697420.774 | 1244317.2766
91 | 2697395.3044 | 1244323.5831 | 2697389.0889 | 1244335.8217
92 | 2697395.308 | 1244267.1489 | 2697395.7677 | 1244264.9062
93 | 2697421.8401 | 1244316.7357 | 2697420.774 | 1244317.2766
94 | 2697388.6653 | 1244336.6558 | 2697389.0889 | 1244335.8217
95 | 2697395.7677 | 1244264.9062 | 2697396.616 | 1244260.7678 | 2697397.1957 | 1244252.6266 | 2697397.1216 | 1244250.3734
96 | 2697272.5623 | 1244043.2381 | 2697251.7623 | 1244010.2666
97 | 2697278.7743 | 1243985.588 | 2697261.4139 | 1243999.2452
98 | 2697272.5623 | 1244043.2381 | 2697273.0456 | 1244044.0042
99 | 2697278.7743 | 1243985.588 | 2697297.8477 | 1243970.5833
100 | 2697317.1415 | 1244018.6474 | 2697321.6544 | 1244014.5428
101 | 2697316.8792 | 1244018.886 | 2697317.1415 | 1244018.6474
102 | 2697316.8792 | 1244018.886 | 2697305.7072 | 1244029.0423
103 | 2697316.8792 | 1244018.886 | 2697325.5622 | 1244031.0399
104 | 2697304.0863 | 1244030.5158 | 2697305.7072 | 1244029.0423
105 | 2697325.5622 | 1244031.0399 | 2697337.4546 | 1244047.6863
106 | 2697299.3306 | 1244033.4853 | 2697303.651 | 1244030.9115 | 2697304.0863 | 1244030.5158
107 | 2697337.4546 | 1244047.6863 | 2697342.7544 | 1244055.1047
108 | 2697288.6214 | 1244039.8719 | 2697296.0943 | 1244035.4132 | 2697299.3306 | 1244033.4853
109 | 2697335.712 | 1244060.5044 | 2697342.7544 | 1244055.1047
110 | 2697301.9564 | 1243967.351 | 2697297.8477 | 1243970.5833
111 | 2697301.9564 | 1243967.351 | 2697316.2927 | 1243956.0729 | 2697317.3881 | 1243955.0886
112 | 2697344.3809 | 1243931.6372 | 2697330.0865 | 1243943.6786 | 2697317.3881 | 1243955.0886
113 | 2697377.2223 | 1243987.3741 | 2697351.4939 | 1243939.9046 | 2697344.3809 | 1243931.6372
114 | 2697299.9046 | 1244001.5163 | 2697287.2724 | 1244012.1581
115 | 2697299.9046 | 1244001.5163 | 2697304.4495 | 1243997.6875
116 | 2697283.0235 | 1244015.7375 | 2697287.2724 | 1244012.1581
117 | 2697281.058 | 1244017.4133 | 2697281.0921 | 1244017.3646 | 2697283.0235 | 1244015.7375
118 | 2697288.6214 | 1244039.8719 | 2697278.2121 | 1244024.7452 | 2697278.3599 | 1244021.2672 | 2697281.058 | 1244017.4133
119 | 2697288.6214 | 1244039.8719 | 2697275.4158 | 1244047.7614
120 | 2697377.2223 | 1243987.3741 | 2697349.0246 | 1244002.3673
121 | 2697275.4158 | 1244047.7614 | 2697273.0456 | 1244044.0042
122 | 2697275.4158 | 1244047.7614 | 2697285.0179 | 1244062.9814
123 | 2697286.0208 | 1244064.5711 | 2697285.0179 | 1244062.9814
124 | 2697421.8401 | 1244316.7357 | 2697475.8348 | 1244380.9486
125 | 2697503.3955 | 1244356.6155 | 2697489.1422 | 1244363.7994 | 2697475.8348 | 1244380.9486
126 | 2697367.9648 | 1244097.0118 | 2697360.444 | 1244103.0351
127 | 2697368.5233 | 1244096.5646 | 2697367.9648 | 1244097.0118
128 | 2697368.5233 | 1244096.5646 | 2697374.8183 | 1244091.523

## bus_geodata
| x | y | coords
0 | 2697218.0637 | 1244155.2534
1 | 2697217.7418 | 1244154.5712
2 | 2697232.0104 | 1244179.8618
3 | 2697210.6489 | 1244139.5404
4 | 2697241.0838 | 1244172.7807
5 | 2697213.8441 | 1244197.611
6 | 2697195.9268 | 1244108.3425
7 | 2697277.5132 | 1244150.4482
8 | 2697182.7895 | 1244229.282
9 | 2697228.8331 | 1244211.8342
10 | 2697190.4569 | 1244096.751
11 | 2697286.6879 | 1244145.565
12 | 2697189.8296 | 1244278.59
13 | 2697228.1579 | 1244226.9723
14 | 2697200.7307 | 1244011.2904
15 | 2697194.2994 | 1244015.11
16 | 2697213.8149 | 1244003.4736
17 | 2697202.9296 | 1244030.7383
18 | 2697227.7735 | 1244004.1658
19 | 2697245.6292 | 1244000.2147
20 | 2697250.3167 | 1244007.9752
21 | 2697181.822 | 1244078.4344
22 | 2697171.7502 | 1244057.0699
23 | 2697156.8145 | 1244042.6053
24 | 2697171.5497 | 1244112.3046
25 | 2697291.9314 | 1244242.2048
26 | 2697277.9671 | 1244253.0832
27 | 2697293.3218 | 1244241.222
28 | 2697271.8207 | 1244258.0377
29 | 2697299.8662 | 1244236.5957
30 | 2697258.6143 | 1244268.683
31 | 2697311.2741 | 1244228.5316
32 | 2697252.6104 | 1244273.5226
33 | 2697315.3241 | 1244225.6687
34 | 2697321.9074 | 1244221.0149
35 | 2697333.1418 | 1244213.0735
36 | 2697351.9903 | 1244202.7726
37 | 2697349.4081 | 1244125.9223
38 | 2697360.0529 | 1244134.6193
39 | 2697339.234 | 1244117.6057
40 | 2697369.1686 | 1244141.1252
41 | 2697315.1579 | 1244130.4155
42 | 2697305.351 | 1244090.6006
43 | 2697352.3614 | 1244109.5083
44 | 2697386.9544 | 1244152.7712
45 | 2697301.4363 | 1244086.514
46 | 2697352.4956 | 1244109.4008
47 | 2697379.415 | 1244166.9821
48 | 2697393.9768 | 1244157.4143
49 | 2697291.0325 | 1244072.515
50 | 2697360.4418 | 1244103.0368
51 | 2697422.6511 | 1244176.3733
52 | 2697464.4765 | 1244204.0277
53 | 2697467.545 | 1244205.8795
54 | 2697446.6806 | 1244247.4796
55 | 2697379.9326 | 1244190.051
56 | 2697451.0212 | 1244256.242
57 | 2697356.3133 | 1244200.8044
58 | 2697227.4886 | 1244241.9763
59 | 2697227.5593 | 1244240.391
60 | 2697386.4197 | 1244208.8218
61 | 2697387.3533 | 1244211.5232
62 | 2697266.4662 | 1244336.1958
63 | 2697276.8701 | 1244328.677
64 | 2697247.4593 | 1244346.435
65 | 2697285.9213 | 1244321.7364
66 | 2697242.1576 | 1244349.2911
67 | 2697296.3147 | 1244313.7666
68 | 2697235.2475 | 1244353.0137
69 | 2697306.3277 | 1244306.3306
70 | 2697214.1502 | 1244328.691
71 | 2697201.2714 | 1244314.9057
72 | 2697218.8156 | 1244300.7637
73 | 2697232.4592 | 1244289.766
74 | 2697314.7748 | 1244301.0026
75 | 2697329.6763 | 1244294.5971
76 | 2697338.2053 | 1244354.9816
77 | 2697360.8779 | 1244322.9497
78 | 2697377.2193 | 1244299.5679
79 | 2697380.3416 | 1244294.9156
80 | 2697385.9476 | 1244318.2663
81 | 2697352.3482 | 1244291.5759
82 | 2697395.0763 | 1244268.2792
83 | 2697395.3044 | 1244323.5831
84 | 2697344.0203 | 1244292.0496
85 | 2697395.308 | 1244267.1489
86 | 2697420.774 | 1244317.2766
87 | 2697389.0889 | 1244335.8217
88 | 2697452.3062 | 1244258.8363
89 | 2697238.6075 | 1244284.81
90 | 2697395.7677 | 1244264.9062
91 | 2697397.1216 | 1244250.3734
92 | 2697251.7623 | 1244010.2666
93 | 2697261.4139 | 1243999.2452
94 | 2697272.5623 | 1244043.2381
95 | 2697278.7743 | 1243985.588
96 | 2697317.1415 | 1244018.6474
97 | 2697321.6544 | 1244014.5428
98 | 2697316.8792 | 1244018.886
99 | 2697305.7072 | 1244029.0423
100 | 2697325.5622 | 1244031.0399
101 | 2697304.0863 | 1244030.5158
102 | 2697337.4546 | 1244047.6863
103 | 2697299.3306 | 1244033.4853
104 | 2697342.7544 | 1244055.1047
105 | 2697297.8477 | 1243970.5833
106 | 2697301.9564 | 1243967.351
107 | 2697317.3881 | 1243955.0886
108 | 2697344.3809 | 1243931.6372
109 | 2697299.9046 | 1244001.5163
110 | 2697287.2724 | 1244012.1581
111 | 2697304.4495 | 1243997.6875
112 | 2697283.0235 | 1244015.7375
113 | 2697281.058 | 1244017.4133
114 | 2697288.6214 | 1244039.8719
115 | 2697377.2223 | 1243987.3741
116 | 2697349.0246 | 1244002.3673
117 | 2697275.4158 | 1244047.7614
118 | 2697273.0456 | 1244044.0042
119 | 2697285.0179 | 1244062.9814
120 | 2697286.0208 | 1244064.5711
121 | 2697335.712 | 1244060.5044
122 | 2697388.6653 | 1244336.6558
123 | 2697421.8401 | 1244316.7357
124 | 2697475.8348 | 1244380.9486
125 | 2697503.3955 | 1244356.6155
126 | 2697360.444 | 1244103.0351
127 | 2697367.9648 | 1244097.0118
128 | 2697368.5233 | 1244096.5646
129 | 2697374.8183 | 1244091.523
130 | 2697379.9326 | 1244190.051

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97611 | -0.46035 | 0.0041632 | 0.0010434
1 | 0.97609 | -0.46067 | 0.0037024 | 0.00092792
2 | 0.97683 | -0.4461 | 0 | 0
3 | 0.97579 | -0.46659 | 0.0041607 | 0.0010428
4 | 0.97743 | -0.43433 | 0.0031677 | 0.0007939
5 | 0.97615 | -0.45944 | 0 | 0
6 | 0.9753 | -0.47625 | 0.0070032 | 0.0017552
7 | 0.97978 | -0.38825 | 0.0073379 | 0.001839
8 | 0.97587 | -0.46503 | 0 | 0
9 | 0.97573 | -0.46768 | 0.0050281 | 0.0012602
10 | 0.9752 | -0.4782 | 0 | 0
11 | 0.98043 | -0.3757 | 0.012549 | 0.0031451
12 | 0.97553 | -0.47166 | 0.0068823 | 0.0017249
13 | 0.9755 | -0.47234 | 0.0045536 | 0.0011412
14 | 0.97778 | -0.4277 | 0.0021774 | 0.00054572
15 | 0.97776 | -0.42825 | 0.0017061 | 0.00042758
16 | 0.97787 | -0.42595 | 0.0015476 | 0.00038786
17 | 0.97771 | -0.42917 | 0.0023124 | 0.00057954
18 | 0.97798 | -0.42394 | 0.0020231 | 0.00050704
19 | 0.97814 | -0.42068 | 0 | 0
20 | 0.97822 | -0.41907 | 0 | 0
21 | 0.97507 | -0.48071 | 0.0037753 | 0.00094619
22 | 0.97501 | -0.48202 | 0.0016243 | 0.0004071
23 | 0.97498 | -0.48254 | 0.0013816 | 0.00034626
24 | 0.97517 | -0.47887 | 0.0015018 | 0.00037638
25 | 0.99445 | -0.10491 | 0.0044362 | 0.0011118
26 | 0.99285 | -0.13531 | 0.0026206 | 0.00065679
27 | 0.99461 | -0.10186 | 0.0040349 | 0.0010112
28 | 0.99215 | -0.14853 | 0.0025103 | 0.00062913
29 | 0.9954 | -0.086944 | 0.0045176 | 0.0011322
30 | 0.9907 | -0.17623 | 0.0025639 | 0.00064257
31 | 0.99683 | -0.059894 | 0.0066502 | 0.0016667
32 | 0.99006 | -0.1885 | 0.00242 | 0.00060651
33 | 0.99737 | -0.049731 | 0.0060046 | 0.0015049
34 | 0.99828 | -0.032388 | 0.01195 | 0.0029948
35 | 1 | 0 | -0.3889 | -0.099502
36 | 0.99755 | -0.046381 | 0.007183 | 0.0018002
37 | 0.98607 | -0.26608 | 0.012622 | 0.0031633
38 | 0.98728 | -0.24266 | 0.0045733 | 0.0011462
39 | 0.98499 | -0.28703 | 0 | 0
40 | 0.98829 | -0.22316 | 0.0055027 | 0.0013791
41 | 0.98279 | -0.32958 | 0.0075926 | 0.0019029
42 | 0.98218 | -0.34166 | 0.0054675 | 0.0013703
43 | 0.98469 | -0.29288 | 0.0034896 | 0.00087458
44 | 0.99026 | -0.18522 | 0 | 0
45 | 0.98184 | -0.34829 | 0.0028136 | 0.00070514
46 | 0.98468 | -0.29293 | 0.0023591 | 0.00059125
47 | 0.99186 | -0.15462 | 0.007323 | 0.0018353
48 | 0.99016 | -0.18725 | 0.0027097 | 0.00067911
49 | 0.98084 | -0.36781 | 0.0022023 | 0.00055194
50 | 0.98454 | -0.29571 | 0.0021183 | 0.00053091
51 | 0.98982 | -0.19385 | 0.0068705 | 0.0017219
52 | 0.98964 | -0.19736 | 0 | 0
53 | 0.98963 | -0.19761 | 0 | 0
54 | 0.9894 | -0.20205 | 0.00092313 | 0.00023136
55 | 0.99425 | -0.10891 | 0 | 0
56 | 0.98937 | -0.20258 | 0.00090326 | 0.00022638
57 | 0.99702 | -0.056326 | 0.0084668 | 0.002122
58 | 0.97534 | -0.47549 | 0.0051118 | 0.0012811
59 | 0.97535 | -0.47534 | 0.0071078 | 0.0017814
60 | 0.99409 | -0.11215 | 0.00099145 | 0.00024848
61 | 0.99407 | -0.11257 | 0.0082713 | 0.002073
62 | 0.97863 | -0.40896 | 0.0022237 | 0.00055731
63 | 0.97779 | -0.42545 | 0.0019909 | 0.00049897
64 | 0.98009 | -0.38048 | 0.0026367 | 0.00066083
65 | 0.97706 | -0.43968 | 0.0019635 | 0.00049211
66 | 0.98052 | -0.37226 | 0.0021525 | 0.00053947
67 | 0.97625 | -0.45558 | 0.0016554 | 0.00041489
68 | 0.98108 | -0.36125 | 0.0022894 | 0.00057378
69 | 0.9755 | -0.47037 | 0.0024924 | 0.00062467
70 | 0.98347 | -0.31491 | 0.0017469 | 0.00043782
71 | 0.98491 | -0.28726 | 0 | 0
72 | 0.98662 | -0.25434 | 0.0015564 | 0.00039008
73 | 0.98797 | -0.22834 | 0.0016684 | 0.00041813
74 | 0.97491 | -0.48179 | 0.0035747 | 0.00089591
75 | 0.97402 | -0.49931 | 0.0048015 | 0.0012034
76 | 0.97138 | -0.55142 | 0.003311 | 0.00082982
77 | 0.9715 | -0.54901 | 0.0021866 | 0.00054802
78 | 0.97165 | -0.54612 | 0 | 0
79 | 0.97176 | -0.54395 | 0 | 0
80 | 0.97135 | -0.55209 | 0.0021704 | 0.00054396
81 | 0.97291 | -0.52127 | 0.0051707 | 0.0012959
82 | 0.97111 | -0.55676 | 0.00088672 | 0.00022223
83 | 0.97121 | -0.55477 | 0 | 0
84 | 0.97329 | -0.51378 | 0.0051519 | 0.0012912
85 | 0.97109 | -0.55722 | 0.010355 | 0.0025953
86 | 0.97105 | -0.55797 | 0.00096188 | 0.00024107
87 | 0.97113 | -0.55651 | 0.0043632 | 0.0010935
88 | 0.98937 | -0.20269 | 0.0021037 | 0.00052723
89 | 0.9886 | -0.21641 | 0.0024636 | 0.00061743
90 | 0.97107 | -0.5577 | 0.00087096 | 0.00021828
91 | 0.97092 | -0.56055 | 0.01053 | 0.0026391
92 | 0.97828 | -0.41796 | 0.0025693 | 0.00064392
93 | 0.97806 | -0.42236 | 0.00063244 | 0.00015851
94 | 0.97919 | -0.40012 | 0.0018383 | 0.00046071
95 | 0.97781 | -0.42726 | 0.0009384 | 0.00023518
96 | 0.97843 | -0.41506 | 0.0015413 | 0.00038628
97 | 0.97842 | -0.41523 | 0.0014705 | 0.00036855
98 | 0.97843 | -0.41504 | 0 | 0
99 | 0.97863 | -0.41108 | 0.0013014 | 0.00032615
100 | 0.97827 | -0.41815 | 0.0020917 | 0.00052422
101 | 0.97866 | -0.41046 | 0.0021265 | 0.00053295
102 | 0.97809 | -0.42162 | 0.00194 | 0.00048621
103 | 0.97876 | -0.40863 | 0.0013496 | 0.00033825
104 | 0.97803 | -0.42284 | 0.0033906 | 0.00084976
105 | 0.97755 | -0.43223 | 0.00055967 | 0.00014027
106 | 0.9775 | -0.43324 | 0.0021201 | 0.00053134
107 | 0.97735 | -0.43632 | 0.0062565 | 0.001568
108 | 0.97727 | -0.43781 | 0 | 0
109 | 0.97879 | -0.40786 | 0.00061365 | 0.0001538
110 | 0.97881 | -0.40747 | 0.0014829 | 0.00037166
111 | 0.97879 | -0.40793 | 0.00067752 | 0.0001698
112 | 0.97883 | -0.40719 | 0.0013575 | 0.00034022
113 | 0.97884 | -0.40699 | 0.0014863 | 0.00037251
114 | 0.97898 | -0.40428 | 0 | 0
115 | 0.97713 | -0.44052 | 0 | 0
116 | 0.97707 | -0.44185 | 0.0022857 | 0.00057284
117 | 0.97933 | -0.39735 | 0 | 0
118 | 0.97921 | -0.39968 | 0.0018203 | 0.00045621
119 | 0.98022 | -0.37984 | 0.0021518 | 0.00053929
120 | 0.98032 | -0.37794 | 0.0037301 | 0.00093485
121 | 0.978 | -0.42348 | 0.0039788 | 0.00099719
122 | 0.97112 | -0.55656 | 0.0025074 | 0.00062841
123 | 0.97105 | -0.55809 | 0.0036178 | 0.0009067
124 | 0.97091 | -0.56089 | 0.00023667 | 5.9314e-05
125 | 0.97085 | -0.56198 | 0.0015691 | 0.00039325
126 | 0.98454 | -0.29571 | 0.0046228 | 0.0011586
127 | 0.98447 | -0.29717 | 0.0021382 | 0.00053589
128 | 0.98446 | -0.29726 | 0.0029842 | 0.0007479
129 | 0.98444 | -0.29774 | 0.003317 | 0.00083132
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.023164 | 0.0058093 | -0.023164 | -0.0058091 | 3.5276e-07 | 2.1634e-07 | 0.035314 | 0.035314 | 0.035314 | 0.97611 | -0.46035 | 0.97609 | -0.46067 | 9.7015
1 | -0.027327 | -0.0068527 | 0.027346 | 0.0068642 | 1.8572e-05 | 1.1529e-05 | 0.04166 | 0.04166 | 0.04166 | 0.97611 | -0.46035 | 0.97683 | -0.4461 | 11.4451
2 | 0.019461 | 0.0048811 | -0.019456 | -0.0048778 | 5.4864e-06 | 3.3036e-06 | 0.029669 | 0.029669 | 0.029669 | 0.97609 | -0.46067 | 0.97579 | -0.46659 | 8.151
3 | -0.056066 | -0.014074 | 0.056097 | 0.014094 | 3.1498e-05 | 2.0014e-05 | 0.085414 | 0.085414 | 0.085414 | 0.97683 | -0.4461 | 0.97743 | -0.43433 | 23.4653
4 | 0.02872 | 0.0072099 | -0.028702 | -0.0071985 | 1.8256e-05 | 1.1366e-05 | 0.043754 | 0.043754 | 0.043754 | 0.97683 | -0.4461 | 0.97615 | -0.45944 | 12.0202
5 | 0.015295 | 0.0038351 | -0.015288 | -0.003831 | 7.038e-06 | 4.0736e-06 | 0.023325 | 0.023325 | 0.023325 | 0.97579 | -0.46659 | 0.9753 | -0.47625 | 6.4079
6 | -0.059265 | -0.014888 | 0.059396 | 0.014971 | 0.00013066 | 8.3088e-05 | 0.090236 | 0.090236 | 0.090236 | 0.97743 | -0.43433 | 0.97978 | -0.38825 | 24.7901
7 | 0.0068863 | 0.0017262 | -0.0068845 | -0.0017256 | 1.8339e-06 | 6.1909e-07 | 0.010497 | 0.010498 | 0.010498 | 0.97615 | -0.45944 | 0.97587 | -0.46503 | 2.884
8 | 0.021815 | 0.0054723 | -0.021807 | -0.005467 | 8.5699e-06 | 5.2266e-06 | 0.033256 | 0.033256 | 0.033256 | 0.97615 | -0.45944 | 0.97573 | -0.46768 | 9.1364
9 | 0.0082849 | 0.0020758 | -0.0082841 | -0.0020755 | 7.6794e-07 | 3.3155e-07 | 0.01264 | 0.01264 | 0.01264 | 0.9753 | -0.47625 | 0.9752 | -0.4782 | 3.4726
10 | -0.066734 | -0.01681 | 0.066774 | 0.016836 | 4.0058e-05 | 2.5506e-05 | 0.10138 | 0.10138 | 0.10138 | 0.97978 | -0.38825 | 0.98043 | -0.3757 | 27.8517
11 | 0.0068845 | 0.0017256 | -0.0068823 | -0.0017249 | 2.1741e-06 | 7.3438e-07 | 0.010498 | 0.010498 | 0.010498 | 0.97587 | -0.46503 | 0.97553 | -0.47166 | 2.884
12 | 0.016779 | 0.0042069 | -0.016775 | -0.0042047 | 3.7207e-06 | 2.192e-06 | 0.025588 | 0.025588 | 0.025588 | 0.97573 | -0.46768 | 0.9755 | -0.47234 | 7.0298
13 | 0.0015018 | 0.0003761 | -0.0015018 | -0.00037638 | 4.8209e-08 | -2.746e-07 | 0.0022914 | 0.0022916 | 0.0022916 | 0.9752 | -0.4782 | 0.97517 | -0.47887 | 0.62955
14 | 0.0067823 | 0.0016994 | -0.0067815 | -0.0016991 | 8.1325e-07 | 2.6786e-07 | 0.010349 | 0.010349 | 0.010349 | 0.9752 | -0.4782 | 0.97507 | -0.48071 | 2.8431
15 | -0.079323 | -0.019981 | 0.079498 | 0.020093 | 0.00017539 | 0.00011184 | 0.12043 | 0.12043 | 0.12043 | 0.98043 | -0.3757 | 0.98279 | -0.32958 | 33.084
16 | 0.012221 | 0.0030635 | -0.01222 | -0.0030625 | 1.7506e-06 | 9.5271e-07 | 0.018643 | 0.018643 | 0.018643 | 0.9755 | -0.47234 | 0.97535 | -0.47534 | 5.1216
17 | 0.0040187 | 0.0010069 | -0.0040186 | -0.0010069 | 1.0694e-07 | -2.7193e-08 | 0.0061156 | 0.0061157 | 0.0061157 | 0.97778 | -0.4277 | 0.97776 | -0.42825 | 1.6801
18 | -0.0061961 | -0.0015526 | 0.0061966 | 0.0015527 | 5.156e-07 | 1.36e-07 | 0.0094293 | 0.0094292 | 0.0094293 | 0.97778 | -0.4277 | 0.97787 | -0.42595 | 2.5905
19 | 0.0023125 | 0.00057933 | -0.0023124 | -0.00057954 | 1.0033e-07 | -2.0672e-07 | 0.0035192 | 0.0035193 | 0.0035193 | 0.97776 | -0.42825 | 0.97771 | -0.42917 | 0.96685
20 | -0.0077442 | -0.0019406 | 0.0077449 | 0.0019409 | 7.3993e-07 | 2.9528e-07 | 0.011784 | 0.011784 | 0.011784 | 0.97787 | -0.42595 | 0.97798 | -0.42394 | 3.2374
21 | -0.0097681 | -0.0024479 | 0.0097696 | 0.0024487 | 1.5182e-06 | 7.4161e-07 | 0.014862 | 0.014862 | 0.014862 | 0.97798 | -0.42394 | 0.97814 | -0.42068 | 4.083
22 | -0.0097696 | -0.0024487 | 0.0097703 | 0.002449 | 7.5046e-07 | 3.6656e-07 | 0.014862 | 0.014862 | 0.014862 | 0.97814 | -0.42068 | 0.97822 | -0.41907 | 4.083
23 | -0.022573 | -0.0056588 | 0.022574 | 0.0056595 | 1.1979e-06 | 7.3263e-07 | 0.034337 | 0.034337 | 0.034337 | 0.97822 | -0.41907 | 0.97828 | -0.41796 | 9.4333
24 | 0.012803 | 0.0032097 | -0.012801 | -0.0032086 | 2.0082e-06 | 1.108e-06 | 0.019475 | 0.019475 | 0.019475 | 0.97822 | -0.41907 | 0.97806 | -0.42236 | 5.3503
25 | 0.0030061 | 0.00075294 | -0.003006 | -0.00075312 | 1.864e-07 | -1.753e-07 | 0.0045874 | 0.0045875 | 0.0045875 | 0.97507 | -0.48071 | 0.97501 | -0.48202 | 1.2603
26 | 0.0013816 | 0.00034602 | -0.0013816 | -0.00034626 | 3.4851e-08 | -2.3839e-07 | 0.0021085 | 0.0021086 | 0.0021086 | 0.97501 | -0.48202 | 0.97498 | -0.48254 | 0.57928
27 | 0.098885 | 0.025423 | -0.098739 | -0.02533 | 0.00014583 | 9.3104e-05 | 0.14819 | 0.14819 | 0.14819 | 0.99445 | -0.10491 | 0.99285 | -0.13531 | 40.712
28 | -0.10332 | -0.026535 | 0.10334 | 0.026544 | 1.5306e-05 | 9.7738e-06 | 0.15483 | 0.15483 | 0.15483 | 0.99445 | -0.10491 | 0.99461 | -0.10186 | 42.5356
29 | 0.096118 | 0.024673 | -0.096057 | -0.024633 | 6.1614e-05 | 3.9331e-05 | 0.14426 | 0.14426 | 0.14426 | 0.99285 | -0.13531 | 0.99215 | -0.14853 | 39.633
30 | -0.10737 | -0.027556 | 0.10745 | 0.027605 | 7.7774e-05 | 4.9671e-05 | 0.16087 | 0.16087 | 0.16087 | 0.99461 | -0.10186 | 0.9954 | -0.086944 | 44.1939
31 | 0.093546 | 0.024004 | -0.093421 | -0.023924 | 0.00012557 | 8.0144e-05 | 0.1405 | 0.1405 | 0.1405 | 0.99215 | -0.14853 | 0.9907 | -0.17623 | 38.5988
32 | -0.11197 | -0.028737 | 0.11211 | 0.028831 | 0.00014719 | 9.4021e-05 | 0.16762 | 0.16762 | 0.16762 | 0.9954 | -0.086944 | 0.99683 | -0.059894 | 46.0492
33 | 0.090857 | 0.023282 | -0.090803 | -0.023247 | 5.3999e-05 | 3.446e-05 | 0.13665 | 0.13665 | 0.13665 | 0.9907 | -0.17623 | 0.99006 | -0.1885 | 37.5409
34 | -0.11876 | -0.030498 | 0.11882 | 0.030536 | 5.8629e-05 | 3.7458e-05 | 0.17755 | 0.17755 | 0.17755 | 0.99683 | -0.059894 | 0.99737 | -0.049731 | 48.7764
35 | 0.088383 | 0.022641 | -0.088264 | -0.022565 | 0.00011933 | 7.6138e-05 | 0.13301 | 0.13301 | 0.13301 | 0.99006 | -0.1885 | 0.9886 | -0.21641 | 36.5417
36 | -0.12483 | -0.032041 | 0.12493 | 0.032108 | 0.00010516 | 6.7198e-05 | 0.1865 | 0.1865 | 0.1865 | 0.99737 | -0.049731 | 0.99828 | -0.032388 | 51.2375
37 | -0.13688 | -0.035103 | 0.1371 | 0.03524 | 0.00021537 | 0.00013766 | 0.20432 | 0.20432 | 0.20432 | 0.99828 | -0.032388 | 1 | 0 | 56.1307
38 | 0.25015 | 0.064262 | -0.24959 | -0.063902 | 0.00056206 | 0.00035915 | 0.37279 | 0.37279 | 0.37279 | 1 | 0 | 0.99755 | -0.046381 | 51.2074
39 | 0.24241 | 0.062102 | -0.24229 | -0.062028 | 0.00011676 | 7.4601e-05 | 0.36208 | 0.36208 | 0.36208 | 0.99755 | -0.046381 | 0.99702 | -0.056326 | 49.7356
40 | -0.19147 | -0.048446 | 0.19169 | 0.048583 | 0.00021541 | 0.00013751 | 0.2891 | 0.2891 | 0.2891 | 0.98607 | -0.26608 | 0.98728 | -0.24266 | 39.7116
41 | 0.17885 | 0.045283 | -0.17867 | -0.045168 | 0.00017969 | 0.00011467 | 0.27005 | 0.27005 | 0.27005 | 0.98607 | -0.26608 | 0.98499 | -0.28703 | 37.0954
42 | -0.19626 | -0.049729 | 0.19644 | 0.049847 | 0.0001841 | 0.00011753 | 0.29599 | 0.29599 | 0.29599 | 0.98728 | -0.24266 | 0.98829 | -0.22316 | 40.6584
43 | 0.087269 | 0.022109 | -0.087091 | -0.021995 | 0.00017798 | 0.00011356 | 0.13192 | 0.13192 | 0.13192 | 0.98499 | -0.28703 | 0.98279 | -0.32958 | 36.2422
44 | 0.070363 | 0.017783 | -0.070179 | -0.017666 | 0.00018379 | 0.00011707 | 0.10635 | 0.10635 | 0.10635 | 0.98499 | -0.28703 | 0.98218 | -0.34166 | 29.2171
45 | 0.021038 | 0.0052754 | -0.021032 | -0.0052718 | 5.864e-06 | 3.556e-06 | 0.031783 | 0.031783 | 0.031783 | 0.98499 | -0.28703 | 0.98469 | -0.29288 | 8.7316
46 | -0.20195 | -0.051226 | 0.20232 | 0.051462 | 0.00036909 | 0.00023567 | 0.30428 | 0.30428 | 0.30428 | 0.98829 | -0.22316 | 0.99026 | -0.18522 | 41.7965
47 | 0.064712 | 0.016296 | -0.064691 | -0.016283 | 2.0498e-05 | 1.3047e-05 | 0.098067 | 0.098067 | 0.098067 | 0.98218 | -0.34166 | 0.98184 | -0.34829 | 26.9415
48 | 0.017542 | 0.0043972 | -0.017542 | -0.0043972 | 4.53e-08 | 2.6805e-08 | 0.026509 | 0.026509 | 0.026509 | 0.98469 | -0.29288 | 0.98468 | -0.29293 | 7.2828
49 | -0.21583 | -0.05485 | 0.21615 | 0.055053 | 0.00031857 | 0.00020347 | 0.32459 | 0.32459 | 0.32459 | 0.99026 | -0.18522 | 0.99186 | -0.15462 | 44.5863
50 | 0.013517 | 0.0033878 | -0.013515 | -0.0033871 | 1.3023e-06 | 7.2519e-07 | 0.020311 | 0.020311 | 0.020311 | 0.99026 | -0.18522 | 0.99016 | -0.18725 | 5.5798
51 | 0.061878 | 0.015578 | -0.06182 | -0.015541 | 5.7682e-05 | 3.6696e-05 | 0.093803 | 0.093803 | 0.093803 | 0.98184 | -0.34829 | 0.98084 | -0.36781 | 25.7701
52 | 0.015183 | 0.003806 | -0.015181 | -0.0038048 | 2.0098e-06 | 1.1568e-06 | 0.022944 | 0.022945 | 0.022945 | 0.98468 | -0.29293 | 0.98454 | -0.29571 | 6.3034
53 | -0.22347 | -0.056888 | 0.22397 | 0.057204 | 0.00049373 | 0.00031538 | 0.33557 | 0.33557 | 0.33557 | 0.99186 | -0.15462 | 0.99425 | -0.10891 | 46.0954
54 | 0.010806 | 0.002708 | -0.010802 | -0.0027062 | 3.3992e-06 | 1.7335e-06 | 0.016239 | 0.016239 | 0.016239 | 0.99016 | -0.18725 | 0.98982 | -0.19385 | 4.4612
55 | 0.059618 | 0.014989 | -0.059589 | -0.014971 | 2.8824e-05 | 1.8329e-05 | 0.090462 | 0.090462 | 0.090462 | 0.98084 | -0.36781 | 0.98032 | -0.37794 | 24.8522
56 | 0.013063 | 0.0032739 | -0.013063 | -0.0032739 | 3.9991e-10 | 1.9882e-10 | 0.019743 | 0.019743 | 0.019743 | 0.98454 | -0.29571 | 0.98454 | -0.29571 | 5.4239
57 | 0.0039317 | 0.00098433 | -0.003931 | -0.00098456 | 6.5682e-07 | -2.2401e-07 | 0.0059102 | 0.0059104 | 0.0059104 | 0.98982 | -0.19385 | 0.98964 | -0.19736 | 1.6237
58 | 0.003931 | 0.00098456 | -0.003931 | -0.00098457 | 4.6845e-08 | -1.5966e-08 | 0.0059104 | 0.0059104 | 0.0059104 | 0.98964 | -0.19736 | 0.98963 | -0.19761 | 1.6237
59 | 0.003931 | 0.00098457 | -0.0039301 | -0.00098486 | 8.3135e-07 | -2.831e-07 | 0.0059104 | 0.0059107 | 0.0059107 | 0.98963 | -0.19761 | 0.9894 | -0.20205 | 1.6238
60 | 0.003007 | 0.0007535 | -0.0030069 | -0.00075358 | 7.4997e-08 | -7.758e-08 | 0.0045224 | 0.0045224 | 0.0045224 | 0.9894 | -0.20205 | 0.98937 | -0.20258 | 1.2424
61 | -0.23323 | -0.059526 | 0.23383 | 0.059906 | 0.00059418 | 0.0003796 | 0.34944 | 0.34944 | 0.34944 | 0.99425 | -0.10891 | 0.99702 | -0.056326 | 47.9999
62 | 0.0092643 | 0.0023222 | -0.0092629 | -0.0023215 | 1.4318e-06 | 6.5881e-07 | 0.013865 | 0.013865 | 0.013865 | 0.99425 | -0.10891 | 0.99409 | -0.11215 | 3.8092
63 | 0.0021037 | 0.0005272 | -0.0021037 | -0.00052723 | 1.0868e-08 | -3.0223e-08 | 0.0031639 | 0.0031639 | 0.0031639 | 0.98937 | -0.20258 | 0.98937 | -0.20269 | 0.86921
64 | -0.0051118 | -0.0012811 | 0.0051118 | 0.0012811 | 3.6192e-08 | 3.3585e-09 | 0.0077987 | 0.0077987 | 0.0077987 | 0.97534 | -0.47549 | 0.97535 | -0.47534 | 2.1425
65 | 0.0082715 | 0.002073 | -0.0082713 | -0.002073 | 1.643e-07 | 6.8101e-08 | 0.012381 | 0.012381 | 0.012381 | 0.99409 | -0.11215 | 0.99407 | -0.11257 | 3.4015
66 | 0.07078 | 0.017894 | -0.070724 | -0.017859 | 5.5916e-05 | 3.5625e-05 | 0.10768 | 0.10768 | 0.10768 | 0.97863 | -0.40896 | 0.97779 | -0.42545 | 29.5818
67 | -0.073004 | -0.018451 | 0.073104 | 0.018515 | 9.9857e-05 | 6.3637e-05 | 0.11106 | 0.11106 | 0.11106 | 0.97863 | -0.40896 | 0.98009 | -0.38048 | 30.5107
68 | 0.068734 | 0.01736 | -0.068687 | -0.01733 | 4.6841e-05 | 2.9835e-05 | 0.10465 | 0.10465 | 0.10465 | 0.97779 | -0.42545 | 0.97706 | -0.43968 | 28.7494
69 | -0.075741 | -0.019176 | 0.075771 | 0.019195 | 2.9897e-05 | 1.9058e-05 | 0.11506 | 0.11506 | 0.11506 | 0.98009 | -0.38048 | 0.98052 | -0.37226 | 31.6104
70 | 0.066723 | 0.016838 | -0.066672 | -0.016805 | 5.0757e-05 | 3.232e-05 | 0.10166 | 0.10166 | 0.10166 | 0.97706 | -0.43968 | 0.97625 | -0.45558 | 27.9279
71 | -0.077923 | -0.019734 | 0.077964 | 0.019761 | 4.1212e-05 | 2.6277e-05 | 0.11833 | 0.11833 | 0.11833 | 0.98052 | -0.37226 | 0.98108 | -0.36125 | 32.5078
72 | 0.065017 | 0.01639 | -0.064971 | -0.016361 | 4.5978e-05 | 2.927e-05 | 0.099134 | 0.099134 | 0.099134 | 0.97625 | -0.45558 | 0.9755 | -0.47037 | 27.2347
73 | -0.080254 | -0.020335 | 0.080433 | 0.020449 | 0.00017912 | 0.00011423 | 0.1218 | 0.1218 | 0.1218 | 0.98108 | -0.36125 | 0.98347 | -0.31491 | 33.4618
74 | 0.062479 | 0.015736 | -0.062444 | -0.015715 | 3.4093e-05 | 2.1695e-05 | 0.095333 | 0.095333 | 0.095333 | 0.9755 | -0.47037 | 0.97491 | -0.48179 | 26.1903
75 | -0.08218 | -0.020887 | 0.082289 | 0.020956 | 0.00010958 | 6.9892e-05 | 0.12444 | 0.12444 | 0.12444 | 0.98347 | -0.31491 | 0.98491 | -0.28726 | 34.1879
76 | -0.082289 | -0.020956 | 0.08242 | 0.02104 | 0.00013086 | 8.3466e-05 | 0.12444 | 0.12444 | 0.12444 | 0.98491 | -0.28726 | 0.98662 | -0.25434 | 34.1878
77 | -0.083977 | -0.02143 | 0.084082 | 0.021497 | 0.00010564 | 6.7388e-05 | 0.12679 | 0.12679 | 0.12679 | 0.98662 | -0.25434 | 0.98797 | -0.22834 | 34.8327
78 | -0.085751 | -0.021916 | 0.0858 | 0.021947 | 4.9513e-05 | 3.1587e-05 | 0.1293 | 0.1293 | 0.1293 | 0.98797 | -0.22834 | 0.9886 | -0.21641 | 35.523
79 | 0.05887 | 0.014819 | -0.05882 | -0.014788 | 4.9256e-05 | 3.1322e-05 | 0.089876 | 0.089877 | 0.089877 | 0.97491 | -0.48179 | 0.97402 | -0.49931 | 24.6914
80 | 0.054019 | 0.013584 | -0.053982 | -0.01356 | 3.7323e-05 | 2.3705e-05 | 0.082541 | 0.082541 | 0.082541 | 0.97402 | -0.49931 | 0.97329 | -0.51378 | 22.6762
81 | -0.003311 | -0.00082982 | 0.0033114 | 0.00082957 | 3.7921e-07 | -2.44e-07 | 0.005072 | 0.0050718 | 0.005072 | 0.97138 | -0.55142 | 0.9715 | -0.54901 | 1.3934
82 | -0.005498 | -0.0013776 | 0.0054988 | 0.0013777 | 7.5856e-07 | 1.3221e-07 | 0.0084209 | 0.0084208 | 0.0084209 | 0.9715 | -0.54901 | 0.97165 | -0.54612 | 2.3134
83 | -0.020933 | -0.0052466 | 0.020935 | 0.005248 | 2.1578e-06 | 1.3116e-06 | 0.032058 | 0.032058 | 0.032058 | 0.97165 | -0.54612 | 0.97176 | -0.54395 | 8.8071
84 | 0.015434 | 0.0038689 | -0.01543 | -0.0038664 | 4.3902e-06 | 2.5503e-06 | 0.023637 | 0.023637 | 0.023637 | 0.97165 | -0.54612 | 0.97135 | -0.55209 | 6.4937
85 | -0.043594 | -0.010932 | 0.043642 | 0.010962 | 4.7189e-05 | 2.9851e-05 | 0.066757 | 0.066756 | 0.066757 | 0.97176 | -0.54395 | 0.97291 | -0.52127 | 18.3397
86 | 0.022659 | 0.0056845 | -0.022645 | -0.005676 | 1.3822e-05 | 8.467e-06 | 0.034699 | 0.034699 | 0.034699 | 0.97176 | -0.54395 | 0.97111 | -0.55676 | 9.5327
87 | 0.01326 | 0.0033224 | -0.013258 | -0.0033215 | 1.6937e-06 | 9.4851e-07 | 0.020312 | 0.020312 | 0.020312 | 0.97135 | -0.55209 | 0.97121 | -0.55477 | 5.5803
88 | -0.048812 | -0.012258 | 0.04883 | 0.012269 | 1.7438e-05 | 1.1057e-05 | 0.074665 | 0.074665 | 0.074665 | 0.97291 | -0.52127 | 0.97329 | -0.51378 | 20.5123
89 | 0.021758 | 0.0054538 | -0.021758 | -0.0054535 | 4.8093e-07 | 2.9352e-07 | 0.03334 | 0.03334 | 0.03334 | 0.97111 | -0.55676 | 0.97109 | -0.55722 | 9.1594
90 | 0.0063867 | 0.0015993 | -0.0063858 | -0.001599 | 9.7228e-07 | 2.872e-07 | 0.0097847 | 0.0097849 | 0.0097849 | 0.97121 | -0.55477 | 0.97105 | -0.55797 | 2.6881
91 | 0.0068712 | 0.0017221 | -0.0068706 | -0.0017219 | 5.7049e-07 | 1.9526e-07 | 0.010528 | 0.010528 | 0.010528 | 0.97121 | -0.55477 | 0.97113 | -0.55651 | 2.8922
92 | 0.011403 | 0.0028583 | -0.011403 | -0.0028581 | 2.6211e-07 | 1.3943e-07 | 0.017473 | 0.017473 | 0.017473 | 0.97109 | -0.55722 | 0.97107 | -0.5577 | 4.8002
93 | 0.0054239 | 0.001358 | -0.0054238 | -0.001358 | 3.0962e-08 | 5.0282e-09 | 0.0083109 | 0.0083109 | 0.0083109 | 0.97105 | -0.55797 | 0.97105 | -0.55809 | 2.2832
94 | 0.0025074 | 0.0006284 | -0.0025074 | -0.00062841 | 5.178e-09 | -8.26e-09 | 0.003842 | 0.003842 | 0.003842 | 0.97113 | -0.55651 | 0.97112 | -0.55656 | 1.0555
95 | 0.010532 | 0.0026398 | -0.01053 | -0.0026391 | 1.4299e-06 | 7.3404e-07 | 0.016138 | 0.016138 | 0.016138 | 0.97107 | -0.5577 | 0.97092 | -0.56055 | 4.4336
96 | -0.025143 | -0.0063034 | 0.025165 | 0.0063166 | 2.1383e-05 | 1.3195e-05 | 0.038245 | 0.038245 | 0.038245 | 0.97828 | -0.41796 | 0.97919 | -0.40012 | 10.5069
97 | 0.012168 | 0.0030501 | -0.012165 | -0.0030486 | 2.8389e-06 | 1.5397e-06 | 0.018513 | 0.018513 | 0.018513 | 0.97806 | -0.42236 | 0.97781 | -0.42726 | 5.086
98 | -0.027003 | -0.0067773 | 0.027004 | 0.0067777 | 5.721e-07 | 3.5475e-07 | 0.041038 | 0.041038 | 0.041038 | 0.97919 | -0.40012 | 0.97921 | -0.39968 | 11.2743
99 | 0.011227 | 0.0028134 | -0.011224 | -0.002812 | 2.6564e-06 | 1.3958e-06 | 0.017085 | 0.017085 | 0.017085 | 0.97781 | -0.42726 | 0.97755 | -0.43223 | 4.6937
100 | 0.0014705 | 0.00036848 | -0.0014705 | -0.00036855 | 1.1442e-08 | -6.9293e-08 | 0.0022364 | 0.0022364 | 0.0022364 | 0.97843 | -0.41506 | 0.97842 | -0.41523 | 0.61441
101 | -0.0030118 | -0.00075476 | 0.0030118 | 0.00075475 | 2.7903e-09 | -2.6677e-09 | 0.0045804 | 0.0045804 | 0.0045804 | 0.97843 | -0.41506 | 0.97843 | -0.41504 | 1.2583
102 | -0.014417 | -0.0036139 | 0.014419 | 0.0036154 | 2.7218e-06 | 1.5523e-06 | 0.021925 | 0.021925 | 0.021925 | 0.97843 | -0.41504 | 0.97863 | -0.41108 | 6.0235
103 | 0.011405 | 0.0028591 | -0.011403 | -0.0028582 | 1.6852e-06 | 8.9095e-07 | 0.017345 | 0.017345 | 0.017345 | 0.97843 | -0.41504 | 0.97827 | -0.41815 | 4.7651
104 | -0.015721 | -0.0039416 | 0.015721 | 0.0039419 | 4.6939e-07 | 2.7288e-07 | 0.023904 | 0.023904 | 0.023904 | 0.97863 | -0.41108 | 0.97866 | -0.41046 | 6.5671
105 | 0.0093115 | 0.002334 | -0.00931 | -0.0023333 | 1.539e-06 | 7.2816e-07 | 0.014164 | 0.014164 | 0.014164 | 0.97827 | -0.41815 | 0.97809 | -0.42162 | 3.8911
106 | -0.017848 | -0.0044748 | 0.017849 | 0.0044757 | 1.5513e-06 | 9.2223e-07 | 0.027137 | 0.027137 | 0.027137 | 0.97866 | -0.41046 | 0.97876 | -0.40863 | 7.4553
107 | 0.00737 | 0.0018471 | -0.0073695 | -0.0018469 | 4.2981e-07 | 1.6066e-07 | 0.011212 | 0.011212 | 0.011212 | 0.97809 | -0.42162 | 0.97803 | -0.42284 | 3.0803
108 | -0.019199 | -0.004814 | 0.019203 | 0.0048164 | 3.9839e-06 | 2.3929e-06 | 0.029189 | 0.029189 | 0.029189 | 0.97876 | -0.40863 | 0.97898 | -0.40428 | 8.019
109 | 0.003979 | 0.00099716 | -0.0039788 | -0.00099719 | 1.2196e-07 | -3.3308e-08 | 0.0060537 | 0.0060538 | 0.0060538 | 0.97803 | -0.42284 | 0.978 | -0.42348 | 1.6631
110 | 0.010665 | 0.0026717 | -0.010664 | -0.0026715 | 5.1659e-07 | 2.6508e-07 | 0.016233 | 0.016233 | 0.016233 | 0.97755 | -0.43223 | 0.9775 | -0.43324 | 4.4596
111 | 0.008544 | 0.0021401 | -0.0085427 | -0.0021396 | 1.2505e-06 | 5.5321e-07 | 0.013006 | 0.013006 | 0.013006 | 0.9775 | -0.43324 | 0.97735 | -0.43632 | 3.573
112 | 0.0022863 | 0.00057157 | -0.0022861 | -0.00057191 | 1.6245e-07 | -3.4415e-07 | 0.0034803 | 0.0034805 | 0.0034805 | 0.97735 | -0.43632 | 0.97727 | -0.43781 | 0.95618
113 | 0.0022861 | 0.00057191 | -0.0022858 | -0.00057253 | 2.9463e-07 | -6.2391e-07 | 0.0034805 | 0.0034808 | 0.0034808 | 0.97727 | -0.43781 | 0.97713 | -0.44052 | 0.95626
114 | -0.0012912 | -0.00032352 | 0.0012912 | 0.00032333 | 2.3864e-08 | -1.9233e-07 | 0.0019629 | 0.0019628 | 0.0019629 | 0.97879 | -0.40786 | 0.97881 | -0.40747 | 0.53925
115 | 0.00067752 | 0.00016973 | -0.00067752 | -0.0001698 | 2.3642e-09 | -7.3179e-08 | 0.00103 | 0.00103 | 0.00103 | 0.97879 | -0.40786 | 0.97879 | -0.40793 | 0.28297
116 | -0.0027741 | -0.00069499 | 0.0027742 | 0.00069495 | 3.7052e-08 | -4.6118e-08 | 0.0042172 | 0.0042172 | 0.0042172 | 0.97881 | -0.40747 | 0.97883 | -0.40719 | 1.1586
117 | -0.0041317 | -0.0010352 | 0.0041317 | 0.0010352 | 3.824e-08 | -8.0186e-09 | 0.0062808 | 0.0062808 | 0.0062808 | 0.97883 | -0.40719 | 0.97884 | -0.40699 | 1.7255
118 | -0.005618 | -0.0014077 | 0.0056187 | 0.0014078 | 7.2611e-07 | 1.3096e-07 | 0.0085403 | 0.0085402 | 0.0085403 | 0.97884 | -0.40699 | 0.97898 | -0.40428 | 2.3462
119 | -0.024822 | -0.0062242 | 0.02483 | 0.0062292 | 8.1946e-06 | 5.0514e-06 | 0.037729 | 0.037729 | 0.037729 | 0.97898 | -0.40428 | 0.97933 | -0.39735 | 10.3652
120 | 0.0022858 | 0.00057253 | -0.0022857 | -0.00057284 | 1.4478e-07 | -3.0646e-07 | 0.0034808 | 0.0034809 | 0.0034809 | 0.97713 | -0.44052 | 0.97707 | -0.44185 | 0.9563
121 | 0.028827 | 0.0072359 | -0.028824 | -0.0072339 | 3.1965e-06 | 1.9899e-06 | 0.043805 | 0.043805 | 0.043805 | 0.97933 | -0.39735 | 0.97921 | -0.39968 | 12.0342
122 | -0.053657 | -0.013465 | 0.053702 | 0.013494 | 4.4862e-05 | 2.8485e-05 | 0.081534 | 0.081534 | 0.081534 | 0.97933 | -0.39735 | 0.98022 | -0.37984 | 22.3994
123 | -0.055854 | -0.014033 | 0.055859 | 0.014036 | 5.0686e-06 | 3.2202e-06 | 0.0848 | 0.0848 | 0.0848 | 0.98022 | -0.37984 | 0.98032 | -0.37794 | 23.2968
124 | 0.0018061 | 0.00045126 | -0.0018058 | -0.00045215 | 2.4092e-07 | -8.8351e-07 | 0.0027671 | 0.0027674 | 0.0027674 | 0.97105 | -0.55809 | 0.97091 | -0.56089 | 0.76029
125 | 0.0015691 | 0.00039283 | -0.0015691 | -0.00039325 | 8.169e-08 | -4.1353e-07 | 0.0024047 | 0.0024049 | 0.0024049 | 0.97091 | -0.56089 | 0.97085 | -0.56198 | 0.66069
126 | 0.0084401 | 0.0021153 | -0.0084395 | -0.0021151 | 5.8796e-07 | 2.5377e-07 | 0.012756 | 0.012756 | 0.012756 | 0.98454 | -0.29571 | 0.98447 | -0.29717 | 3.5044
127 | 0.0063013 | 0.0015792 | -0.0063012 | -0.0015792 | 2.4339e-08 | 6.4796e-09 | 0.0095243 | 0.0095243 | 0.0095243 | 0.98447 | -0.29717 | 0.98446 | -0.29726 | 2.6166
128 | 0.0033171 | 0.00083126 | -0.003317 | -0.00083132 | 7.6026e-08 | -5.3886e-08 | 0.0050137 | 0.0050138 | 0.0050138 | 0.98446 | -0.29726 | 0.98444 | -0.29774 | 1.3774

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3972 | 0.10158

## res_load
| p_mw | q_mvar
0 | 0.0041632 | 0.0010434
1 | 0.0037024 | 0.00092792
2 | 0.0041607 | 0.0010428
3 | 0.0031677 | 0.0007939
4 | 0.0070032 | 0.0017552
5 | 0.0073379 | 0.001839
6 | 0.0050281 | 0.0012602
7 | 0.012549 | 0.0031451
8 | 0.0068823 | 0.0017249
9 | 0.0045536 | 0.0011412
10 | 0.0021774 | 0.00054572
11 | 0.0017061 | 0.00042758
12 | 0.0015476 | 0.00038786
13 | 0.0023124 | 0.00057954
14 | 0.0020231 | 0.00050704
15 | 0.0037753 | 0.00094619
16 | 0.0016243 | 0.0004071
17 | 0.0013816 | 0.00034626
18 | 0.0015018 | 0.00037638
19 | 0.0044362 | 0.0011118
20 | 0.0026206 | 0.00065679
21 | 0.0040349 | 0.0010112
22 | 0.0025103 | 0.00062913
23 | 0.0045176 | 0.0011322
24 | 0.0025639 | 0.00064257
25 | 0.0066502 | 0.0016667
26 | 0.00242 | 0.00060651
27 | 0.0060046 | 0.0015049
28 | 0.01195 | 0.0029948
29 | 0.0083003 | 0.0020803
30 | 0.007183 | 0.0018002
31 | 0.012622 | 0.0031633
32 | 0.0045733 | 0.0011462
33 | 0.0055027 | 0.0013791
34 | 0.0075926 | 0.0019029
35 | 0.0054675 | 0.0013703
36 | 0.0034896 | 0.00087458
37 | 0.0028136 | 0.00070514
38 | 0.0023591 | 0.00059125
39 | 0.007323 | 0.0018353
40 | 0.0027097 | 0.00067911
41 | 0.0022023 | 0.00055194
42 | 0.0021183 | 0.00053091
43 | 0.0068705 | 0.0017219
44 | 0.00092313 | 0.00023136
45 | 0.00090326 | 0.00022638
46 | 0.0084668 | 0.002122
47 | 0.0051118 | 0.0012811
48 | 0.0071078 | 0.0017814
49 | 0.00099145 | 0.00024848
50 | 0.0082713 | 0.002073
51 | 0.0022237 | 0.00055731
52 | 0.0019909 | 0.00049897
53 | 0.0026367 | 0.00066083
54 | 0.0019635 | 0.00049211
55 | 0.0021525 | 0.00053947
56 | 0.0016554 | 0.00041489
57 | 0.0022894 | 0.00057378
58 | 0.0024924 | 0.00062467
59 | 0.0017469 | 0.00043782
60 | 0.0015564 | 0.00039008
61 | 0.0016684 | 0.00041813
62 | 0.0035747 | 0.00089591
63 | 0.0048015 | 0.0012034
64 | 0.003311 | 0.00082982
65 | 0.0021866 | 0.00054802
66 | 0.0021704 | 0.00054396
67 | 0.0051707 | 0.0012959
68 | 0.00088672 | 0.00022223
69 | 0.0051519 | 0.0012912
70 | 0.010355 | 0.0025953
71 | 0.00096188 | 0.00024107
72 | 0.0043632 | 0.0010935
73 | 0.0021037 | 0.00052723
74 | 0.0024636 | 0.00061743
75 | 0.00087096 | 0.00021828
76 | 0.01053 | 0.0026391
77 | 0.0025693 | 0.00064392
78 | 0.00063244 | 0.00015851
79 | 0.0018383 | 0.00046071
80 | 0.0009384 | 0.00023518
81 | 0.0015413 | 0.00038628
82 | 0.0014705 | 0.00036855
83 | 0.0013014 | 0.00032615
84 | 0.0020917 | 0.00052422
85 | 0.0021265 | 0.00053295
86 | 0.00194 | 0.00048621
87 | 0.0013496 | 0.00033825
88 | 0.0033906 | 0.00084976
89 | 0.00055967 | 0.00014027
90 | 0.0021201 | 0.00053134
91 | 0.0062565 | 0.001568
92 | 0.00061365 | 0.0001538
93 | 0.0014829 | 0.00037166
94 | 0.00067752 | 0.0001698
95 | 0.0013575 | 0.00034022
96 | 0.0014863 | 0.00037251
97 | 0.0022857 | 0.00057284
98 | 0.0018203 | 0.00045621
99 | 0.0021518 | 0.00053929
100 | 0.0037301 | 0.00093485
101 | 0.0039788 | 0.00099719
102 | 0.0025074 | 0.00062841
103 | 0.0036178 | 0.0009067
104 | 0.00023667 | 5.9314e-05
105 | 0.0015691 | 0.00039325
106 | 0.0046228 | 0.0011586
107 | 0.0021382 | 0.00053589
108 | 0.0029842 | 0.0007479
109 | 0.003317 | 0.00083132

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1