## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_198-67_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_198-67_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_198-67_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_198-67_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_198-67_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_198-67_0_6_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_198-67_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_198-67_0_6_node_107 | 0.4 | n |  | TRUE
8 | bus_LV_198-67_0_6_node_48 | 0.4 | n |  | TRUE
9 | bus_LV_198-67_0_6_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_198-67_0_6_node_105 | 0.4 | n |  | TRUE
11 | bus_LV_198-67_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_198-67_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_198-67_0_6_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_198-67_0_6_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_198-67_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_198-67_0_6_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_198-67_0_6_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_198-67_0_6_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_198-67_0_6_node_89 | 0.4 | n |  | TRUE
20 | bus_LV_198-67_0_6_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_198-67_0_6_node_87 | 0.4 | n |  | TRUE
22 | bus_LV_198-67_0_6_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_198-67_0_6_node_80 | 0.4 | n |  | TRUE
24 | bus_LV_198-67_0_6_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_198-67_0_6_node_64 | 0.4 | n |  | TRUE
26 | bus_LV_198-67_0_6_node_65 | 0.4 | n |  | TRUE
27 | bus_LV_198-67_0_6_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_198-67_0_6_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_198-67_0_6_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_198-67_0_6_node_108 | 0.4 | n |  | TRUE
31 | bus_LV_198-67_0_6_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_198-67_0_6_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_198-67_0_6_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_198-67_0_6_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_198-67_0_6_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_198-67_0_6_node_77 | 0.4 | n |  | TRUE
37 | bus_LV_198-67_0_6_node_113 | 0.4 | n |  | TRUE
38 | bus_LV_198-67_0_6_node_121 | 0.4 | n |  | TRUE
39 | bus_LV_198-67_0_6_node_112 | 0.4 | n |  | TRUE
40 | bus_LV_198-67_0_6_node_76 | 0.4 | n |  | TRUE
41 | bus_LV_198-67_0_6_node_138 | 0.4 | n |  | TRUE
42 | bus_LV_198-67_0_6_node_74 | 0.4 | n |  | TRUE
43 | bus_LV_198-67_0_6_node_73 | 0.4 | n |  | TRUE
44 | bus_LV_198-67_0_6_node_123 | 0.4 | n |  | TRUE
45 | bus_LV_198-67_0_6_node_122 | 0.4 | n |  | TRUE
46 | bus_LV_198-67_0_6_node_15 | 0.4 | n |  | TRUE
47 | bus_LV_198-67_0_6_node_16 | 0.4 | n |  | TRUE
48 | bus_LV_198-67_0_6_node_17 | 0.4 | n |  | TRUE
49 | bus_LV_198-67_0_6_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_198-67_0_6_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_198-67_0_6_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_198-67_0_6_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_198-67_0_6_node_88 | 0.4 | n |  | TRUE
54 | bus_LV_198-67_0_6_node_66 | 0.4 | n |  | TRUE
55 | bus_LV_198-67_0_6_node_75 | 0.4 | n |  | TRUE
56 | bus_LV_198-67_0_6_node_97 | 0.4 | n |  | TRUE
57 | bus_LV_198-67_0_6_node_78 | 0.4 | n |  | TRUE
58 | bus_LV_198-67_0_6_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_198-67_0_6_node_109 | 0.4 | n |  | TRUE
60 | bus_LV_198-67_0_6_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_198-67_0_6_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_198-67_0_6_node_91 | 0.4 | n |  | TRUE
63 | bus_LV_198-67_0_6_node_120 | 0.4 | n |  | TRUE
64 | bus_LV_198-67_0_6_node_126 | 0.4 | n |  | TRUE
65 | bus_LV_198-67_0_6_node_111 | 0.4 | n |  | TRUE
66 | bus_LV_198-67_0_6_node_125 | 0.4 | n |  | TRUE
67 | bus_LV_198-67_0_6_node_32 | 0.4 | n |  | TRUE
68 | bus_LV_198-67_0_6_node_29 | 0.4 | n |  | TRUE
69 | bus_LV_198-67_0_6_node_30 | 0.4 | n |  | TRUE
70 | bus_LV_198-67_0_6_node_31 | 0.4 | n |  | TRUE
71 | bus_LV_198-67_0_6_node_33 | 0.4 | n |  | TRUE
72 | bus_LV_198-67_0_6_node_34 | 0.4 | n |  | TRUE
73 | bus_LV_198-67_0_6_node_36 | 0.4 | n |  | TRUE
74 | bus_LV_198-67_0_6_node_81 | 0.4 | n |  | TRUE
75 | bus_LV_198-67_0_6_node_37 | 0.4 | n |  | TRUE
76 | bus_LV_198-67_0_6_node_40 | 0.4 | n |  | TRUE
77 | bus_LV_198-67_0_6_node_45 | 0.4 | n |  | TRUE
78 | bus_LV_198-67_0_6_node_38 | 0.4 | n |  | TRUE
79 | bus_LV_198-67_0_6_node_39 | 0.4 | n |  | TRUE
80 | bus_LV_198-67_0_6_node_41 | 0.4 | n |  | TRUE
81 | bus_LV_198-67_0_6_node_44 | 0.4 | n |  | TRUE
82 | bus_LV_198-67_0_6_node_42 | 0.4 | n |  | TRUE
83 | bus_LV_198-67_0_6_node_132 | 0.4 | n |  | TRUE
84 | bus_LV_198-67_0_6_node_43 | 0.4 | n |  | TRUE
85 | bus_LV_198-67_0_6_node_133 | 0.4 | n |  | TRUE
86 | bus_LV_198-67_0_6_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_198-67_0_6_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_198-67_0_6_node_139 | 0.4 | n |  | TRUE
89 | bus_LV_198-67_0_6_node_92 | 0.4 | n |  | TRUE
90 | bus_LV_198-67_0_6_node_117 | 0.4 | n |  | TRUE
91 | bus_LV_198-67_0_6_node_49 | 0.4 | n |  | TRUE
92 | bus_LV_198-67_0_6_node_100 | 0.4 | n |  | TRUE
93 | bus_LV_198-67_0_6_node_118 | 0.4 | n |  | TRUE
94 | bus_LV_198-67_0_6_node_99 | 0.4 | n |  | TRUE
95 | bus_LV_198-67_0_6_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_198-67_0_6_node_59 | 0.4 | n |  | TRUE
97 | bus_LV_198-67_0_6_node_61 | 0.4 | n |  | TRUE
98 | bus_LV_198-67_0_6_node_62 | 0.4 | n |  | TRUE
99 | bus_LV_198-67_0_6_node_98 | 0.4 | n |  | TRUE
100 | bus_LV_198-67_0_6_node_134 | 0.4 | n |  | TRUE
101 | bus_LV_198-67_0_6_node_135 | 0.4 | n |  | TRUE
102 | bus_LV_198-67_0_6_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_198-67_0_6_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_198-67_0_6_node_68 | 0.4 | n |  | TRUE
105 | bus_LV_198-67_0_6_node_69 | 0.4 | n |  | TRUE
106 | bus_LV_198-67_0_6_node_70 | 0.4 | n |  | TRUE
107 | bus_LV_198-67_0_6_node_71 | 0.4 | n |  | TRUE
108 | bus_LV_198-67_0_6_node_72 | 0.4 | n |  | TRUE
109 | bus_LV_198-67_0_6_node_86 | 0.4 | n |  | TRUE
110 | bus_LV_198-67_0_6_node_84 | 0.4 | n |  | TRUE
111 | bus_LV_198-67_0_6_node_85 | 0.4 | n |  | TRUE
112 | bus_LV_198-67_0_6_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_198-67_0_6_node_90 | 0.4 | n |  | TRUE
114 | bus_LV_198-67_0_6_node_82 | 0.4 | n |  | TRUE
115 | bus_LV_198-67_0_6_node_137 | 0.4 | n |  | TRUE
116 | bus_LV_198-67_0_6_node_94 | 0.4 | n |  | TRUE
117 | bus_LV_198-67_0_6_node_136 | 0.4 | n |  | TRUE
118 | bus_LV_198-67_0_6_node_101 | 0.4 | n |  | TRUE
119 | bus_LV_198-67_0_6_node_102 | 0.4 | n |  | TRUE
120 | bus_LV_198-67_0_6_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_198-67_0_6_node_115 | 0.4 | n |  | TRUE
122 | bus_LV_198-67_0_6_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_198-67_0_6_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_198-67_0_6_node_104 | 0.4 | n |  | TRUE
125 | bus_LV_198-67_0_6_node_106 | 0.4 | n |  | TRUE
126 | bus_LV_198-67_0_6_node_131 | 0.4 | n |  | TRUE
127 | bus_LV_198-67_0_6_node_130 | 0.4 | n |  | TRUE
128 | bus_LV_198-67_0_6_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_198-67_0_6_node_124 | 0.4 | n |  | TRUE
130 | bus_LV_198-67_0_6_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_198-67_0_6_node_127 | 0.4 | n |  | TRUE
132 | bus_LV_198-67_0_6_node_128 | 0.4 | n |  | TRUE
133 | bus_LV_198-67_0_6_node_129 | 0.4 | n |  | TRUE
134 | bus_MV_501_0_node_149 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_198-67_0_6_load_0 | 0 | 0.0047872 | 0.0011998 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_198-67_0_6_load_1 | 1 | 0.0083344 | 0.0020888 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_198-67_0_6_load_2 | 2 | 0.0025373 | 0.0006359 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_198-67_0_6_load_3 | 3 | 0.0053088 | 0.0013305 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_198-67_0_6_load_5 | 4 | 0.021758 | 0.0054532 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_198-67_0_6_load_6 | 6 | 0.0034169 | 0.00085636 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_198-67_0_6_load_107 | 7 | 0.0039828 | 0.00099818 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_198-67_0_6_load_48 | 8 | 0.0014898 | 0.00037337 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_198-67_0_6_load_105 | 10 | 0.0017416 | 0.00043648 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_198-67_0_6_load_7 | 11 | 0.0045817 | 0.0011483 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_198-67_0_6_load_8 | 12 | 0.0046136 | 0.0011563 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_198-67_0_6_load_10 | 13 | 0.001385 | 0.0003471 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_198-67_0_6_load_14 | 14 | 0.0034779 | 0.00087165 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_198-67_0_6_load_18 | 17 | 0.019876 | 0.0049813 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_198-67_0_6_load_89 | 19 | 0.0010802 | 0.00027073 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_198-67_0_6_load_87 | 21 | 0.0018505 | 0.00046377 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_198-67_0_6_load_80 | 23 | 0.0021208 | 0.00053153 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_198-67_0_6_load_64 | 25 | 0.0022673 | 0.00056824 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_198-67_0_6_load_63 | 27 | 0.01338 | 0.0033533 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_198-67_0_6_load_108 | 30 | 0.0076602 | 0.0019198 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_198-67_0_6_load_54 | 33 | 0.0051079 | 0.0012801 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_198-67_0_6_load_51 | 34 | 0.0033424 | 0.00083768 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_198-67_0_6_load_77 | 36 | 0.0011572 | 0.00029002 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_198-67_0_6_load_113 | 37 | 0.009187 | 0.0023025 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_198-67_0_6_load_121 | 38 | 0.0018333 | 0.00045948 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_198-67_0_6_load_112 | 39 | 0.0032453 | 0.00081336 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_198-67_0_6_load_138 | 41 | 0.0019078 | 0.00047814 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_198-67_0_6_load_74 | 42 | 0.018939 | 0.0047466 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_198-67_0_6_load_73 | 43 | 0.013363 | 0.003349 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_198-67_0_6_load_123 | 44 | 0.015306 | 0.0038361 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_198-67_0_6_load_122 | 45 | 0.0026333 | 0.00065997 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_198-67_0_6_load_15 | 46 | 0.0060456 | 0.0015152 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_198-67_0_6_load_16 | 47 | 0.00073367 | 0.00018388 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_198-67_0_6_load_17 | 48 | 0.0035353 | 0.00088602 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_198-67_0_6_load_46 | 50 | 0.0019729 | 0.00049445 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_198-67_0_6_load_35 | 51 | 0.0008751 | 0.00021932 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_198-67_0_6_load_58 | 52 | 0.00066558 | 0.00016681 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_198-67_0_6_load_75 | 55 | 0.0024301 | 0.00060905 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_198-67_0_6_load_97 | 56 | 0.0056253 | 0.0014098 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_198-67_0_6_load_95 | 58 | 0.0084753 | 0.0021241 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_198-67_0_6_load_55 | 60 | 0.004648 | 0.0011649 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_198-67_0_6_load_52 | 61 | 0.0035519 | 0.00089019 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_198-67_0_6_load_120 | 63 | 0.0041955 | 0.0010515 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_198-67_0_6_load_111 | 65 | 0.010207 | 0.002558 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_198-67_0_6_load_29 | 68 | 0.00064136 | 0.00016074 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_198-67_0_6_load_30 | 69 | 0.00076082 | 0.00019068 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_198-67_0_6_load_31 | 70 | 0.0038976 | 0.00097684 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_198-67_0_6_load_33 | 71 | 0.0047974 | 0.0012023 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_198-67_0_6_load_34 | 72 | 0.00098544 | 0.00024697 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_198-67_0_6_load_36 | 73 | 0.00083296 | 0.00020876 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_198-67_0_6_load_81 | 74 | 0.0012143 | 0.00030433 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_198-67_0_6_load_37 | 75 | 0.003197 | 0.00080124 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_198-67_0_6_load_45 | 77 | 0.0045561 | 0.0011419 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_198-67_0_6_load_38 | 78 | 0.0027259 | 0.00068319 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_198-67_0_6_load_41 | 80 | 0.016294 | 0.0040837 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_198-67_0_6_load_132 | 83 | 0.0033518 | 0.00084004 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_198-67_0_6_load_67 | 86 | 0.0040285 | 0.0010096 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_198-67_0_6_load_56 | 87 | 0.0040601 | 0.0010175 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_198-67_0_6_load_139 | 88 | 0.020221 | 0.0050678 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_198-67_0_6_load_92 | 89 | 0.0027155 | 0.00068056 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_198-67_0_6_load_117 | 90 | 0.0029083 | 0.00072889 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_198-67_0_6_load_100 | 92 | 0.0045147 | 0.0011315 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_198-67_0_6_load_118 | 93 | 0.0026551 | 0.00066542 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_198-67_0_6_load_99 | 94 | 0.0082859 | 0.0020766 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_198-67_0_6_load_57 | 95 | 0.0068442 | 0.0017153 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_198-67_0_6_load_61 | 97 | 0.0017854 | 0.00044745 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_198-67_0_6_load_62 | 98 | 0.0014728 | 0.00036911 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_198-67_0_6_load_98 | 99 | 0.0015938 | 0.00039946 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_198-67_0_6_load_134 | 100 | 0.0016075 | 0.00040287 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_198-67_0_6_load_135 | 101 | 0.0016455 | 0.0004124 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_198-67_0_6_load_96 | 102 | 0.0067598 | 0.0016942 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_198-67_0_6_load_93 | 103 | 0.0046489 | 0.0011651 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_198-67_0_6_load_68 | 104 | 0.001538 | 0.00038547 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_198-67_0_6_load_69 | 105 | 0.0032754 | 0.00082089 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_198-67_0_6_load_70 | 106 | 0.0011694 | 0.00029307 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_198-67_0_6_load_71 | 107 | 0.0019784 | 0.00049584 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_198-67_0_6_load_72 | 108 | 0.0014097 | 0.0003533 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_198-67_0_6_load_86 | 109 | 0.0015774 | 0.00039533 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_198-67_0_6_load_84 | 110 | 0.0021879 | 0.00054834 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_198-67_0_6_load_85 | 111 | 0.0039557 | 0.00099139 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_198-67_0_6_load_83 | 112 | 0.0057538 | 0.001442 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_198-67_0_6_load_90 | 113 | 0.033242 | 0.0083311 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_198-67_0_6_load_82 | 114 | 0.001821 | 0.00045637 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_198-67_0_6_load_137 | 115 | 0.0086636 | 0.0021713 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_198-67_0_6_load_94 | 116 | 0.0014209 | 0.00035611 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_198-67_0_6_load_136 | 117 | 0.0014208 | 0.00035608 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_198-67_0_6_load_101 | 118 | 0.0049854 | 0.0012495 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_198-67_0_6_load_102 | 119 | 0.0084466 | 0.0021169 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_198-67_0_6_load_115 | 121 | 0.0090023 | 0.0022562 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_198-67_0_6_load_103 | 123 | 0.011338 | 0.0028415 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_198-67_0_6_load_104 | 124 | 0.0012714 | 0.00031863 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_198-67_0_6_load_130 | 127 | 0.0014175 | 0.00035526 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_198-67_0_6_load_110 | 128 | 0.011543 | 0.0028928 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_198-67_0_6_load_124 | 129 | 0.012217 | 0.0030619 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_198-67_0_6_load_119 | 130 | 0.011551 | 0.0028951 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_198-67_0_6_load_127 | 131 | 0.0024833 | 0.00062237 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_198-67_0_6_load_128 | 132 | 0.0032267 | 0.00080868 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_198-67_0_6_load_129 | 133 | 0.0018729 | 0.00046939 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_198-67_0_6_line_0 |  | 0 | 1 | 0.033558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_198-67_0_6_line_1 |  | 0 | 2 | 0.00065507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_198-67_0_6_line_2 |  | 1 | 3 | 0.025472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_198-67_0_6_line_3 |  | 3 | 4 | 0.036198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_198-67_0_6_line_4 |  | 4 | 5 | 0.056943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_198-67_0_6_line_5 |  | 5 | 8 | 0.015112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_198-67_0_6_line_6 |  | 5 | 9 | 0.037822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_198-67_0_6_line_7 |  | 6 | 7 | 0.012547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_198-67_0_6_line_8 |  | 7 | 10 | 0.075979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_198-67_0_6_line_9 |  | 8 | 90 | 0.003038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_198-67_0_6_line_10 |  | 9 | 92 | 0.018075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_198-67_0_6_line_11 |  | 9 | 91 | 0.024787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_198-67_0_6_line_12 |  | 10 | 123 | 0.0067786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_198-67_0_6_line_13 |  | 11 | 12 | 0.029459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_198-67_0_6_line_14 |  | 12 | 13 | 0.011476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_198-67_0_6_line_15 |  | 13 | 14 | 0.027846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_198-67_0_6_line_16 |  | 14 | 17 | 0.042138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_198-67_0_6_line_17 |  | 15 | 16 | 0.048272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_198-67_0_6_line_18 |  | 15 | 17 | 0.035215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_198-67_0_6_line_19 |  | 16 | 18 | 0.013609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_198-67_0_6_line_20 |  | 16 | 19 | 0.01924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_198-67_0_6_line_21 |  | 18 | 52 | 0.021946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_198-67_0_6_line_22 |  | 18 | 40 | 0.010374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_198-67_0_6_line_23 |  | 19 | 53 | 0.018252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_198-67_0_6_line_24 |  | 20 | 21 | 0.0043166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_198-67_0_6_line_25 |  | 20 | 22 | 0.027772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_198-67_0_6_line_26 |  | 20 | 23 | 0.019216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_198-67_0_6_line_27 |  | 21 | 57 | 0.013272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_198-67_0_6_line_28 |  | 22 | 37 | 0.025135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_198-67_0_6_line_29 |  | 22 | 38 | 0.017081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_198-67_0_6_line_30 |  | 23 | 25 | 0.013826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_198-67_0_6_line_31 |  | 24 | 25 | 0.018509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_198-67_0_6_line_32 |  | 24 | 26 | 0.018798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_198-67_0_6_line_33 |  | 24 | 27 | 0.013901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_198-67_0_6_line_34 |  | 26 | 58 | 0.011945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_198-67_0_6_line_35 |  | 28 | 29 | 0.008396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_198-67_0_6_line_36 |  | 28 | 30 | 0.012434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_198-67_0_6_line_37 |  | 29 | 39 | 0.025456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_198-67_0_6_line_38 |  | 29 | 35 | 0.01209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_198-67_0_6_line_39 |  | 30 | 59 | 0.035206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_198-67_0_6_line_40 |  | 31 | 32 | 0.015166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_198-67_0_6_line_41 |  | 31 | 33 | 0.01766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_198-67_0_6_line_42 |  | 31 | 34 | 0.072276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_198-67_0_6_line_43 |  | 32 | 36 | 0.014615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_198-67_0_6_line_44 |  | 33 | 60 | 0.0034174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_198-67_0_6_line_45 |  | 34 | 61 | 0.0057248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_198-67_0_6_line_46 |  | 35 | 36 | 0.0019507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_198-67_0_6_line_47 |  | 37 | 39 | 0.0277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_198-67_0_6_line_48 |  | 38 | 63 | 0.0069354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_198-67_0_6_line_49 |  | 40 | 41 | 0.017629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_198-67_0_6_line_50 |  | 42 | 43 | 0.02799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_198-67_0_6_line_51 |  | 43 | 55 | 0.0065899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_198-67_0_6_line_52 |  | 44 | 45 | 0.034605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_198-67_0_6_line_53 |  | 45 | 63 | 0.0031166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_198-67_0_6_line_54 |  | 46 | 47 | 0.056574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_198-67_0_6_line_55 |  | 47 | 48 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_198-67_0_6_line_56 |  | 48 | 49 | 0.014017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_198-67_0_6_line_57 |  | 49 | 50 | 0.05794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_198-67_0_6_line_58 |  | 49 | 51 | 0.011673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_198-67_0_6_line_59 |  | 51 | 67 | 0.01619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_198-67_0_6_line_60 |  | 52 | 95 | 0.029901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_198-67_0_6_line_61 |  | 53 | 113 | 0.025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_198-67_0_6_line_62 |  | 53 | 74 | 0.01503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_198-67_0_6_line_63 |  | 54 | 55 | 0.010018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_198-67_0_6_line_64 |  | 54 | 56 | 0.020548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_198-67_0_6_line_65 |  | 56 | 102 | 0.0014474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_198-67_0_6_line_66 |  | 57 | 62 | 0.018903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_198-67_0_6_line_67 |  | 58 | 102 | 0.023514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_198-67_0_6_line_68 |  | 59 | 128 | 0.0045079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_198-67_0_6_line_69 |  | 59 | 65 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_198-67_0_6_line_70 |  | 60 | 91 | 0.016216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_198-67_0_6_line_71 |  | 61 | 82 | 0.023653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_198-67_0_6_line_72 |  | 62 | 99 | 0.019742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_198-67_0_6_line_73 |  | 62 | 107 | 0.015136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_198-67_0_6_line_74 |  | 64 | 65 | 0.029059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_198-67_0_6_line_75 |  | 64 | 66 | 0.036849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_198-67_0_6_line_76 |  | 66 | 129 | 0.028025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_198-67_0_6_line_77 |  | 67 | 72 | 0.014857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_198-67_0_6_line_78 |  | 67 | 73 | 0.031533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_198-67_0_6_line_79 |  | 67 | 69 | 0.010498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_198-67_0_6_line_80 |  | 68 | 69 | 0.019317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_198-67_0_6_line_81 |  | 68 | 70 | 0.010814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_198-67_0_6_line_82 |  | 70 | 71 | 0.052736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_198-67_0_6_line_83 |  | 71 | 74 | 0.0047996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_198-67_0_6_line_84 |  | 72 | 75 | 0.018933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_198-67_0_6_line_85 |  | 73 | 76 | 0.01669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_198-67_0_6_line_86 |  | 76 | 77 | 0.036602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_198-67_0_6_line_87 |  | 76 | 78 | 0.0021644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_198-67_0_6_line_88 |  | 77 | 87 | 0.016765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_198-67_0_6_line_89 |  | 78 | 79 | 0.037272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_198-67_0_6_line_90 |  | 79 | 80 | 0.053617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_198-67_0_6_line_91 |  | 80 | 81 | 0.0078151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_198-67_0_6_line_92 |  | 81 | 86 | 0.01825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_198-67_0_6_line_93 |  | 82 | 83 | 0.0056874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_198-67_0_6_line_94 |  | 83 | 84 | 0.031564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_198-67_0_6_line_95 |  | 84 | 85 | 0.078217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_198-67_0_6_line_96 |  | 85 | 88 | 0.05239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_198-67_0_6_line_97 |  | 86 | 89 | 0.0051143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_198-67_0_6_line_98 |  | 89 | 103 | 0.026516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_198-67_0_6_line_99 |  | 90 | 93 | 0.017154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_198-67_0_6_line_100 |  | 92 | 94 | 0.0066973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_198-67_0_6_line_101 |  | 93 | 130 | 0.051915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_198-67_0_6_line_102 |  | 94 | 118 | 0.014155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_198-67_0_6_line_103 |  | 96 | 97 | 0.016753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_198-67_0_6_line_104 |  | 96 | 98 | 0.0094642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_198-67_0_6_line_105 |  | 97 | 99 | 0.0018329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_198-67_0_6_line_106 |  | 98 | 100 | 0.0020072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_198-67_0_6_line_107 |  | 100 | 101 | 0.0046216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_198-67_0_6_line_108 |  | 101 | 117 | 0.017129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_198-67_0_6_line_109 |  | 103 | 116 | 0.0090211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_198-67_0_6_line_110 |  | 104 | 105 | 0.0046049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_198-67_0_6_line_111 |  | 104 | 106 | 0.00036919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_198-67_0_6_line_112 |  | 105 | 107 | 0.0044801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_198-67_0_6_line_113 |  | 106 | 108 | 0.017047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_198-67_0_6_line_114 |  | 108 | 109 | 0.00042712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_198-67_0_6_line_115 |  | 109 | 110 | 0.012061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_198-67_0_6_line_116 |  | 110 | 114 | 0.0093846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_198-67_0_6_line_117 |  | 111 | 112 | 0.01173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_198-67_0_6_line_118 |  | 112 | 114 | 0.0018521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_198-67_0_6_line_119 |  | 113 | 115 | 0.030835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_198-67_0_6_line_120 |  | 116 | 117 | 0.0042635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_198-67_0_6_line_121 |  | 119 | 120 | 0.015579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_198-67_0_6_line_122 |  | 120 | 121 | 0.0095654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_198-67_0_6_line_123 |  | 120 | 122 | 0.027021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_198-67_0_6_line_124 |  | 121 | 128 | 0.017226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_198-67_0_6_line_125 |  | 122 | 125 | 0.029372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_198-67_0_6_line_126 |  | 123 | 124 | 0.0010638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_198-67_0_6_line_127 |  | 124 | 125 | 0.049491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_198-67_0_6_line_128 |  | 125 | 126 | 0.019708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_198-67_0_6_line_129 |  | 126 | 127 | 0.028268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_198-67_0_6_line_130 |  | 127 | 133 | 0.0046644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_198-67_0_6_line_131 |  | 131 | 132 | 0.023538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_198-67_0_6_line_132 |  | 132 | 133 | 0.029227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_198-67_0_6_trafo_78 | 0.63 MVA 20/0.4 kV | 134 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2698067.5338 | 1244667.0432 | 2698059.4379 | 1244664.3832 | 2698035.6695 | 1244656.5166
1 | 2698068.1562 | 1244667.2477 | 2698067.5338 | 1244667.0432
2 | 2698035.6695 | 1244656.5166 | 2698022.6593 | 1244652.2106 | 2698011.4093 | 1244648.7573
3 | 2697976.4536 | 1244639.4127 | 2697980.6237 | 1244640.296 | 2698000.5293 | 1244645.4176 | 2698011.4093 | 1244648.7573
4 | 2697920.7904 | 1244627.4094 | 2697937.6347 | 1244631.1903 | 2697976.4536 | 1244639.4127
5 | 2697920.7904 | 1244627.4094 | 2697921.5216 | 1244642.5036
6 | 2697883.8377 | 1244619.349 | 2697910.7374 | 1244625.1973 | 2697916.7319 | 1244626.4973 | 2697920.7904 | 1244627.4094
7 | 2697980.0676 | 1244702.9173 | 2697992.5672 | 1244701.8241
8 | 2697904.4289 | 1244710.0721 | 2697937.5522 | 1244706.6356 | 2697980.0676 | 1244702.9173
9 | 2697921.6686 | 1244645.5381 | 2697921.5216 | 1244642.5036
10 | 2697883.8377 | 1244619.349 | 2697881.0786 | 1244630.3675 | 2697877.837 | 1244636.25
11 | 2697883.8377 | 1244619.349 | 2697865.6324 | 1244616.9802 | 2697859.1842 | 1244616.151
12 | 2697897.6865 | 1244710.7716 | 2697904.4289 | 1244710.0721
13 | 2697408.7545 | 1244605.5374 | 2697438.0434 | 1244608.6986
14 | 2697449.4053 | 1244610.3019 | 2697440.7614 | 1244608.992 | 2697438.0434 | 1244608.6986
15 | 2697449.4053 | 1244610.3019 | 2697476.9368 | 1244614.4742
16 | 2697518.8671 | 1244615.9764 | 2697504.3082 | 1244617.1867 | 2697487.4276 | 1244616.064 | 2697476.9368 | 1244614.4742
17 | 2697565.3812 | 1244565.8181 | 2697563.4399 | 1244576.3164 | 2697554.8457 | 1244607.1543 | 2697553.389 | 1244612.5456
18 | 2697553.389 | 1244612.5456 | 2697549.3886 | 1244611.7681 | 2697544.8004 | 1244610.892 | 2697524.2956 | 1244615.5251 | 2697518.8671 | 1244615.9764
19 | 2697565.3812 | 1244565.8181 | 2697578.9539 | 1244567.2647
20 | 2697565.3812 | 1244565.8181 | 2697566.3787 | 1244552.9691 | 2697566.4501 | 1244546.6168
21 | 2697578.9539 | 1244567.2647 | 2697599.389 | 1244559.2622
22 | 2697582.6944 | 1244576.9447 | 2697578.9539 | 1244567.2647
23 | 2697566.6551 | 1244528.366 | 2697566.4501 | 1244546.6168
24 | 2697704.2195 | 1244593.7131 | 2697708.3827 | 1244592.5724
25 | 2697704.2195 | 1244593.7131 | 2697707.2517 | 1244598.6668 | 2697714.8703 | 1244597.269 | 2697722.5646 | 1244595.8613 | 2697725.616 | 1244601.4826
26 | 2697704.2195 | 1244593.7131 | 2697696.8457 | 1244595.393 | 2697691.9923 | 1244597.3034 | 2697686.1356 | 1244599.9764
27 | 2697721.3846 | 1244589.9596 | 2697717.2305 | 1244590.714 | 2697711.4547 | 1244591.7308 | 2697708.3827 | 1244592.5724
28 | 2697725.616 | 1244601.4826 | 2697738.863 | 1244600.2109 | 2697750.6896 | 1244600.1484
29 | 2697725.616 | 1244601.4826 | 2697716.1855 | 1244603.2175 | 2697708.9668 | 1244605.2223
30 | 2697673.925 | 1244606.4577 | 2697678.2462 | 1244604.0934 | 2697685.5728 | 1244600.2333 | 2697686.1356 | 1244599.9764
31 | 2697657.5973 | 1244615.1731 | 2697663.8809 | 1244611.7739 | 2697668.9343 | 1244609.1884 | 2697673.925 | 1244606.4577
32 | 2697656.3518 | 1244597.1832 | 2697654.3867 | 1244601.3207 | 2697657.5973 | 1244615.1731
33 | 2697657.5973 | 1244615.1731 | 2697645.392 | 1244621.8268
34 | 2697656.3518 | 1244597.1832 | 2697651.1452 | 1244589.803 | 2697648.353 | 1244588.9725
35 | 2697810.5734 | 1244612.4465 | 2697802.5275 | 1244609.9675
36 | 2697810.5734 | 1244612.4465 | 2697808.8995 | 1244617.2448 | 2697805.8036 | 1244623.9132
37 | 2697802.5275 | 1244609.9675 | 2697784.6767 | 1244603.5128 | 2697778.2543 | 1244602.6987
38 | 2697802.5275 | 1244609.9675 | 2697804.1315 | 1244603.9004 | 2697805.6074 | 1244598.276
39 | 2697790.9782 | 1244655.8456 | 2697805.8036 | 1244623.9132
40 | 2697822.5867 | 1244609.4534 | 2697819.7717 | 1244594.5511
41 | 2697822.5867 | 1244609.4534 | 2697836.2351 | 1244613.1702 | 2697839.7064 | 1244613.7182
42 | 2697822.5867 | 1244609.4534 | 2697828.2769 | 1244590.2659 | 2697831.9209 | 1244577.8275 | 2697833.7759 | 1244571.6756 | 2697837.4201 | 1244563.3516 | 2697842.2742 | 1244553.6131 | 2697848.5105 | 1244542.3115
43 | 2697819.7717 | 1244594.5511 | 2697817.5815 | 1244598.1178 | 2697813.2325 | 1244599.6917 | 2697807.5254 | 1244598.6321
44 | 2697839.7064 | 1244613.7182 | 2697843.0821 | 1244614.2511
45 | 2697848.5105 | 1244542.3115 | 2697849.5586 | 1244540.412 | 2697851.5257 | 1244537.4504
46 | 2697805.6074 | 1244598.276 | 2697807.5254 | 1244598.6321
47 | 2697778.2543 | 1244602.6987 | 2697766.2214 | 1244601.1735 | 2697752.6496 | 1244600.138 | 2697750.6896 | 1244600.1484
48 | 2697702.3202 | 1244607.1934 | 2697704.1666 | 1244606.5554 | 2697708.9668 | 1244605.2223
49 | 2697595.1016 | 1244589.5028 | 2697590.4236 | 1244584.9001 | 2697583.5634 | 1244577.8708 | 2697582.6944 | 1244576.9447
50 | 2697594.9859 | 1244612.652 | 2697593.2021 | 1244614.4462 | 2697591.0886 | 1244616.1238 | 2697581.0255 | 1244620.9398 | 2697570.3403 | 1244625.4699
51 | 2697599.6319 | 1244607.9787 | 2697594.9859 | 1244612.652
52 | 2697668.1051 | 1244622.8643 | 2697671.4244 | 1244620.8939 | 2697679.4514 | 1244616.7229 | 2697682.5388 | 1244615.1169 | 2697692.0657 | 1244610.7371 | 2697699.3746 | 1244608.2114
53 | 2697702.3202 | 1244607.1934 | 2697699.3746 | 1244608.2114
54 | 2697432.4313 | 1244419.1182 | 2697469.062 | 1244417.0324 | 2697488.924 | 1244416.1078
55 | 2697509.4289 | 1244415.1534 | 2697488.924 | 1244416.1078
56 | 2697523.4304 | 1244414.5016 | 2697509.4289 | 1244415.1534
57 | 2697523.4304 | 1244414.5016 | 2697525.6427 | 1244432.0959 | 2697534.1717 | 1244471.3883
58 | 2697523.4304 | 1244414.5016 | 2697535.0733 | 1244413.6649
59 | 2697550.6863 | 1244416.6958 | 2697540.5544 | 1244413.2711 | 2697535.0733 | 1244413.6649
60 | 2697627.5966 | 1244550.0532 | 2697622.1989 | 1244550.3298 | 2697599.389 | 1244559.2622
61 | 2697566.6551 | 1244528.366 | 2697551.4581 | 1244528.7164 | 2697543.8584 | 1244522.5311
62 | 2697566.6551 | 1244528.366 | 2697566.6614 | 1244513.3364
63 | 2697606.7564 | 1244600.9366 | 2697603.2849 | 1244604.3043 | 2697599.6319 | 1244607.9787
64 | 2697606.7564 | 1244600.9366 | 2697612.8931 | 1244595.4445 | 2697619.3729 | 1244591.6037 | 2697623.8435 | 1244589.9107
65 | 2697623.8435 | 1244589.9107 | 2697625.1972 | 1244589.3981
66 | 2697721.3846 | 1244589.9596 | 2697721.641 | 1244586.7836 | 2697724.184 | 1244577.3961 | 2697724.5446 | 1244576.1566 | 2697725.8509 | 1244571.6414
67 | 2697648.353 | 1244588.9725 | 2697646.3167 | 1244588.3669 | 2697639.6584 | 1244587.4455 | 2697632.6174 | 1244587.7298 | 2697626.4077 | 1244588.9397 | 2697625.1972 | 1244589.3981
68 | 2697790.9782 | 1244655.8456 | 2697794.8326 | 1244658.1833
69 | 2697790.9782 | 1244655.8456 | 2697782.3883 | 1244652.9018 | 2697775.0105 | 1244650.2448 | 2697773.5486 | 1244649.5577
70 | 2697859.1842 | 1244616.151 | 2697845.8311 | 1244614.6852 | 2697843.0821 | 1244614.2511
71 | 2697864.5877 | 1244517.7314 | 2697851.721 | 1244537.1563 | 2697851.5257 | 1244537.4504
72 | 2697725.8509 | 1244571.6414 | 2697721.2764 | 1244571.3102 | 2697716.1693 | 1244570.2698 | 2697706.744 | 1244567.1032
73 | 2697725.8509 | 1244571.6414 | 2697731.4722 | 1244571.7452 | 2697740.7046 | 1244569.4467
74 | 2697749.3522 | 1244633.7316 | 2697751.5473 | 1244635.8249 | 2697758.9141 | 1244641.4395 | 2697767.0909 | 1244646.5226 | 2697773.5486 | 1244649.5577
75 | 2697749.3522 | 1244633.7316 | 2697746.4613 | 1244636.7196 | 2697743.2703 | 1244640.0251 | 2697737.9631 | 1244643.7961 | 2697729.0088 | 1244649.1972 | 2697721.9206 | 1244657.8537
76 | 2697721.9206 | 1244657.8537 | 2697731.0592 | 1244669.6911 | 2697739.1058 | 1244679.9912
77 | 2697550.6863 | 1244416.6958 | 2697549.2734 | 1244401.9059
78 | 2697550.6863 | 1244416.6958 | 2697558.4356 | 1244418.3912 | 2697573.6741 | 1244417.3743 | 2697581.9897 | 1244416.9115
79 | 2697550.6863 | 1244416.6958 | 2697552.1093 | 1244427.0969
80 | 2697552.1093 | 1244427.0969 | 2697552.6091 | 1244430.7493 | 2697555.855 | 1244446.0389
81 | 2697558.1008 | 1244456.6173 | 2697555.855 | 1244446.0389
82 | 2697558.1008 | 1244456.6173 | 2697564.6315 | 1244487.3791 | 2697566.2012 | 1244497.6239 | 2697566.664 | 1244507.161 | 2697566.6634 | 1244508.5368
83 | 2697566.6614 | 1244513.3364 | 2697566.6634 | 1244508.5368
84 | 2697549.2734 | 1244401.9059 | 2697548.752 | 1244396.4485 | 2697549.1041 | 1244383.002
85 | 2697598.6535 | 1244415.9841 | 2697581.9897 | 1244416.9115
86 | 2697598.6535 | 1244415.9841 | 2697600.4701 | 1244441.9894 | 2697611.0036 | 1244442.0169
87 | 2697598.6535 | 1244415.9841 | 2697600.8163 | 1244415.9021
88 | 2697611.0036 | 1244442.0169 | 2697627.7681 | 1244442.0607
89 | 2697638.0755 | 1244415.0987 | 2697617.462 | 1244415.2708 | 2697600.8163 | 1244415.9021
90 | 2697638.0755 | 1244415.0987 | 2697638.4959 | 1244419.3978 | 2697644.12 | 1244443.6645 | 2697646.9214 | 1244457.5879 | 2697648.7707 | 1244467.6034
91 | 2697650.1897 | 1244475.2886 | 2697648.7707 | 1244467.6034
92 | 2697650.1897 | 1244475.2886 | 2697652.9004 | 1244493.3359
93 | 2697864.5877 | 1244517.7314 | 2697869.2501 | 1244520.9886
94 | 2697885.7093 | 1244494.0951 | 2697880.1962 | 1244504.3675 | 2697870.8051 | 1244518.3567 | 2697869.2501 | 1244520.9886
95 | 2697885.7093 | 1244494.0951 | 2697892.3139 | 1244495.0714 | 2697920.1101 | 1244494.2629 | 2697929.3793 | 1244494.9831 | 2697946.0995 | 1244495.7708 | 2697957.1591 | 1244496.9987 | 2697963.5833 | 1244498.3725
96 | 2697956.029 | 1244545.7285 | 2697958.5476 | 1244531.4369 | 2697964.3484 | 1244530.2874 | 2697964.9204 | 1244516.2528 | 2697963.5833 | 1244498.3725
97 | 2697654.9097 | 1244498.0389 | 2697652.9004 | 1244493.3359 | 2697652.9004 | 1244493.3359
98 | 2697654.9097 | 1244498.0389 | 2697658.2493 | 1244505.8557 | 2697663.253 | 1244514.0888 | 2697667.9977 | 1244520.9977
99 | 2697921.6686 | 1244645.5381 | 2697922.4986 | 1244662.6716
100 | 2697874.6047 | 1244642.1156 | 2697877.837 | 1244636.25
101 | 2697944.2339 | 1244680.0589 | 2697941.3748 | 1244688.8851 | 2697923.7042 | 1244687.5591 | 2697922.4986 | 1244662.6716
102 | 2697874.6047 | 1244642.1156 | 2697870.5917 | 1244649.3979 | 2697867.2142 | 1244654.1629
103 | 2697689.126 | 1244561.1841 | 2697705.0065 | 1244566.5194
104 | 2697689.126 | 1244561.1841 | 2697689.47 | 1244554.5291 | 2697688.0533 | 1244552.1136
105 | 2697706.744 | 1244567.1032 | 2697705.0065 | 1244566.5194
106 | 2697688.0533 | 1244552.1136 | 2697687.0378 | 1244550.3822
107 | 2697687.0378 | 1244550.3822 | 2697684.6997 | 1244546.3957
108 | 2697684.6997 | 1244546.3957 | 2697680.3691 | 1244539.0119 | 2697675.5183 | 1244531.9486
109 | 2697673.1047 | 1244528.434 | 2697667.9977 | 1244520.9977
110 | 2697748.717 | 1244565.2538 | 2697744.7225 | 1244567.5449
111 | 2697749.0373 | 1244565.0701 | 2697748.717 | 1244565.2538
112 | 2697740.7046 | 1244569.4467 | 2697741.945 | 1244569.1379 | 2697744.7225 | 1244567.5449
113 | 2697764.0354 | 1244556.9671 | 2697750.0862 | 1244564.4685 | 2697749.0373 | 1244565.0701
114 | 2697764.4115 | 1244556.7648 | 2697764.0354 | 1244556.9671
115 | 2697764.4115 | 1244556.7648 | 2697775.0341 | 1244551.0523
116 | 2697783.2994 | 1244546.6076 | 2697775.0341 | 1244551.0523
117 | 2697784.9305 | 1244545.7304 | 2697795.2612 | 1244540.1749
118 | 2697783.2994 | 1244546.6076 | 2697784.9305 | 1244545.7304
119 | 2697538.6825 | 1244492.1339 | 2697543.8584 | 1244522.5311
120 | 2697675.5183 | 1244531.9486 | 2697673.1047 | 1244528.434
121 | 2697817.8454 | 1244671.9008 | 2697825.9973 | 1244671.1569 | 2697831.3175 | 1244666.0225
122 | 2697817.8454 | 1244671.9008 | 2697809.5987 | 1244667.0545
123 | 2697831.5674 | 1244691.7645 | 2697823.2037 | 1244682.4417 | 2697819.1505 | 1244678.4607 | 2697815.596 | 1244675.3998 | 2697817.8454 | 1244671.9008
124 | 2697809.5987 | 1244667.0545 | 2697805.1133 | 1244664.4185 | 2697794.8326 | 1244658.1833
125 | 2697847.4014 | 1244715.9886 | 2697844.8993 | 1244709.1532 | 2697843.6487 | 1244705.7078 | 2697839.6785 | 1244700.8163 | 2697831.5674 | 1244691.7645
126 | 2697897.6865 | 1244710.7716 | 2697896.6284 | 1244710.8814
127 | 2697847.4014 | 1244715.9886 | 2697896.6284 | 1244710.8814
128 | 2697847.4014 | 1244715.9886 | 2697848.9019 | 1244719.8608 | 2697854.0177 | 1244734.5564
129 | 2697854.0177 | 1244734.5564 | 2697863.8608 | 1244732.9954 | 2697866.9298 | 1244732.9571 | 2697870.8369 | 1244734.3448 | 2697875.2617 | 1244735.9524 | 2697879.0298 | 1244737.0598 | 2697881.4792 | 1244737.1642
130 | 2697881.4792 | 1244737.1642 | 2697884.1427 | 1244737.2777 | 2697886.1381 | 1244737.1659
131 | 2697938.6632 | 1244732.3217 | 2697915.266 | 1244734.8907
132 | 2697886.1381 | 1244737.1659 | 2697903.3039 | 1244736.2041 | 2697915.266 | 1244734.8907

## bus_geodata
| x | y | coords
0 | 2698067.5338 | 1244667.0432
1 | 2698035.6695 | 1244656.5166
2 | 2698068.1561 | 1244667.2477
3 | 2698011.4093 | 1244648.7573
4 | 2697976.4536 | 1244639.4127
5 | 2697920.7904 | 1244627.4094
6 | 2697992.5672 | 1244701.8241
7 | 2697980.0676 | 1244702.9173
8 | 2697921.5216 | 1244642.5036
9 | 2697883.8377 | 1244619.349
10 | 2697904.4289 | 1244710.0721
11 | 2697408.7545 | 1244605.5374
12 | 2697438.0434 | 1244608.6986
13 | 2697449.4053 | 1244610.3019
14 | 2697476.9368 | 1244614.4742
15 | 2697553.389 | 1244612.5456
16 | 2697565.3812 | 1244565.8181
17 | 2697518.8671 | 1244615.9764
18 | 2697578.9539 | 1244567.2647
19 | 2697566.4501 | 1244546.6168
20 | 2697704.2195 | 1244593.7131
21 | 2697708.3827 | 1244592.5724
22 | 2697725.616 | 1244601.4826
23 | 2697686.1356 | 1244599.9764
24 | 2697657.5973 | 1244615.1731
25 | 2697673.925 | 1244606.4577
26 | 2697656.3518 | 1244597.1832
27 | 2697645.392 | 1244621.8268
28 | 2697810.5734 | 1244612.4465
29 | 2697802.5275 | 1244609.9675
30 | 2697805.8036 | 1244623.9132
31 | 2697822.5867 | 1244609.4534
32 | 2697819.7717 | 1244594.5511
33 | 2697839.7064 | 1244613.7182
34 | 2697848.5105 | 1244542.3115
35 | 2697805.6074 | 1244598.276
36 | 2697807.5254 | 1244598.6321
37 | 2697750.6896 | 1244600.1484
38 | 2697708.9668 | 1244605.2223
39 | 2697778.2543 | 1244602.6987
40 | 2697582.6944 | 1244576.9447
41 | 2697595.1016 | 1244589.5028
42 | 2697570.3403 | 1244625.4699
43 | 2697594.9859 | 1244612.652
44 | 2697668.1051 | 1244622.8643
45 | 2697699.3746 | 1244608.2114
46 | 2697432.4313 | 1244419.1182
47 | 2697488.924 | 1244416.1078
48 | 2697509.4289 | 1244415.1534
49 | 2697523.4304 | 1244414.5016
50 | 2697534.1717 | 1244471.3883
51 | 2697535.0733 | 1244413.6649
52 | 2697599.389 | 1244559.2622
53 | 2697566.6551 | 1244528.366
54 | 2697606.7564 | 1244600.9366
55 | 2697599.6319 | 1244607.9787
56 | 2697623.8435 | 1244589.9107
57 | 2697721.3846 | 1244589.9596
58 | 2697648.353 | 1244588.9725
59 | 2697790.9782 | 1244655.8456
60 | 2697843.0821 | 1244614.2511
61 | 2697851.5257 | 1244537.4504
62 | 2697725.8509 | 1244571.6414
63 | 2697702.3202 | 1244607.1934
64 | 2697749.3522 | 1244633.7316
65 | 2697773.5486 | 1244649.5577
66 | 2697721.9206 | 1244657.8537
67 | 2697550.6863 | 1244416.6958
68 | 2697555.855 | 1244446.0389
69 | 2697552.1093 | 1244427.0969
70 | 2697558.1008 | 1244456.6173
71 | 2697566.6634 | 1244508.5368
72 | 2697549.2734 | 1244401.9059
73 | 2697581.9897 | 1244416.9115
74 | 2697566.6614 | 1244513.3364
75 | 2697549.1041 | 1244383.002
76 | 2697598.6535 | 1244415.9841
77 | 2697611.0036 | 1244442.0169
78 | 2697600.8163 | 1244415.9021
79 | 2697638.0755 | 1244415.0987
80 | 2697648.7707 | 1244467.6034
81 | 2697650.1897 | 1244475.2886
82 | 2697864.5877 | 1244517.7314
83 | 2697869.2501 | 1244520.9886
84 | 2697885.7093 | 1244494.0951
85 | 2697963.5833 | 1244498.3725
86 | 2697652.9004 | 1244493.3359
87 | 2697627.7681 | 1244442.0607
88 | 2697956.029 | 1244545.7285
89 | 2697654.9097 | 1244498.0389
90 | 2697921.6686 | 1244645.5381
91 | 2697859.1842 | 1244616.151
92 | 2697877.837 | 1244636.25
93 | 2697922.4986 | 1244662.6716
94 | 2697874.6047 | 1244642.1156
95 | 2697627.5966 | 1244550.0532
96 | 2697689.126 | 1244561.1841
97 | 2697705.0065 | 1244566.5194
98 | 2697688.0533 | 1244552.1136
99 | 2697706.744 | 1244567.1032
100 | 2697687.0378 | 1244550.3822
101 | 2697684.6997 | 1244546.3957
102 | 2697625.1972 | 1244589.3981
103 | 2697667.9977 | 1244520.9977
104 | 2697748.717 | 1244565.2538
105 | 2697744.7225 | 1244567.5449
106 | 2697749.0373 | 1244565.0701
107 | 2697740.7046 | 1244569.4467
108 | 2697764.0354 | 1244556.9671
109 | 2697764.4115 | 1244556.7648
110 | 2697775.0341 | 1244551.0523
111 | 2697795.2612 | 1244540.1749
112 | 2697784.9305 | 1244545.7304
113 | 2697543.8584 | 1244522.5311
114 | 2697783.2994 | 1244546.6075
115 | 2697538.6825 | 1244492.1339
116 | 2697673.1047 | 1244528.434
117 | 2697675.5183 | 1244531.9486
118 | 2697867.2142 | 1244654.1629
119 | 2697831.3175 | 1244666.0225
120 | 2697817.8454 | 1244671.9008
121 | 2697809.5987 | 1244667.0545
122 | 2697831.5674 | 1244691.7645
123 | 2697897.6865 | 1244710.7716
124 | 2697896.6284 | 1244710.8814
125 | 2697847.4014 | 1244715.9886
126 | 2697854.0177 | 1244734.5564
127 | 2697881.4792 | 1244737.1642
128 | 2697794.8326 | 1244658.1833
129 | 2697739.1058 | 1244679.9912
130 | 2697944.2339 | 1244680.0589
131 | 2697938.6632 | 1244732.3217
132 | 2697915.266 | 1244734.8907
133 | 2697886.1381 | 1244737.1659
134 | 2697724.5446 | 1244576.1566

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97481 | -0.48614 | 0.0047872 | 0.0011998
1 | 0.97503 | -0.48164 | 0.0083344 | 0.0020888
2 | 0.9748 | -0.48617 | 0.0025373 | 0.0006359
3 | 0.97541 | -0.47433 | 0.0053088 | 0.0013305
4 | 0.97611 | -0.46043 | 0.021758 | 0.0054532
5 | 0.97837 | -0.41602 | 0 | 0
6 | 0.98114 | -0.36286 | 0.0034169 | 0.00085636
7 | 0.98118 | -0.36208 | 0.0039828 | 0.00099818
8 | 0.97811 | -0.42114 | 0.0014898 | 0.00037337
9 | 0.98053 | -0.37387 | 0 | 0
10 | 0.9817 | -0.3519 | 0.0017416 | 0.00043648
11 | 0.97108 | -0.55844 | 0.0045817 | 0.0011483
12 | 0.9712 | -0.55595 | 0.0046136 | 0.0011563
13 | 0.9713 | -0.554 | 0.001385 | 0.0003471
14 | 0.97158 | -0.54856 | 0.0034779 | 0.00087165
15 | 0.97324 | -0.51561 | 0 | 0
16 | 0.97477 | -0.48551 | 0 | 0
17 | 0.97213 | -0.53762 | 0.019876 | 0.0049813
18 | 0.97465 | -0.48786 | 0 | 0
19 | 0.97555 | -0.47022 | 0.0010802 | 0.00027073
20 | 0.99826 | -0.032914 | 0 | 0
21 | 0.99869 | -0.024861 | 0.0018505 | 0.00046377
22 | 0.99615 | -0.072954 | 0 | 0
23 | 0.99697 | -0.057604 | 0.0021208 | 0.00053153
24 | 0.99491 | -0.097346 | 0 | 0
25 | 0.99607 | -0.074892 | 0.0022673 | 0.00056824
26 | 0.99395 | -0.11577 | 0 | 0
27 | 0.99474 | -0.10062 | 0.01338 | 0.0033533
28 | 0.98943 | -0.20153 | 0 | 0
29 | 0.99013 | -0.18811 | 0 | 0
30 | 0.9884 | -0.22144 | 0.0076602 | 0.0019198
31 | 0.98526 | -0.28185 | 0 | 0
32 | 0.98694 | -0.24941 | 0 | 0
33 | 0.9838 | -0.31008 | 0.0051079 | 0.0012801
34 | 0.98322 | -0.32148 | 0.0033424 | 0.00083768
35 | 0.98877 | -0.21405 | 0 | 0
36 | 0.98856 | -0.21824 | 0.0011572 | 0.00029002
37 | 0.99443 | -0.1058 | 0.009187 | 0.0023025
38 | 0.99578 | -0.080148 | 0.0018333 | 0.00045948
39 | 0.9926 | -0.14063 | 0.0032453 | 0.00081336
40 | 0.97464 | -0.48822 | 0 | 0
41 | 0.9746 | -0.48884 | 0.0019078 | 0.00047814
42 | 0.99063 | -0.18011 | 0.018939 | 0.0047466
43 | 0.99111 | -0.1707 | 0.013363 | 0.003349
44 | 0.99511 | -0.093149 | 0.015306 | 0.0038361
45 | 0.99559 | -0.08383 | 0.0026333 | 0.00065997
46 | 0.98521 | -0.28242 | 0.0060456 | 0.0015152
47 | 0.98552 | -0.27628 | 0.00073367 | 0.00018388
48 | 0.98565 | -0.27378 | 0.0035353 | 0.00088602
49 | 0.98578 | -0.27119 | 0 | 0
50 | 0.98568 | -0.27324 | 0.0019729 | 0.00049445
51 | 0.98591 | -0.26862 | 0.0008751 | 0.00021932
52 | 0.9745 | -0.49089 | 0.00066558 | 0.00016681
53 | 0.97631 | -0.45537 | 0 | 0
54 | 0.99162 | -0.16076 | 0 | 0
55 | 0.99131 | -0.16693 | 0.0024301 | 0.00060905
56 | 0.99228 | -0.14811 | 0.0056253 | 0.0014098
57 | 1 | 0 | -0.52144 | -0.1331
58 | 0.99334 | -0.12749 | 0.0084753 | 0.0021241
59 | 0.98573 | -0.2732 | 0 | 0
60 | 0.98354 | -0.31523 | 0.004648 | 0.0011649
61 | 0.98308 | -0.32428 | 0.0035519 | 0.00089019
62 | 0.99889 | -0.020948 | 0 | 0
63 | 0.99564 | -0.082847 | 0.0041955 | 0.0010515
64 | 0.98502 | -0.28703 | 0 | 0
65 | 0.98535 | -0.28066 | 0.010207 | 0.002558
66 | 0.98461 | -0.29512 | 0 | 0
67 | 0.98611 | -0.2648 | 0 | 0
68 | 0.98341 | -0.31687 | 0.00064136 | 0.00016074
69 | 0.98515 | -0.28319 | 0.00076082 | 0.00019068
70 | 0.98244 | -0.33565 | 0.0038976 | 0.00097684
71 | 0.97791 | -0.42401 | 0.0047974 | 0.0012023
72 | 0.98605 | -0.26591 | 0.00098544 | 0.00024697
73 | 0.9878 | -0.23235 | 0.00083296 | 0.00020876
74 | 0.97752 | -0.43167 | 0.0012143 | 0.00030433
75 | 0.986 | -0.26699 | 0.003197 | 0.00080124
76 | 0.98839 | -0.22084 | 0 | 0
77 | 0.9881 | -0.22647 | 0.0045561 | 0.0011419
78 | 0.98848 | -0.21924 | 0.0027259 | 0.00068319
79 | 0.98995 | -0.19109 | 0 | 0
80 | 0.99206 | -0.15074 | 0.016294 | 0.0040837
81 | 0.9924 | -0.14413 | 0 | 0
82 | 0.98256 | -0.33435 | 0 | 0
83 | 0.98244 | -0.33677 | 0.0033518 | 0.00084004
84 | 0.98185 | -0.3483 | 0 | 0
85 | 0.98039 | -0.37694 | 0 | 0
86 | 0.99321 | -0.12869 | 0.0040285 | 0.0010096
87 | 0.98804 | -0.22769 | 0.0040601 | 0.0010175
88 | 0.9794 | -0.39617 | 0.020221 | 0.0050678
89 | 0.99345 | -0.12425 | 0.0027155 | 0.00068056
90 | 0.97806 | -0.42209 | 0.0029083 | 0.00072889
91 | 0.98235 | -0.33838 | 0 | 0
92 | 0.98023 | -0.3797 | 0.0045147 | 0.0011315
93 | 0.97784 | -0.42653 | 0.0026551 | 0.00066542
94 | 0.98015 | -0.38132 | 0.0082859 | 0.0020766
95 | 0.97431 | -0.49464 | 0.0068442 | 0.0017153
96 | 0.99695 | -0.057685 | 0 | 0
97 | 0.99779 | -0.041788 | 0.0017854 | 0.00044745
98 | 0.99647 | -0.066678 | 0.0014728 | 0.00036911
99 | 0.99788 | -0.040031 | 0.0015938 | 0.00039946
100 | 0.99637 | -0.068568 | 0.0016075 | 0.00040287
101 | 0.99615 | -0.07288 | 0.0016455 | 0.0004124
102 | 0.99233 | -0.14708 | 0.0067598 | 0.0016942
103 | 0.99468 | -0.10082 | 0.0046489 | 0.0011651
104 | 0.99838 | -0.030813 | 0.001538 | 0.00038547
105 | 0.99846 | -0.029249 | 0.0032754 | 0.00082089
106 | 0.99837 | -0.030928 | 0.0011694 | 0.00029307
107 | 0.99855 | -0.027472 | 0.0019784 | 0.00049584
108 | 0.99811 | -0.03591 | 0.0014097 | 0.0003533
109 | 0.99811 | -0.036024 | 0.0015774 | 0.00039533
110 | 0.99796 | -0.038919 | 0.0021879 | 0.00054834
111 | 0.9978 | -0.04194 | 0.0039557 | 0.00099139
112 | 0.99784 | -0.041128 | 0.0057538 | 0.001442
113 | 0.97533 | -0.47455 | 0.033242 | 0.0083311
114 | 0.99786 | -0.040813 | 0.001821 | 0.00045637
115 | 0.97508 | -0.47945 | 0.0086636 | 0.0021713
116 | 0.99511 | -0.092622 | 0.0014209 | 0.00035611
117 | 0.99531 | -0.088713 | 0.0014208 | 0.00035608
118 | 0.98008 | -0.3826 | 0.0049854 | 0.0012495
119 | 0.98425 | -0.30206 | 0.0084466 | 0.0021169
120 | 0.98437 | -0.29969 | 0 | 0
121 | 0.98472 | -0.29295 | 0.0090023 | 0.0022562
122 | 0.98361 | -0.31465 | 0 | 0
123 | 0.98176 | -0.35078 | 0.011338 | 0.0028415
124 | 0.98178 | -0.35039 | 0.0012714 | 0.00031863
125 | 0.98277 | -0.33094 | 0 | 0
126 | 0.98261 | -0.33414 | 0 | 0
127 | 0.98237 | -0.33874 | 0.0014175 | 0.00035526
128 | 0.98549 | -0.27803 | 0.011543 | 0.0028928
129 | 0.98429 | -0.30128 | 0.012217 | 0.0030619
130 | 0.97728 | -0.43747 | 0.011551 | 0.0028951
131 | 0.98213 | -0.34345 | 0.0024833 | 0.00062237
132 | 0.98219 | -0.34239 | 0.0032267 | 0.00080868
133 | 0.98234 | -0.33938 | 0.0018729 | 0.00046939
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0073244 | -0.0018357 | 0.007326 | 0.0018363 | 1.5731e-06 | 5.8832e-07 | 0.011181 | 0.01118 | 0.011181 | 0.97481 | -0.48614 | 0.97503 | -0.48164 | 3.0716
1 | 0.0025373 | 0.0006359 | -0.0025373 | -0.0006359 | 3.6851e-09 | -5.8081e-09 | 0.0038731 | 0.0038731 | 0.0038731 | 0.97481 | -0.48614 | 0.9748 | -0.48617 | 1.064
2 | -0.01566 | -0.003925 | 0.015666 | 0.0039282 | 5.4561e-06 | 3.1741e-06 | 0.0239 | 0.0239 | 0.0239 | 0.97503 | -0.48164 | 0.97541 | -0.47433 | 6.5658
3 | -0.020975 | -0.0052587 | 0.020989 | 0.0052672 | 1.3898e-05 | 8.4428e-06 | 0.031998 | 0.031998 | 0.031998 | 0.97541 | -0.47433 | 0.97611 | -0.46043 | 8.7907
4 | -0.042747 | -0.01072 | 0.042838 | 0.010778 | 9.0685e-05 | 5.7325e-05 | 0.065167 | 0.065167 | 0.065167 | 0.97611 | -0.46043 | 0.97837 | -0.41602 | 17.9031
5 | 0.018619 | 0.0046708 | -0.018614 | -0.0046681 | 4.5448e-06 | 2.719e-06 | 0.028319 | 0.028319 | 0.028319 | 0.97837 | -0.41602 | 0.97811 | -0.42114 | 7.78
6 | -0.061457 | -0.015448 | 0.06158 | 0.015527 | 0.00012396 | 7.8856e-05 | 0.093486 | 0.093486 | 0.093486 | 0.97837 | -0.41602 | 0.98053 | -0.37387 | 25.6831
7 | -0.0034169 | -0.00085636 | 0.003417 | 0.00085628 | 1.2636e-07 | -7.76e-08 | 0.0051822 | 0.0051821 | 0.0051822 | 0.98114 | -0.36286 | 0.98118 | -0.36208 | 1.4237
8 | -0.0073998 | -0.0018545 | 0.0074034 | 0.0018558 | 3.5881e-06 | 1.3363e-06 | 0.011222 | 0.011222 | 0.011222 | 0.98118 | -0.36208 | 0.9817 | -0.3519 | 3.083
9 | 0.017125 | 0.0042947 | -0.017124 | -0.0042943 | 7.7328e-07 | 4.5677e-07 | 0.026053 | 0.026053 | 0.026053 | 0.97811 | -0.42114 | 0.97806 | -0.42209 | 7.1574
10 | 0.017792 | 0.0044611 | -0.017787 | -0.0044582 | 4.9419e-06 | 2.9349e-06 | 0.027002 | 0.027002 | 0.027002 | 0.98053 | -0.37387 | 0.98023 | -0.3797 | 7.4181
11 | -0.079373 | -0.019988 | 0.079508 | 0.020075 | 0.00013494 | 8.6048e-05 | 0.12049 | 0.12049 | 0.12049 | 0.98053 | -0.37387 | 0.98235 | -0.33838 | 33.101
12 | -0.009145 | -0.0022923 | 0.0091455 | 0.0022925 | 4.8843e-07 | 2.2688e-07 | 0.013862 | 0.013862 | 0.013862 | 0.9817 | -0.3519 | 0.98176 | -0.35078 | 3.8081
13 | -0.0045817 | -0.0011483 | 0.0045822 | 0.0011483 | 5.4449e-07 | -1.6019e-08 | 0.0070206 | 0.0070205 | 0.0070206 | 0.97108 | -0.55844 | 0.9712 | -0.55595 | 1.9287
14 | -0.0091958 | -0.0023045 | 0.0091967 | 0.0023049 | 8.5429e-07 | 4.0472e-07 | 0.014089 | 0.014089 | 0.014089 | 0.9712 | -0.55595 | 0.9713 | -0.554 | 3.8707
15 | -0.010582 | -0.002652 | 0.010584 | 0.0026535 | 2.7441e-06 | 1.4115e-06 | 0.016211 | 0.016211 | 0.016211 | 0.9713 | -0.554 | 0.97158 | -0.54856 | 4.4535
16 | -0.014062 | -0.0035251 | 0.01407 | 0.0035293 | 7.3296e-06 | 4.1688e-06 | 0.021537 | 0.021537 | 0.021537 | 0.97158 | -0.54856 | 0.97213 | -0.53762 | 5.9169
17 | -0.033981 | -0.0085329 | 0.03403 | 0.0085636 | 4.8872e-05 | 3.0677e-05 | 0.05196 | 0.05196 | 0.05196 | 0.97324 | -0.51561 | 0.97477 | -0.48551 | 14.2747
18 | 0.033981 | 0.0085329 | -0.033945 | -0.0085105 | 3.5654e-05 | 2.2381e-05 | 0.05196 | 0.05196 | 0.05196 | 0.97324 | -0.51561 | 0.97213 | -0.53762 | 14.2748
19 | 0.009421 | 0.0023613 | -0.00942 | -0.0023608 | 1.0555e-06 | 5.0591e-07 | 0.014382 | 0.014382 | 0.014382 | 0.97477 | -0.48551 | 0.97465 | -0.48786 | 3.951
20 | -0.043451 | -0.010925 | 0.043482 | 0.010945 | 3.1755e-05 | 2.0083e-05 | 0.066341 | 0.066341 | 0.066341 | 0.97477 | -0.48551 | 0.97555 | -0.47022 | 18.2256
21 | 0.0075121 | 0.001883 | -0.007511 | -0.0018825 | 1.0825e-06 | 4.1935e-07 | 0.011469 | 0.011469 | 0.011469 | 0.97465 | -0.48786 | 0.9745 | -0.49089 | 3.1508
22 | 0.0019079 | 0.00047784 | -0.0019078 | -0.00047795 | 3.3004e-08 | -1.0816e-07 | 0.0029127 | 0.0029127 | 0.0029127 | 0.97465 | -0.48786 | 0.97464 | -0.48822 | 0.80019
23 | -0.044563 | -0.011216 | 0.044594 | 0.011236 | 3.1638e-05 | 2.0021e-05 | 0.067989 | 0.067989 | 0.067989 | 0.97555 | -0.47022 | 0.97631 | -0.45537 | 18.6783
24 | -0.32399 | -0.0827 | 0.32412 | 0.08278 | 0.00012613 | 8.0552e-05 | 0.48348 | 0.48348 | 0.48348 | 0.99826 | -0.032914 | 0.99869 | -0.024861 | 44.2744
25 | 0.25024 | 0.064064 | -0.24975 | -0.063755 | 0.00048424 | 0.00030883 | 0.37348 | 0.37349 | 0.37349 | 0.99826 | -0.032914 | 0.99615 | -0.072954 | 34.2019
26 | 0.073755 | 0.018636 | -0.073668 | -0.01858 | 8.7183e-05 | 5.5546e-05 | 0.10999 | 0.10999 | 0.10999 | 0.99826 | -0.032914 | 0.99697 | -0.057604 | 30.2178
27 | -0.32597 | -0.083244 | 0.32636 | 0.083495 | 0.00039222 | 0.0002505 | 0.48623 | 0.48623 | 0.48623 | 0.99869 | -0.024861 | 1 | 0 | 44.5269
28 | 0.22577 | 0.057737 | -0.22541 | -0.057509 | 0.0003582 | 0.00022827 | 0.33765 | 0.33765 | 0.33765 | 0.99615 | -0.072954 | 0.99443 | -0.1058 | 30.9205
29 | 0.023987 | 0.0060182 | -0.023979 | -0.0060132 | 8.2246e-06 | 5.0415e-06 | 0.035833 | 0.035834 | 0.035834 | 0.99615 | -0.072954 | 0.99578 | -0.080148 | 9.8444
30 | 0.071547 | 0.018049 | -0.071488 | -0.018011 | 5.9167e-05 | 3.7687e-05 | 0.10683 | 0.10683 | 0.10683 | 0.99697 | -0.057604 | 0.99607 | -0.074892 | 29.3482
31 | -0.069146 | -0.017396 | 0.06922 | 0.017443 | 7.4268e-05 | 4.7291e-05 | 0.10344 | 0.10344 | 0.10344 | 0.99491 | -0.097346 | 0.99607 | -0.074892 | 28.4177
32 | 0.055764 | 0.014041 | -0.055715 | -0.01401 | 4.9062e-05 | 3.1156e-05 | 0.083426 | 0.083426 | 0.083426 | 0.99491 | -0.097346 | 0.99395 | -0.11577 | 22.9192
33 | 0.013382 | 0.0033545 | -0.01338 | -0.0033533 | 2.0882e-06 | 1.156e-06 | 0.020015 | 0.020015 | 0.020015 | 0.99491 | -0.097346 | 0.99474 | -0.10062 | 5.4985
34 | 0.055715 | 0.01401 | -0.055684 | -0.01399 | 3.1176e-05 | 1.9798e-05 | 0.083426 | 0.083426 | 0.083426 | 0.99395 | -0.11577 | 0.99334 | -0.12749 | 22.9192
35 | -0.090273 | -0.022792 | 0.090331 | 0.022829 | 5.8083e-05 | 3.7065e-05 | 0.13582 | 0.13582 | 0.13582 | 0.98943 | -0.20153 | 0.99013 | -0.18811 | 37.3139
36 | 0.090273 | 0.022792 | -0.090187 | -0.022737 | 8.6016e-05 | 5.4891e-05 | 0.13582 | 0.13582 | 0.13582 | 0.98943 | -0.20153 | 0.9884 | -0.22144 | 37.3139
37 | -0.21213 | -0.053851 | 0.21261 | 0.054161 | 0.00048582 | 0.00031027 | 0.31904 | 0.31904 | 0.31904 | 0.99013 | -0.18811 | 0.9926 | -0.14063 | 43.8243
38 | 0.1218 | 0.031022 | -0.12164 | -0.030925 | 0.0001522 | 9.7252e-05 | 0.18322 | 0.18322 | 0.18322 | 0.99013 | -0.18811 | 0.98877 | -0.21405 | 50.3348
39 | 0.082527 | 0.020817 | -0.082323 | -0.020687 | 0.00020395 | 0.00013008 | 0.12429 | 0.12429 | 0.12429 | 0.9884 | -0.22144 | 0.98573 | -0.2732 | 34.1458
40 | -0.12009 | -0.030384 | 0.12028 | 0.030504 | 0.0001873 | 0.00011968 | 0.18148 | 0.18148 | 0.18148 | 0.98526 | -0.28185 | 0.98694 | -0.24941 | 49.8563
41 | 0.089494 | 0.022666 | -0.089373 | -0.022589 | 0.00012113 | 7.73e-05 | 0.13525 | 0.13525 | 0.13525 | 0.98526 | -0.28185 | 0.9838 | -0.31008 | 37.1553
42 | 0.0306 | 0.0077175 | -0.030542 | -0.0076813 | 5.7931e-05 | 3.6157e-05 | 0.046232 | 0.046232 | 0.046232 | 0.98526 | -0.28185 | 0.98322 | -0.32148 | 12.7011
43 | -0.12028 | -0.030504 | 0.12046 | 0.030619 | 0.0001805 | 0.00011533 | 0.18148 | 0.18148 | 0.18148 | 0.98694 | -0.24941 | 0.98856 | -0.21824 | 49.8563
44 | 0.084265 | 0.021309 | -0.084244 | -0.021296 | 2.084e-05 | 1.3294e-05 | 0.12752 | 0.12752 | 0.12752 | 0.9838 | -0.31008 | 0.98354 | -0.31523 | 35.0329
45 | 0.0272 | 0.0068436 | -0.027196 | -0.0068414 | 3.6394e-06 | 2.2566e-06 | 0.041174 | 0.041174 | 0.041174 | 0.98322 | -0.32148 | 0.98308 | -0.32428 | 11.3115
46 | 0.12164 | 0.030925 | -0.12162 | -0.030909 | 2.4557e-05 | 1.5691e-05 | 0.18322 | 0.18322 | 0.18322 | 0.98877 | -0.21405 | 0.98856 | -0.21824 | 50.3348
47 | 0.21622 | 0.055206 | -0.21586 | -0.054975 | 0.00036327 | 0.00023142 | 0.32391 | 0.32391 | 0.32391 | 0.99443 | -0.1058 | 0.9926 | -0.14063 | 29.6617
48 | 0.022146 | 0.0055537 | -0.022143 | -0.005552 | 2.8484e-06 | 1.7328e-06 | 0.033094 | 0.033094 | 0.033094 | 0.99578 | -0.080148 | 0.99564 | -0.082847 | 9.0918
49 | 0.0019078 | 0.00047795 | -0.0019078 | -0.00047814 | 5.6087e-08 | -1.8379e-07 | 0.0029127 | 0.0029128 | 0.0029128 | 0.97464 | -0.48822 | 0.9746 | -0.48884 | 0.80022
50 | -0.018939 | -0.0047466 | 0.018948 | 0.0047516 | 8.4947e-06 | 5.0761e-06 | 0.028448 | 0.028448 | 0.028448 | 0.99063 | -0.18011 | 0.99111 | -0.1707 | 7.8155
51 | -0.03231 | -0.0081006 | 0.032316 | 0.0081043 | 5.8154e-06 | 3.6369e-06 | 0.04851 | 0.04851 | 0.04851 | 0.99111 | -0.1707 | 0.99131 | -0.16693 | 13.327
52 | -0.015306 | -0.0038361 | 0.015313 | 0.00384 | 6.798e-06 | 3.9009e-06 | 0.022888 | 0.022888 | 0.022888 | 0.99511 | -0.093149 | 0.99559 | -0.08383 | 6.2879
53 | -0.017946 | -0.0045 | 0.017947 | 0.0045005 | 8.4091e-07 | 4.9765e-07 | 0.026824 | 0.026824 | 0.026824 | 0.99559 | -0.08383 | 0.99564 | -0.082847 | 7.3691
54 | -0.0060456 | -0.0015152 | 0.0060474 | 0.0015156 | 1.7688e-06 | 4.1139e-07 | 0.0091311 | 0.0091308 | 0.0091311 | 0.98521 | -0.28242 | 0.98552 | -0.27628 | 2.5085
55 | -0.0067811 | -0.0016995 | 0.0067819 | 0.0016997 | 8.0693e-07 | 2.5484e-07 | 0.010239 | 0.010238 | 0.010239 | 0.98552 | -0.27628 | 0.98565 | -0.27378 | 2.8128
56 | -0.010317 | -0.0025857 | 0.010318 | 0.0025864 | 1.2752e-06 | 6.3743e-07 | 0.015576 | 0.015576 | 0.015576 | 0.98565 | -0.27378 | 0.98578 | -0.27119 | 4.279
57 | 0.0019731 | 0.00049384 | -0.0019729 | -0.00049445 | 1.9272e-07 | -6.1525e-07 | 0.0029781 | 0.0029784 | 0.0029784 | 0.98578 | -0.27119 | 0.98568 | -0.27324 | 0.81823
58 | -0.012291 | -0.0030802 | 0.012293 | 0.003081 | 1.5068e-06 | 8.1553e-07 | 0.018554 | 0.018554 | 0.018554 | 0.98578 | -0.27119 | 0.98591 | -0.26862 | 5.0971
59 | -0.013168 | -0.0033003 | 0.01317 | 0.0033017 | 2.3981e-06 | 1.3283e-06 | 0.019874 | 0.019874 | 0.019874 | 0.98591 | -0.26862 | 0.98611 | -0.2648 | 5.46
60 | 0.0068454 | 0.0017157 | -0.0068442 | -0.0017153 | 1.2251e-06 | 4.1163e-07 | 0.010453 | 0.010453 | 0.010453 | 0.9745 | -0.49089 | 0.97431 | -0.49464 | 2.8717
61 | 0.041946 | 0.010528 | -0.041907 | -0.010503 | 3.8322e-05 | 2.4214e-05 | 0.063936 | 0.063936 | 0.063936 | 0.97631 | -0.45537 | 0.97533 | -0.47455 | 17.5648
62 | -0.08654 | -0.021763 | 0.086638 | 0.021826 | 9.8091e-05 | 6.259e-05 | 0.13192 | 0.13192 | 0.13192 | 0.97631 | -0.45537 | 0.97752 | -0.43167 | 36.243
63 | 0.034756 | 0.0087197 | -0.034746 | -0.0087133 | 1.022e-05 | 6.4116e-06 | 0.052158 | 0.052158 | 0.052158 | 0.99162 | -0.16076 | 0.99131 | -0.16693 | 14.3291
64 | -0.034756 | -0.0087197 | 0.034777 | 0.0087329 | 2.0963e-05 | 1.3151e-05 | 0.052158 | 0.052158 | 0.052158 | 0.99162 | -0.16076 | 0.99228 | -0.14811 | 14.3291
65 | -0.040403 | -0.010143 | 0.040405 | 0.010144 | 1.9929e-06 | 1.2567e-06 | 0.060594 | 0.060594 | 0.060594 | 0.99228 | -0.14811 | 0.99233 | -0.14708 | 16.6466
66 | 0.19343 | 0.049609 | -0.19323 | -0.049484 | 0.0001963 | 0.00012489 | 0.28823 | 0.28823 | 0.28823 | 1 | 0 | 0.99889 | -0.020948 | 26.3945
67 | 0.047209 | 0.011866 | -0.047164 | -0.011838 | 4.4113e-05 | 2.7928e-05 | 0.07073 | 0.07073 | 0.07073 | 0.99334 | -0.12749 | 0.99233 | -0.14708 | 19.4313
68 | 0.059879 | 0.015056 | -0.059865 | -0.015047 | 1.3817e-05 | 8.7856e-06 | 0.090408 | 0.090408 | 0.090408 | 0.98573 | -0.2732 | 0.98549 | -0.27803 | 24.8374
69 | 0.022444 | 0.0056313 | -0.022436 | -0.0056265 | 7.9805e-06 | 4.8713e-06 | 0.033882 | 0.033883 | 0.033883 | 0.98573 | -0.2732 | 0.98535 | -0.28066 | 9.3084
70 | 0.079596 | 0.020131 | -0.079508 | -0.020075 | 8.8282e-05 | 5.6295e-05 | 0.12049 | 0.12049 | 0.12049 | 0.98354 | -0.31523 | 0.98235 | -0.33838 | 33.101
71 | 0.023644 | 0.0059512 | -0.023633 | -0.0059442 | 1.1366e-05 | 6.9747e-06 | 0.035797 | 0.035798 | 0.035798 | 0.98308 | -0.32428 | 0.98256 | -0.33435 | 9.8345
72 | 0.16855 | 0.043291 | -0.16839 | -0.043192 | 0.00015603 | 9.9085e-05 | 0.25145 | 0.25145 | 0.25145 | 0.99889 | -0.020948 | 0.99788 | -0.040031 | 23.0269
73 | 0.024685 | 0.0061928 | -0.024677 | -0.0061881 | 7.6764e-06 | 4.7148e-06 | 0.036775 | 0.036775 | 0.036775 | 0.99889 | -0.020948 | 0.99855 | -0.027472 | 10.103
74 | -0.012226 | -0.0030664 | 0.012229 | 0.0030684 | 3.7172e-06 | 2.009e-06 | 0.018469 | 0.018469 | 0.018469 | 0.98502 | -0.28703 | 0.98535 | -0.28066 | 5.074
75 | 0.012226 | 0.0030664 | -0.012221 | -0.0030639 | 4.7137e-06 | 2.5479e-06 | 0.018469 | 0.01847 | 0.01847 | 0.98502 | -0.28703 | 0.98461 | -0.29512 | 5.074
76 | 0.012221 | 0.0030639 | -0.012217 | -0.0030619 | 3.585e-06 | 1.9381e-06 | 0.01847 | 0.01847 | 0.01847 | 0.98461 | -0.29512 | 0.98429 | -0.30128 | 5.0741
77 | 0.0041828 | 0.001048 | -0.0041826 | -0.0010481 | 2.2195e-07 | -4.7478e-08 | 0.0063117 | 0.0063117 | 0.0063117 | 0.98611 | -0.2648 | 0.98605 | -0.26591 | 1.734
78 | -0.11606 | -0.029495 | 0.11624 | 0.029611 | 0.00018165 | 0.00011545 | 0.17528 | 0.17528 | 0.17528 | 0.98611 | -0.2648 | 0.9878 | -0.23235 | 24.0771
79 | 0.098709 | 0.025146 | -0.098621 | -0.02509 | 8.7512e-05 | 5.5874e-05 | 0.1491 | 0.1491 | 0.1491 | 0.98611 | -0.2648 | 0.98515 | -0.28319 | 40.9603
80 | -0.097702 | -0.024798 | 0.097861 | 0.024899 | 0.00015855 | 0.00010123 | 0.14795 | 0.14795 | 0.14795 | 0.98341 | -0.31687 | 0.98515 | -0.28319 | 40.6446
81 | 0.097061 | 0.024637 | -0.096973 | -0.024581 | 8.7603e-05 | 5.5929e-05 | 0.14698 | 0.14698 | 0.14698 | 0.98341 | -0.31687 | 0.98244 | -0.33565 | 40.378
82 | 0.093075 | 0.023604 | -0.092682 | -0.023353 | 0.00039357 | 0.00025122 | 0.14107 | 0.14107 | 0.14107 | 0.98244 | -0.33565 | 0.97791 | -0.42401 | 38.7562
83 | 0.087884 | 0.022151 | -0.087852 | -0.02213 | 3.2209e-05 | 2.0554e-05 | 0.13377 | 0.13377 | 0.13377 | 0.97791 | -0.42401 | 0.97752 | -0.43167 | 36.7508
84 | 0.0031971 | 0.0008011 | -0.003197 | -0.00080124 | 1.6527e-07 | -1.3573e-07 | 0.0048246 | 0.0048247 | 0.0048247 | 0.98605 | -0.26591 | 0.986 | -0.26699 | 1.3255
85 | -0.11708 | -0.02982 | 0.11714 | 0.029861 | 6.5016e-05 | 4.0969e-05 | 0.17654 | 0.17654 | 0.17654 | 0.9878 | -0.23235 | 0.98839 | -0.22084 | 16.1663
86 | 0.0086187 | 0.0021604 | -0.0086164 | -0.0021594 | 2.311e-06 | 1.01e-06 | 0.012976 | 0.012976 | 0.012976 | 0.98839 | -0.22084 | 0.9881 | -0.22647 | 3.5647
87 | -0.12576 | -0.032021 | 0.12577 | 0.032027 | 9.7167e-06 | 6.1355e-06 | 0.18951 | 0.18951 | 0.18951 | 0.98839 | -0.22084 | 0.98848 | -0.21924 | 17.3545
88 | 0.0040603 | 0.0010175 | -0.0040601 | -0.0010175 | 2.3504e-07 | -6.4297e-08 | 0.0061145 | 0.0061145 | 0.0061145 | 0.9881 | -0.22647 | 0.98804 | -0.22769 | 1.6798
89 | -0.1285 | -0.03271 | 0.12867 | 0.032821 | 0.00017465 | 0.00011034 | 0.19361 | 0.19361 | 0.19361 | 0.98848 | -0.21924 | 0.98995 | -0.19109 | 17.7302
90 | -0.12867 | -0.032821 | 0.12892 | 0.032979 | 0.00025124 | 0.00015872 | 0.19361 | 0.19361 | 0.19361 | 0.98995 | -0.19109 | 0.99206 | -0.15074 | 17.7302
91 | -0.14522 | -0.037063 | 0.14526 | 0.037092 | 4.6448e-05 | 2.9424e-05 | 0.21805 | 0.21805 | 0.21805 | 0.99206 | -0.15074 | 0.9924 | -0.14413 | 19.9682
92 | -0.14526 | -0.037092 | 0.14537 | 0.037161 | 0.00010846 | 6.8709e-05 | 0.21805 | 0.21805 | 0.21805 | 0.9924 | -0.14413 | 0.99321 | -0.12869 | 19.9682
93 | 0.023633 | 0.0059442 | -0.02363 | -0.0059425 | 2.7331e-06 | 1.6771e-06 | 0.035798 | 0.035798 | 0.035798 | 0.98256 | -0.33435 | 0.98244 | -0.33677 | 9.8345
94 | 0.020278 | 0.0051025 | -0.020267 | -0.0050958 | 1.1171e-05 | 6.7501e-06 | 0.030721 | 0.030721 | 0.030721 | 0.98244 | -0.33677 | 0.98185 | -0.3483 | 8.4399
95 | 0.020267 | 0.0050958 | -0.020239 | -0.005079 | 2.7683e-05 | 1.6729e-05 | 0.030721 | 0.030721 | 0.030721 | 0.98185 | -0.3483 | 0.98039 | -0.37694 | 8.4399
96 | 0.020239 | 0.005079 | -0.020221 | -0.0050678 | 1.8542e-05 | 1.1207e-05 | 0.030721 | 0.030722 | 0.030722 | 0.98039 | -0.37694 | 0.9794 | -0.39617 | 8.44
97 | -0.1494 | -0.038171 | 0.14943 | 0.038191 | 3.2102e-05 | 2.0347e-05 | 0.22409 | 0.22409 | 0.22409 | 0.99321 | -0.12869 | 0.99345 | -0.12425 | 20.5208
98 | -0.15215 | -0.038872 | 0.15232 | 0.038981 | 0.00017253 | 0.00010939 | 0.22815 | 0.22815 | 0.22815 | 0.99345 | -0.12425 | 0.99468 | -0.10082 | 20.8933
99 | 0.014216 | 0.0035654 | -0.014212 | -0.0035637 | 3.0091e-06 | 1.7106e-06 | 0.021628 | 0.021628 | 0.021628 | 0.97806 | -0.42209 | 0.97784 | -0.42653 | 5.9419
100 | 0.013273 | 0.0033267 | -0.013272 | -0.0033261 | 1.0195e-06 | 5.6809e-07 | 0.020148 | 0.020148 | 0.020148 | 0.98023 | -0.3797 | 0.98015 | -0.38132 | 5.5352
101 | 0.011557 | 0.0028983 | -0.011551 | -0.0028951 | 6.0223e-06 | 3.2034e-06 | 0.017588 | 0.017588 | 0.017588 | 0.97784 | -0.42653 | 0.97728 | -0.43747 | 4.8319
102 | 0.0049857 | 0.0012495 | -0.0049854 | -0.0012495 | 3.0412e-07 | 1.6237e-08 | 0.007569 | 0.0075691 | 0.0075691 | 0.98015 | -0.38132 | 0.98008 | -0.3826 | 2.0794
103 | -0.16487 | -0.042256 | 0.165 | 0.042336 | 0.00012715 | 8.0723e-05 | 0.24641 | 0.24641 | 0.24641 | 0.99695 | -0.057685 | 0.99779 | -0.041788 | 22.5655
104 | 0.16487 | 0.042256 | -0.1648 | -0.04221 | 7.1833e-05 | 4.5603e-05 | 0.24641 | 0.24642 | 0.24642 | 0.99695 | -0.057685 | 0.99647 | -0.066678 | 22.5655
105 | -0.16678 | -0.042784 | 0.1668 | 0.042793 | 1.4214e-05 | 9.0252e-06 | 0.24908 | 0.24908 | 0.24908 | 0.99779 | -0.041788 | 0.99788 | -0.040031 | 22.8093
106 | 0.16333 | 0.041841 | -0.16331 | -0.041831 | 1.4964e-05 | 9.4987e-06 | 0.24422 | 0.24422 | 0.24422 | 0.99647 | -0.066678 | 0.99637 | -0.068568 | 22.3641
107 | 0.1617 | 0.041429 | -0.16167 | -0.041407 | 3.3781e-05 | 2.1439e-05 | 0.24182 | 0.24182 | 0.24182 | 0.99637 | -0.068568 | 0.99615 | -0.07288 | 22.1443
108 | 0.16003 | 0.040995 | -0.1599 | -0.040917 | 0.00012267 | 7.7839e-05 | 0.23936 | 0.23936 | 0.23936 | 0.99615 | -0.07288 | 0.99531 | -0.088713 | 21.9192
109 | -0.15697 | -0.040146 | 0.15703 | 0.040186 | 6.2332e-05 | 3.9541e-05 | 0.23511 | 0.23511 | 0.23511 | 0.99468 | -0.10082 | 0.99511 | -0.092622 | 21.5301
110 | -0.01942 | -0.0048694 | 0.019422 | 0.0048702 | 1.4468e-06 | 8.6574e-07 | 0.028945 | 0.028945 | 0.028945 | 0.99838 | -0.030813 | 0.99846 | -0.029249 | 7.952
111 | 0.017882 | 0.0044839 | -0.017882 | -0.0044838 | 9.835e-08 | 5.8117e-08 | 0.026653 | 0.026653 | 0.026653 | 0.99838 | -0.030813 | 0.99837 | -0.030928 | 7.3223
112 | -0.022697 | -0.0056911 | 0.022699 | 0.0056923 | 1.9224e-06 | 1.1717e-06 | 0.033827 | 0.033827 | 0.033827 | 0.99846 | -0.029249 | 0.99855 | -0.027472 | 9.293
113 | 0.016713 | 0.0041908 | -0.016709 | -0.0041884 | 3.9668e-06 | 2.3159e-06 | 0.02491 | 0.02491 | 0.02491 | 0.99837 | -0.030928 | 0.99811 | -0.03591 | 6.8435
114 | 0.015299 | 0.0038351 | -0.015299 | -0.0038351 | 8.3326e-08 | 4.7746e-08 | 0.022809 | 0.022809 | 0.022809 | 0.99811 | -0.03591 | 0.99811 | -0.036024 | 6.2661
115 | 0.013722 | 0.0034398 | -0.01372 | -0.0034387 | 1.8928e-06 | 1.0538e-06 | 0.020457 | 0.020457 | 0.020457 | 0.99811 | -0.036024 | 0.99796 | -0.038919 | 5.6201
116 | 0.011532 | 0.0028904 | -0.011531 | -0.0028898 | 1.0405e-06 | 5.4331e-07 | 0.017195 | 0.017195 | 0.017195 | 0.99796 | -0.038919 | 0.99786 | -0.040813 | 4.7238
117 | -0.0039557 | -0.00099139 | 0.0039559 | 0.00099134 | 1.5307e-07 | -5.5251e-08 | 0.0058991 | 0.0058991 | 0.0058991 | 0.9978 | -0.04194 | 0.99784 | -0.041128 | 1.6206
118 | -0.0097097 | -0.0024334 | 0.0097098 | 0.0024334 | 1.4561e-07 | 6.8996e-08 | 0.014479 | 0.014479 | 0.014479 | 0.99784 | -0.041128 | 0.99786 | -0.040813 | 3.9778
119 | 0.0086657 | 0.0021722 | -0.0086636 | -0.0021713 | 2.0211e-06 | 9.0881e-07 | 0.013221 | 0.013221 | 0.013221 | 0.97533 | -0.47455 | 0.97508 | -0.47945 | 3.6321
120 | -0.15845 | -0.040542 | 0.15848 | 0.040561 | 2.9994e-05 | 1.903e-05 | 0.23723 | 0.23723 | 0.23723 | 0.99511 | -0.092622 | 0.99531 | -0.088713 | 21.7247
121 | -0.0084466 | -0.0021169 | 0.0084476 | 0.0021173 | 9.5268e-07 | 4.1169e-07 | 0.01277 | 0.01277 | 0.01277 | 0.98425 | -0.30206 | 0.98437 | -0.29969 | 3.5082
122 | -0.039274 | -0.0098684 | 0.039286 | 0.0098764 | 1.2646e-05 | 7.972e-06 | 0.059376 | 0.059376 | 0.059376 | 0.98437 | -0.29969 | 0.98472 | -0.29295 | 16.3122
123 | 0.030826 | 0.0077511 | -0.030804 | -0.0077374 | 2.2011e-05 | 1.3744e-05 | 0.046607 | 0.046607 | 0.046607 | 0.98437 | -0.29969 | 0.98361 | -0.31465 | 12.8041
124 | -0.048288 | -0.012133 | 0.048323 | 0.012154 | 3.4406e-05 | 2.18e-05 | 0.07298 | 0.07298 | 0.07298 | 0.98472 | -0.29295 | 0.98549 | -0.27803 | 20.0494
125 | 0.030804 | 0.0077374 | -0.03078 | -0.0077224 | 2.3926e-05 | 1.494e-05 | 0.046607 | 0.046607 | 0.046607 | 0.98361 | -0.31465 | 0.98277 | -0.33094 | 12.8041
126 | -0.020483 | -0.005134 | 0.020484 | 0.0051343 | 3.845e-07 | 2.3263e-07 | 0.031046 | 0.031046 | 0.031046 | 0.98176 | -0.35078 | 0.98178 | -0.35039 | 8.5291
127 | -0.021755 | -0.0054529 | 0.021775 | 0.0054652 | 2.0178e-05 | 1.2287e-05 | 0.032973 | 0.032973 | 0.032973 | 0.98178 | -0.35039 | 0.98277 | -0.33094 | 9.0585
128 | 0.0090048 | 0.0022572 | -0.0090035 | -0.0022566 | 1.3739e-06 | 6.296e-07 | 0.013634 | 0.013634 | 0.013634 | 0.98277 | -0.33094 | 0.98261 | -0.33414 | 3.7457
129 | 0.0090035 | 0.0022566 | -0.0090015 | -0.0022557 | 1.9707e-06 | 9.0324e-07 | 0.013634 | 0.013635 | 0.013635 | 0.98261 | -0.33414 | 0.98237 | -0.33874 | 3.7458
130 | 0.007584 | 0.0019005 | -0.0075837 | -0.0019004 | 2.3082e-07 | 8.8672e-08 | 0.011487 | 0.011487 | 0.011487 | 0.98237 | -0.33874 | 0.98234 | -0.33938 | 3.1559
131 | -0.0024833 | -0.00062237 | 0.0024834 | 0.00062215 | 1.2494e-07 | -2.1792e-07 | 0.0037624 | 0.0037623 | 0.0037624 | 0.98213 | -0.34345 | 0.98219 | -0.34239 | 1.0336
132 | -0.00571 | -0.0014308 | 0.0057109 | 0.001431 | 8.2017e-07 | 1.5495e-07 | 0.0086506 | 0.0086505 | 0.0086506 | 0.98219 | -0.34239 | 0.98234 | -0.33938 | 2.3766

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52144 | 0.1331

## res_load
| p_mw | q_mvar
0 | 0.0047872 | 0.0011998
1 | 0.0083344 | 0.0020888
2 | 0.0025373 | 0.0006359
3 | 0.0053088 | 0.0013305
4 | 0.021758 | 0.0054532
5 | 0.0034169 | 0.00085636
6 | 0.0039828 | 0.00099818
7 | 0.0014898 | 0.00037337
8 | 0.0017416 | 0.00043648
9 | 0.0045817 | 0.0011483
10 | 0.0046136 | 0.0011563
11 | 0.001385 | 0.0003471
12 | 0.0034779 | 0.00087165
13 | 0.019876 | 0.0049813
14 | 0.0010802 | 0.00027073
15 | 0.0018505 | 0.00046377
16 | 0.0021208 | 0.00053153
17 | 0.0022673 | 0.00056824
18 | 0.01338 | 0.0033533
19 | 0.0076602 | 0.0019198
20 | 0.0051079 | 0.0012801
21 | 0.0033424 | 0.00083768
22 | 0.0011572 | 0.00029002
23 | 0.009187 | 0.0023025
24 | 0.0018333 | 0.00045948
25 | 0.0032453 | 0.00081336
26 | 0.0019078 | 0.00047814
27 | 0.018939 | 0.0047466
28 | 0.013363 | 0.003349
29 | 0.015306 | 0.0038361
30 | 0.0026333 | 0.00065997
31 | 0.0060456 | 0.0015152
32 | 0.00073367 | 0.00018388
33 | 0.0035353 | 0.00088602
34 | 0.0019729 | 0.00049445
35 | 0.0008751 | 0.00021932
36 | 0.00066558 | 0.00016681
37 | 0.0024301 | 0.00060905
38 | 0.0056253 | 0.0014098
39 | 0.0084753 | 0.0021241
40 | 0.004648 | 0.0011649
41 | 0.0035519 | 0.00089019
42 | 0.0041955 | 0.0010515
43 | 0.010207 | 0.002558
44 | 0.00064136 | 0.00016074
45 | 0.00076082 | 0.00019068
46 | 0.0038976 | 0.00097684
47 | 0.0047974 | 0.0012023
48 | 0.00098544 | 0.00024697
49 | 0.00083296 | 0.00020876
50 | 0.0012143 | 0.00030433
51 | 0.003197 | 0.00080124
52 | 0.0045561 | 0.0011419
53 | 0.0027259 | 0.00068319
54 | 0.016294 | 0.0040837
55 | 0.0033518 | 0.00084004
56 | 0.0040285 | 0.0010096
57 | 0.0040601 | 0.0010175
58 | 0.020221 | 0.0050678
59 | 0.0027155 | 0.00068056
60 | 0.0029083 | 0.00072889
61 | 0.0045147 | 0.0011315
62 | 0.0026551 | 0.00066542
63 | 0.0082859 | 0.0020766
64 | 0.0068442 | 0.0017153
65 | 0.0017854 | 0.00044745
66 | 0.0014728 | 0.00036911
67 | 0.0015938 | 0.00039946
68 | 0.0016075 | 0.00040287
69 | 0.0016455 | 0.0004124
70 | 0.0067598 | 0.0016942
71 | 0.0046489 | 0.0011651
72 | 0.001538 | 0.00038547
73 | 0.0032754 | 0.00082089
74 | 0.0011694 | 0.00029307
75 | 0.0019784 | 0.00049584
76 | 0.0014097 | 0.0003533
77 | 0.0015774 | 0.00039533
78 | 0.0021879 | 0.00054834
79 | 0.0039557 | 0.00099139
80 | 0.0057538 | 0.001442
81 | 0.033242 | 0.0083311
82 | 0.001821 | 0.00045637
83 | 0.0086636 | 0.0021713
84 | 0.0014209 | 0.00035611
85 | 0.0014208 | 0.00035608
86 | 0.0049854 | 0.0012495
87 | 0.0084466 | 0.0021169
88 | 0.0090023 | 0.0022562
89 | 0.011338 | 0.0028415
90 | 0.0012714 | 0.00031863
91 | 0.0014175 | 0.00035526
92 | 0.011543 | 0.0028928
93 | 0.012217 | 0.0030619
94 | 0.011551 | 0.0028951
95 | 0.0024833 | 0.00062237
96 | 0.0032267 | 0.00080868
97 | 0.0018729 | 0.00046939

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1