## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_199-12_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_199-12_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_199-12_0_2_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_199-12_0_2_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_199-12_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_199-12_0_2_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_199-12_0_2_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_199-12_0_2_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_199-12_0_2_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_199-12_0_2_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_199-12_0_2_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_199-12_0_2_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_199-12_0_2_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_199-12_0_2_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_199-12_0_2_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_199-12_0_2_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_199-12_0_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_199-12_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_199-12_0_2_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_199-12_0_2_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_199-12_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_199-12_0_2_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_199-12_0_2_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_199-12_0_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_199-12_0_2_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_199-12_0_2_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_199-12_0_2_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_199-12_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_MV_502_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_199-12_0_2_load_0 | 0 | 0.0075338 | 0.0018881 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_199-12_0_2_load_4 | 2 | 0.00043048 | 0.00010789 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_199-12_0_2_load_7 | 3 | 0.00055233 | 0.00013843 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_199-12_0_2_load_5 | 4 | 0.0023758 | 0.00059542 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_199-12_0_2_load_6 | 5 | 0.00010719 | 2.6864e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_199-12_0_2_load_8 | 6 | 0.001717 | 0.00043032 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_199-12_0_2_load_10 | 7 | 0.00042499 | 0.00010651 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_199-12_0_2_load_9 | 8 | 0.00048164 | 0.00012071 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_199-12_0_2_load_12 | 10 | 0.0044189 | 0.0011075 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_199-12_0_2_load_30 | 12 | 0.0022485 | 0.00056352 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_199-12_0_2_load_28 | 13 | 0.0021586 | 0.000541 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_199-12_0_2_load_13 | 14 | 0.00039567 | 9.9165e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_199-12_0_2_load_14 | 15 | 0.0027538 | 0.00069017 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_199-12_0_2_load_15 | 16 | 0.0036835 | 0.00092317 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_199-12_0_2_load_16 | 17 | 0.039454 | 0.0098881 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_199-12_0_2_load_17 | 19 | 0.001414 | 0.00035438 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_199-12_0_2_load_18 | 20 | 0.001228 | 0.00030777 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_199-12_0_2_load_21 | 23 | 0.00056172 | 0.00014078 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_199-12_0_2_load_23 | 25 | 0.0023858 | 0.00059794 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_199-12_0_2_load_25 | 26 | 0.0005326 | 0.00013348 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_199-12_0_2_load_24 | 27 | 0.0038605 | 0.00096752 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_199-12_0_2_line_0 |  | 0 | 1 | 0.032853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_199-12_0_2_line_1 |  | 1 | 2 | 0.0076279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_199-12_0_2_line_2 |  | 2 | 3 | 0.0046937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_199-12_0_2_line_3 |  | 3 | 4 | 0.014609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_199-12_0_2_line_4 |  | 4 | 5 | 0.011652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_199-12_0_2_line_5 |  | 5 | 6 | 0.0013151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_199-12_0_2_line_6 |  | 6 | 7 | 0.02039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_199-12_0_2_line_7 |  | 7 | 8 | 0.035218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_199-12_0_2_line_8 |  | 8 | 9 | 0.14756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_199-12_0_2_line_9 |  | 9 | 10 | 0.066565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_199-12_0_2_line_10 |  | 10 | 11 | 0.028823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_199-12_0_2_line_11 |  | 11 | 12 | 0.046861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_199-12_0_2_line_12 |  | 11 | 13 | 0.097732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_199-12_0_2_line_13 |  | 12 | 17 | 0.030952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_199-12_0_2_line_14 |  | 14 | 15 | 0.002544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_199-12_0_2_line_15 |  | 14 | 16 | 0.038275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_199-12_0_2_line_16 |  | 15 | 17 | 0.029744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_199-12_0_2_line_17 |  | 16 | 18 | 0.46837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_199-12_0_2_line_18 |  | 18 | 23 | 0.20967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_199-12_0_2_line_19 |  | 19 | 20 | 0.060919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_199-12_0_2_line_20 |  | 19 | 21 | 0.055676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_199-12_0_2_line_21 |  | 20 | 22 | 0.034143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_199-12_0_2_line_22 |  | 21 | 23 | 0.025579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_199-12_0_2_line_23 |  | 21 | 24 | 0.09638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_199-12_0_2_line_24 |  | 22 | 25 | 0.046392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_199-12_0_2_line_25 |  | 24 | 26 | 0.16539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_199-12_0_2_line_26 |  | 25 | 27 | 0.0038797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_199-12_0_2_trafo_14 | 0.63 MVA 20/0.4 kV | 28 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2694745.722 | 1248740.0606 | 2694738.4678 | 1248722.8314 | 2694732.1443 | 1248710.1628
1 | 2694745.722 | 1248740.0606 | 2694748.1439 | 1248747.2937
2 | 2694748.1439 | 1248747.2937 | 2694749.2567 | 1248751.8536
3 | 2694752.1365 | 1248766.1661 | 2694750.7593 | 1248758.0104 | 2694749.2567 | 1248751.8536
4 | 2694752.1365 | 1248766.1661 | 2694753.5534 | 1248774.5567 | 2694753.7468 | 1248777.6938
5 | 2694753.8277 | 1248779.0064 | 2694753.7468 | 1248777.6938
6 | 2694753.8277 | 1248779.0064 | 2694754.6567 | 1248792.4548 | 2694754.7501 | 1248799.3702
7 | 2694754.2553 | 1248834.5793 | 2694754.8815 | 1248809.0934 | 2694754.7501 | 1248799.3702
8 | 2694770.6181 | 1248980.6102 | 2694767.3341 | 1248964.4897 | 2694761.1013 | 1248935.8347 | 2694757.6184 | 1248914.6739 | 2694754.8276 | 1248894.625 | 2694754.0313 | 1248884.9159 | 2694753.7801 | 1248875.5936 | 2694753.54 | 1248863.6917 | 2694754.2553 | 1248834.5793
9 | 2694770.6181 | 1248980.6102 | 2694835.8576 | 1248967.392
10 | 2694864.1063 | 1248961.6685 | 2694835.8576 | 1248967.392
11 | 2694864.1063 | 1248961.6685 | 2694910.0339 | 1248952.3605
12 | 2694864.1063 | 1248961.6685 | 2694874.3592 | 1249009.0024 | 2694826.0816 | 1249018.9951
13 | 2694940.3694 | 1248946.2125 | 2694910.0339 | 1248952.3605
14 | 2694969.5208 | 1248940.3045 | 2694972.0141 | 1248939.7992
15 | 2695009.5263 | 1248932.1967 | 2694972.0141 | 1248939.7992
16 | 2694940.3694 | 1248946.2125 | 2694969.5208 | 1248940.3045
17 | 2695009.5263 | 1248932.1967 | 2695473.3753 | 1248997.0871
18 | 2695473.3753 | 1248997.0871 | 2695477.9719 | 1249003.8107 | 2695492.2338 | 1249017.173 | 2695514.627 | 1249044.2546 | 2695533.2378 | 1249066.1046 | 2695596.8101 | 1249135.8499 | 2695602.6221 | 1249142.5822 | 2695605.1623 | 1249146.6262 | 2695607.1373 | 1249151.0615 | 2695608.6381 | 1249156.0909
19 | 2695562.1991 | 1249196.703 | 2695503.8444 | 1249214.1912
20 | 2695615.532 | 1249180.7198 | 2695562.1991 | 1249196.703
21 | 2695471.1382 | 1249223.9928 | 2695503.8444 | 1249214.1912
22 | 2695615.532 | 1249180.7198 | 2695612.052 | 1249167.5313 | 2695608.6381 | 1249156.0909
23 | 2695615.532 | 1249180.7198 | 2695682.6367 | 1249160.6759 | 2695692.4899 | 1249185.1093
24 | 2695471.1382 | 1249223.9928 | 2695476.7989 | 1249242.4649 | 2695457.6907 | 1249261.6417
25 | 2695692.4899 | 1249185.1093 | 2695574.886 | 1249301.4016
26 | 2695454.9523 | 1249264.3899 | 2695457.6907 | 1249261.6417

## bus_geodata
| x | y | coords
0 | 2694732.1443 | 1248710.1628
1 | 2694745.722 | 1248740.0606
2 | 2694748.1439 | 1248747.2937
3 | 2694749.2567 | 1248751.8536
4 | 2694752.1365 | 1248766.1661
5 | 2694753.7468 | 1248777.6938
6 | 2694753.8277 | 1248779.0064
7 | 2694754.7501 | 1248799.3702
8 | 2694754.2553 | 1248834.5793
9 | 2694770.6181 | 1248980.6102
10 | 2694835.8576 | 1248967.392
11 | 2694864.1063 | 1248961.6685
12 | 2694910.0339 | 1248952.3605
13 | 2694826.0816 | 1249018.9951
14 | 2694972.0141 | 1248939.7992
15 | 2694969.5208 | 1248940.3045
16 | 2695009.5263 | 1248932.1967
17 | 2694940.3694 | 1248946.2125
18 | 2695473.3753 | 1248997.0871
19 | 2695562.1991 | 1249196.703
20 | 2695503.8444 | 1249214.1912
21 | 2695615.532 | 1249180.7198
22 | 2695471.1382 | 1249223.9928
23 | 2695608.6381 | 1249156.0909
24 | 2695692.4899 | 1249185.1093
25 | 2695457.6907 | 1249261.6417
26 | 2695574.886 | 1249301.4016
27 | 2695454.9523 | 1249264.3899
28 | 2695009.5263 | 1248932.1967

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99247 | -0.14496 | 0.0075338 | 0.0018881
1 | 0.9927 | -0.14058 | 0 | 0
2 | 0.99275 | -0.13956 | 0.00043048 | 0.00010789
3 | 0.99279 | -0.1389 | 0.00055233 | 0.00013843
4 | 0.9929 | -0.1367 | 0.0023758 | 0.00059542
5 | 0.99302 | -0.13445 | 0.00010719 | 2.6864e-05
6 | 0.99303 | -0.1342 | 0.001717 | 0.00043032
7 | 0.99327 | -0.12962 | 0.00042499 | 0.00010651
8 | 0.99369 | -0.12144 | 0.00048164 | 0.00012071
9 | 0.99553 | -0.086006 | 0 | 0
10 | 0.99635 | -0.07006 | 0.0044189 | 0.0011075
11 | 0.99683 | -0.060928 | 0 | 0
12 | 0.99769 | -0.044324 | 0.0022485 | 0.00056352
13 | 0.99664 | -0.064632 | 0.0021586 | 0.000541
14 | 0.99997 | -0.00062532 | 0.00039567 | 9.9165e-05
15 | 1 | 0 | -0.077868 | -0.019178
16 | 0.99949 | -0.0097734 | 0.0036835 | 0.00092317
17 | 0.99833 | -0.032155 | 0.039454 | 0.0098881
18 | 0.99522 | -0.091953 | 0 | 0
19 | 0.99263 | -0.14195 | 0.001414 | 0.00035438
20 | 0.99222 | -0.15001 | 0.001228 | 0.00030777
21 | 0.99309 | -0.13319 | 0 | 0
22 | 0.99202 | -0.15379 | 0 | 0
23 | 0.99331 | -0.12893 | 0.00056172 | 0.00014078
24 | 0.99304 | -0.13411 | 0 | 0
25 | 0.99176 | -0.15892 | 0.0023858 | 0.00059794
26 | 0.99296 | -0.13568 | 0.0005326 | 0.00013348
27 | 0.99174 | -0.15919 | 0.0038605 | 0.00096752
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0075338 | -0.0018881 | 0.0075354 | 0.0018887 | 1.5718e-06 | 5.8133e-07 | 0.011295 | 0.011295 | 0.011295 | 0.99247 | -0.14496 | 0.9927 | -0.14058 | 3.1031
1 | -0.0075354 | -0.0018887 | 0.0075357 | 0.0018889 | 3.6494e-07 | 1.3494e-07 | 0.011295 | 0.011295 | 0.011295 | 0.9927 | -0.14058 | 0.99275 | -0.13956 | 3.1031
2 | -0.0079662 | -0.0019967 | 0.0079665 | 0.0019968 | 2.5095e-07 | 9.9917e-08 | 0.01194 | 0.01194 | 0.01194 | 0.99275 | -0.13956 | 0.99279 | -0.1389 | 3.2803
3 | -0.0085188 | -0.0021353 | 0.0085197 | 0.0021357 | 8.9311e-07 | 3.8267e-07 | 0.012768 | 0.012768 | 0.012768 | 0.99279 | -0.1389 | 0.9929 | -0.1367 | 3.5078
4 | -0.010895 | -0.0027311 | 0.010897 | 0.0027317 | 1.1651e-06 | 5.9491e-07 | 0.016329 | 0.016329 | 0.016329 | 0.9929 | -0.1367 | 0.99302 | -0.13445 | 4.4859
5 | -0.011004 | -0.0027585 | 0.011004 | 0.0027586 | 1.3408e-07 | 6.8801e-08 | 0.016489 | 0.016489 | 0.016489 | 0.99302 | -0.13445 | 0.99303 | -0.1342 | 4.53
6 | -0.012721 | -0.0031889 | 0.012724 | 0.0031904 | 2.7784e-06 | 1.5143e-06 | 0.019062 | 0.019062 | 0.019062 | 0.99303 | -0.1342 | 0.99327 | -0.12962 | 5.2368
7 | -0.013149 | -0.003297 | 0.013154 | 0.0032998 | 5.1246e-06 | 2.8237e-06 | 0.019699 | 0.019699 | 0.019699 | 0.99327 | -0.12962 | 0.99369 | -0.12144 | 5.4117
8 | -0.013635 | -0.0034205 | 0.013659 | 0.0034333 | 2.3072e-05 | 1.2851e-05 | 0.02042 | 0.020419 | 0.02042 | 0.99369 | -0.12144 | 0.99553 | -0.086006 | 5.6098
9 | -0.013659 | -0.0034333 | 0.013669 | 0.0034391 | 1.0407e-05 | 5.7946e-06 | 0.020419 | 0.020419 | 0.020419 | 0.99553 | -0.086006 | 0.99635 | -0.07006 | 5.6096
10 | -0.018088 | -0.0045466 | 0.018096 | 0.0045513 | 7.89e-06 | 4.6741e-06 | 0.027018 | 0.027018 | 0.027018 | 0.99635 | -0.07006 | 0.99683 | -0.060928 | 7.4226
11 | -0.020255 | -0.0050913 | 0.020271 | 0.0051009 | 1.607e-05 | 9.6735e-06 | 0.030241 | 0.03024 | 0.030241 | 0.99683 | -0.060928 | 0.99769 | -0.044324 | 8.3078
12 | 0.002159 | 0.00053997 | -0.0021586 | -0.000541 | 3.8063e-07 | -1.0302e-06 | 0.0032225 | 0.0032229 | 0.0032229 | 0.99683 | -0.060928 | 0.99664 | -0.064632 | 0.88542
13 | -0.022519 | -0.0056645 | 0.022532 | 0.0056724 | 1.3099e-05 | 7.979e-06 | 0.033594 | 0.033594 | 0.033594 | 0.99769 | -0.044324 | 0.99833 | -0.032155 | 9.2291
14 | -0.014136 | -0.0035561 | 0.014136 | 0.0035563 | 4.2232e-07 | 2.3691e-07 | 0.02104 | 0.02104 | 0.02104 | 0.99997 | -0.00062532 | 1 | 0 | 5.7802
15 | 0.01374 | 0.0034569 | -0.013734 | -0.0034536 | 6.0033e-06 | 3.3402e-06 | 0.020451 | 0.020451 | 0.020451 | 0.99997 | -0.00062532 | 0.99949 | -0.0097734 | 5.6185
16 | 0.062081 | 0.015621 | -0.061986 | -0.01556 | 9.523e-05 | 6.0558e-05 | 0.0924 | 0.0924 | 0.0924 | 1 | 0 | 0.99833 | -0.032155 | 25.3846
17 | 0.010051 | 0.0025304 | -0.010012 | -0.0025113 | 3.9353e-05 | 1.9074e-05 | 0.014967 | 0.01497 | 0.01497 | 0.99949 | -0.0097734 | 0.99522 | -0.091953 | 4.1125
18 | 0.010012 | 0.0025113 | -0.0099939 | -0.0025028 | 1.7621e-05 | 8.5581e-06 | 0.01497 | 0.014971 | 0.014971 | 0.99522 | -0.091953 | 0.99331 | -0.12893 | 4.1128
19 | 0.0074799 | 0.0018749 | -0.007477 | -0.0018739 | 2.8723e-06 | 1.0511e-06 | 0.011213 | 0.011213 | 0.011213 | 0.99263 | -0.14195 | 0.99222 | -0.15001 | 3.0805
20 | -0.0088939 | -0.0022293 | 0.0088976 | 0.002231 | 3.7113e-06 | 1.6552e-06 | 0.013333 | 0.013332 | 0.013333 | 0.99263 | -0.14195 | 0.99309 | -0.13319 | 3.6628
21 | 0.006249 | 0.0015661 | -0.0062479 | -0.0015658 | 1.1245e-06 | 2.7878e-07 | 0.0093715 | 0.0093717 | 0.0093717 | 0.99222 | -0.15001 | 0.99202 | -0.15379 | 2.5746
22 | -0.0094303 | -0.0023611 | 0.0094322 | 0.002362 | 1.9149e-06 | 8.9451e-07 | 0.014129 | 0.014129 | 0.014129 | 0.99309 | -0.13319 | 0.99331 | -0.12893 | 3.8817
23 | 0.00053267 | 0.00013014 | -0.00053264 | -0.00013137 | 2.2968e-08 | -1.2322e-06 | 0.00079696 | 0.00079739 | 0.00079739 | 0.99309 | -0.13319 | 0.99304 | -0.13411 | 0.21906
24 | 0.0062479 | 0.0015658 | -0.0062463 | -0.0015654 | 1.528e-06 | 3.791e-07 | 0.0093717 | 0.0093719 | 0.0093719 | 0.99202 | -0.15379 | 0.99176 | -0.15892 | 2.5747
25 | 0.00053264 | 0.00013137 | -0.0005326 | -0.00013348 | 3.9473e-08 | -2.1143e-06 | 0.00079739 | 0.00079814 | 0.00079814 | 0.99304 | -0.13411 | 0.99296 | -0.13568 | 0.21927
26 | 0.0038605 | 0.0009675 | -0.0038605 | -0.00096752 | 4.8811e-08 | -1.8823e-08 | 0.0057922 | 0.0057923 | 0.0057923 | 0.99176 | -0.15892 | 0.99174 | -0.15919 | 1.5913

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.080622 | 0.019868

## res_load
| p_mw | q_mvar
0 | 0.0075338 | 0.0018881
1 | 0.00043048 | 0.00010789
2 | 0.00055233 | 0.00013843
3 | 0.0023758 | 0.00059542
4 | 0.00010719 | 2.6864e-05
5 | 0.001717 | 0.00043032
6 | 0.00042499 | 0.00010651
7 | 0.00048164 | 0.00012071
8 | 0.0044189 | 0.0011075
9 | 0.0022485 | 0.00056352
10 | 0.0021586 | 0.000541
11 | 0.00039567 | 9.9165e-05
12 | 0.0027538 | 0.00069017
13 | 0.0036835 | 0.00092317
14 | 0.039454 | 0.0098881
15 | 0.001414 | 0.00035438
16 | 0.001228 | 0.00030777
17 | 0.00056172 | 0.00014078
18 | 0.0023858 | 0.00059794
19 | 0.0005326 | 0.00013348
20 | 0.0038605 | 0.00096752

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1