## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_199-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_199-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_199-2_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_199-2_0_3_node_128 | 0.4 | n |  | TRUE
4 | bus_LV_199-2_0_3_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_199-2_0_3_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_199-2_0_3_node_39 | 0.4 | n |  | TRUE
7 | bus_LV_199-2_0_3_node_129 | 0.4 | n |  | TRUE
8 | bus_LV_199-2_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_199-2_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_199-2_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_199-2_0_3_node_135 | 0.4 | n |  | TRUE
12 | bus_LV_199-2_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_199-2_0_3_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_199-2_0_3_node_117 | 0.4 | n |  | TRUE
15 | bus_LV_199-2_0_3_node_105 | 0.4 | n |  | TRUE
16 | bus_LV_199-2_0_3_node_127 | 0.4 | n |  | TRUE
17 | bus_LV_199-2_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_199-2_0_3_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_199-2_0_3_node_107 | 0.4 | n |  | TRUE
20 | bus_LV_199-2_0_3_node_134 | 0.4 | n |  | TRUE
21 | bus_LV_199-2_0_3_node_133 | 0.4 | n |  | TRUE
22 | bus_LV_199-2_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_199-2_0_3_node_112 | 0.4 | n |  | TRUE
24 | bus_LV_199-2_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_199-2_0_3_node_102 | 0.4 | n |  | TRUE
26 | bus_LV_199-2_0_3_node_103 | 0.4 | n |  | TRUE
27 | bus_LV_199-2_0_3_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_199-2_0_3_node_106 | 0.4 | n |  | TRUE
29 | bus_LV_199-2_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_199-2_0_3_node_104 | 0.4 | n |  | TRUE
31 | bus_LV_199-2_0_3_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_199-2_0_3_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_199-2_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_199-2_0_3_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_199-2_0_3_node_110 | 0.4 | n |  | TRUE
36 | bus_LV_199-2_0_3_node_100 | 0.4 | n |  | TRUE
37 | bus_LV_199-2_0_3_node_101 | 0.4 | n |  | TRUE
38 | bus_LV_199-2_0_3_node_115 | 0.4 | n |  | TRUE
39 | bus_LV_199-2_0_3_node_116 | 0.4 | n |  | TRUE
40 | bus_MV_502_0_node_137 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_199-2_0_3_load_0 | 0 | 0.042062 | 0.010542 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_199-2_0_3_load_128 | 3 | 0.0030054 | 0.00075321 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_199-2_0_3_load_39 | 6 | 0.091282 | 0.022878 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_199-2_0_3_load_129 | 7 | 0.00095146 | 0.00023846 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_199-2_0_3_load_135 | 11 | 0.0043672 | 0.0010945 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_199-2_0_3_load_117 | 14 | 0.0088887 | 0.0022277 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_199-2_0_3_load_105 | 15 | 0.0076182 | 0.0019093 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_199-2_0_3_load_127 | 16 | 0.0076282 | 0.0019118 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_199-2_0_3_load_107 | 19 | 0.097807 | 0.024513 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_199-2_0_3_load_134 | 20 | 0.016218 | 0.0040645 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_199-2_0_3_load_133 | 21 | 0.023597 | 0.0059139 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_199-2_0_3_load_102 | 25 | 0.0027701 | 0.00069425 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_199-2_0_3_load_103 | 26 | 0.0024175 | 0.00060589 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_199-2_0_3_load_106 | 28 | 0.0044519 | 0.0011158 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_199-2_0_3_load_104 | 30 | 0.002949 | 0.00073909 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_199-2_0_3_load_34 | 32 | 0.024927 | 0.0062473 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_199-2_0_3_load_110 | 35 | 0.0052959 | 0.0013273 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_199-2_0_3_load_100 | 36 | 0.027139 | 0.0068018 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_199-2_0_3_load_101 | 37 | 0.0041316 | 0.0010355 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_199-2_0_3_load_115 | 38 | 0.005297 | 0.0013276 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_199-2_0_3_load_116 | 39 | 0.0063599 | 0.0015939 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_199-2_0_3_line_0 |  | 0 | 1 | 0.08416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_199-2_0_3_line_1 |  | 1 | 2 | 0.065783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_199-2_0_3_line_2 |  | 2 | 5 | 0.020255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_199-2_0_3_line_3 |  | 2 | 6 | 0.052647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_199-2_0_3_line_4 |  | 3 | 4 | 0.010886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_199-2_0_3_line_5 |  | 4 | 15 | 0.022803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_199-2_0_3_line_6 |  | 4 | 16 | 0.033562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_199-2_0_3_line_7 |  | 5 | 36 | 0.042267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_199-2_0_3_line_8 |  | 7 | 8 | 0.017243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_199-2_0_3_line_9 |  | 7 | 9 | 0.042772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_199-2_0_3_line_10 |  | 8 | 12 | 0.032461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_199-2_0_3_line_11 |  | 9 | 10 | 0.031785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_199-2_0_3_line_12 |  | 10 | 11 | 0.005011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_199-2_0_3_line_13 |  | 12 | 13 | 0.041467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_199-2_0_3_line_14 |  | 12 | 14 | 0.029842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_199-2_0_3_line_15 |  | 13 | 21 | 0.029744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_199-2_0_3_line_16 |  | 14 | 22 | 0.034617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_199-2_0_3_line_17 |  | 15 | 29 | 0.027706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_199-2_0_3_line_18 |  | 17 | 18 | 0.093817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_199-2_0_3_line_19 |  | 17 | 19 | 0.068702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_199-2_0_3_line_20 |  | 18 | 24 | 0.030415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_199-2_0_3_line_21 |  | 18 | 25 | 0.0422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_199-2_0_3_line_22 |  | 18 | 26 | 0.038139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_199-2_0_3_line_23 |  | 20 | 21 | 0.037081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_199-2_0_3_line_24 |  | 22 | 23 | 0.002865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_199-2_0_3_line_25 |  | 23 | 39 | 0.022105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_199-2_0_3_line_26 |  | 24 | 27 | 0.039157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_199-2_0_3_line_27 |  | 24 | 28 | 0.044088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_199-2_0_3_line_28 |  | 25 | 37 | 5.9392e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_199-2_0_3_line_29 |  | 27 | 31 | 0.076929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_199-2_0_3_line_30 |  | 28 | 29 | 0.028516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_199-2_0_3_line_31 |  | 29 | 30 | 0.0095995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_199-2_0_3_line_32 |  | 31 | 36 | 0.043748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_199-2_0_3_line_33 |  | 31 | 33 | 0.022659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_199-2_0_3_line_34 |  | 32 | 33 | 0.050592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_199-2_0_3_line_35 |  | 33 | 34 | 0.009708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_199-2_0_3_line_36 |  | 34 | 35 | 0.03112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_199-2_0_3_line_37 |  | 35 | 38 | 0.023818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_199-2_0_3_line_38 |  | 38 | 39 | 0.031881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_199-2_0_3_trafo_26 | 0.63 MVA 20/0.4 kV | 40 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2693332.6179 | 1248558.9088 | 2693341.5362 | 1248554.6793 | 2693345.3109 | 1248548.067 | 2693352.3102 | 1248544.3521 | 2693410.9652 | 1248540.9813
1 | 2693332.6179 | 1248558.9088 | 2693334.1906 | 1248585.1647 | 2693336.0025 | 1248591.4425 | 2693339.4468 | 1248603.4058 | 2693340.5325 | 1248612.63 | 2693329.3383 | 1248613.1987
2 | 2693329.3383 | 1248613.1987 | 2693318.0466 | 1248630.0338
3 | 2693329.3383 | 1248613.1987 | 2693321.1362 | 1248607.454 | 2693307.2802 | 1248607.2803 | 2693303.5449 | 1248588.8519 | 2693303.0314 | 1248578.892
4 | 2693138.9355 | 1248511.1933 | 2693139.0486 | 1248513.1299 | 2693136.2837 | 1248521.6383
5 | 2693138.9355 | 1248511.1933 | 2693161.6911 | 1248509.7239
6 | 2693138.9355 | 1248511.1933 | 2693105.4746 | 1248513.7956
7 | 2693318.0466 | 1248630.0338 | 2693293.4711 | 1248631.4593 | 2693292.2787 | 1248629.0053 | 2693291.8977 | 1248622.9836 | 2693283.8769 | 1248619.1544
8 | 2693135.3846 | 1248631.8631 | 2693127.1911 | 1248616.6915
9 | 2693107.4148 | 1248579.1947 | 2693108.1673 | 1248584.6551 | 2693126.6146 | 1248615.624 | 2693127.1911 | 1248616.6915
10 | 2693135.3846 | 1248631.8631 | 2693139.5949 | 1248637.8783 | 2693142.0023 | 1248640.3958 | 2693146.8986 | 1248645.5322 | 2693150.7531 | 1248653.9992 | 2693145.9984 | 1248656.1929
11 | 2693107.4148 | 1248579.1947 | 2693108.5659 | 1248575.1541 | 2693116.0776 | 1248573.4263 | 2693123.6637 | 1248573.2119 | 2693129.2051 | 1248577.6691 | 2693132.2051 | 1248581.8861
12 | 2693132.2051 | 1248581.8861 | 2693127.8239 | 1248584.3413
13 | 2693145.9984 | 1248656.1929 | 2693150.7531 | 1248653.9992 | 2693153.118 | 1248652.98 | 2693162.8709 | 1248651.3654 | 2693177.0197 | 1248651.1653 | 2693186.6371 | 1248650.9608
14 | 2693145.9984 | 1248656.1929 | 2693149.1309 | 1248661.5906 | 2693148.2787 | 1248666.7923 | 2693157.5179 | 1248682.6231
15 | 2693186.6371 | 1248650.9608 | 2693184.7139 | 1248621.2786
16 | 2693168.4743 | 1248713.3452 | 2693170.7732 | 1248705.4753 | 2693160.9722 | 1248688.5417 | 2693157.5179 | 1248682.6231
17 | 2693189.3399 | 1248507.9384 | 2693161.6911 | 1248509.7239
18 | 2693245.0138 | 1248418.4453 | 2693248.224 | 1248466.4102 | 2693249.0745 | 1248479.0777 | 2693249.4842 | 1248485.2 | 2693250.0901 | 1248494.2053 | 2693251.0455 | 1248508.3644 | 2693254.7285 | 1248508.0555
19 | 2693245.0138 | 1248418.4453 | 2693199.8926 | 1248420.9267 | 2693188.2087 | 1248421.8771 | 2693183.7034 | 1248427.8887 | 2693183.9005 | 1248432.1617
20 | 2693242.305 | 1248525.7736 | 2693252.1708 | 1248525.1616 | 2693251.2833 | 1248511.9709 | 2693251.0455 | 1248508.3644 | 2693254.7285 | 1248508.0555
21 | 2693254.7285 | 1248508.0555 | 2693261.0975 | 1248509.8348 | 2693263.3226 | 1248510.5036 | 2693265.6555 | 1248511.997 | 2693269.3693 | 1248515.0022 | 2693271.4943 | 1248516.2699 | 2693273.3306 | 1248516.688 | 2693279.5241 | 1248516.6632 | 2693294.6519 | 1248515.6058
22 | 2693254.7285 | 1248508.0555 | 2693259.7453 | 1248505.5324 | 2693262.4456 | 1248503.8403 | 2693264.3874 | 1248501.8693 | 2693265.4281 | 1248500.051 | 2693268.2011 | 1248492.2998 | 2693268.734 | 1248491.552 | 2693269.6861 | 1248491.0444 | 2693283.9003 | 1248490.1024
23 | 2693182.3162 | 1248584.2752 | 2693184.7139 | 1248621.2786
24 | 2693168.4743 | 1248713.3452 | 2693169.8546 | 1248715.8577
25 | 2693169.8546 | 1248715.8577 | 2693189.1048 | 1248704.993
26 | 2693242.305 | 1248525.7736 | 2693242.1445 | 1248527.8171 | 2693239.2911 | 1248529.6403 | 2693239.631 | 1248534.9163 | 2693240.3571 | 1248546.3698 | 2693240.7354 | 1248551.1239 | 2693245.3889 | 1248551.0525 | 2693242.5601 | 1248558.0356
27 | 2693242.305 | 1248525.7736 | 2693241.6045 | 1248505.5027 | 2693238.7475 | 1248505.6356 | 2693217.8249 | 1248506.6108
28 | 2693294.7112 | 1248515.6016 | 2693294.6519 | 1248515.6058
29 | 2693242.5601 | 1248558.0356 | 2693249.4732 | 1248634.6473
30 | 2693189.3399 | 1248507.9384 | 2693217.8249 | 1248506.6108
31 | 2693189.3399 | 1248507.9384 | 2693189.4434 | 1248509.9972 | 2693189.9484 | 1248517.5184
32 | 2693249.4732 | 1248634.6473 | 2693274.9229 | 1248632.8574 | 2693276.3971 | 1248630.3676 | 2693276.2614 | 1248624.1162 | 2693283.8769 | 1248619.1544
33 | 2693239.6574 | 1248647.4583 | 2693250.2509 | 1248646.6576 | 2693249.4732 | 1248634.6473
34 | 2693239.6574 | 1248647.4583 | 2693238.6736 | 1248631.2638 | 2693236.1755 | 1248596.9872
35 | 2693239.6574 | 1248647.4583 | 2693229.9485 | 1248648.1951
36 | 2693229.9485 | 1248648.1951 | 2693231.4586 | 1248666.9332 | 2693237.6119 | 1248677.6159
37 | 2693237.6119 | 1248677.6159 | 2693216.8691 | 1248689.323
38 | 2693216.8691 | 1248689.323 | 2693189.1048 | 1248704.993

## bus_geodata
| x | y | coords
0 | 2693410.9652 | 1248540.9813
1 | 2693332.6179 | 1248558.9088
2 | 2693329.3383 | 1248613.1987
3 | 2693136.2837 | 1248521.6383
4 | 2693138.9355 | 1248511.1933
5 | 2693318.0466 | 1248630.0338
6 | 2693303.0314 | 1248578.892
7 | 2693127.1911 | 1248616.6915
8 | 2693135.3846 | 1248631.8631
9 | 2693107.4148 | 1248579.1947
10 | 2693132.2051 | 1248581.8861
11 | 2693127.8239 | 1248584.3413
12 | 2693145.9984 | 1248656.1929
13 | 2693186.6371 | 1248650.9608
14 | 2693157.5179 | 1248682.6231
15 | 2693161.6911 | 1248509.7239
16 | 2693105.4746 | 1248513.7956
17 | 2693245.0138 | 1248418.4453
18 | 2693254.7285 | 1248508.0555
19 | 2693183.9005 | 1248432.1617
20 | 2693182.3162 | 1248584.2752
21 | 2693184.7139 | 1248621.2786
22 | 2693168.4743 | 1248713.3452
23 | 2693169.8546 | 1248715.8577
24 | 2693242.305 | 1248525.7736
25 | 2693294.6519 | 1248515.6058
26 | 2693283.9003 | 1248490.1024
27 | 2693242.5601 | 1248558.0356
28 | 2693217.8249 | 1248506.6108
29 | 2693189.3399 | 1248507.9384
30 | 2693189.9484 | 1248517.5184
31 | 2693249.4732 | 1248634.6473
32 | 2693236.1755 | 1248596.9872
33 | 2693239.6574 | 1248647.4583
34 | 2693229.9485 | 1248648.1951
35 | 2693237.6119 | 1248677.6159
36 | 2693283.8769 | 1248619.1544
37 | 2693294.7112 | 1248515.6016
38 | 2693216.8691 | 1248689.323
39 | 2693189.1048 | 1248704.993
40 | 2693245.3889 | 1248551.0525

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97395 | -0.50139 | 0.042062 | 0.010542
1 | 0.97725 | -0.43657 | 0 | 0
2 | 0.97982 | -0.3862 | 0 | 0
3 | 0.99289 | -0.13546 | 0.0030054 | 0.00075321
4 | 0.99292 | -0.13488 | 0 | 0
5 | 0.98234 | -0.33729 | 0 | 0
6 | 0.97536 | -0.47384 | 0.091282 | 0.022878
7 | 0.97842 | -0.41427 | 0.00095146 | 0.00023846
8 | 0.97851 | -0.4126 | 0 | 0
9 | 0.97825 | -0.41768 | 0 | 0
10 | 0.97812 | -0.4202 | 0 | 0
11 | 0.9781 | -0.4206 | 0.0043672 | 0.0010945
12 | 0.97867 | -0.40946 | 0 | 0
13 | 0.97714 | -0.43955 | 0 | 0
14 | 0.97992 | -0.38498 | 0.0088887 | 0.0022277
15 | 0.99314 | -0.1306 | 0.0076182 | 0.0019093
16 | 0.99269 | -0.13941 | 0.0076282 | 0.0019118
17 | 0.98364 | -0.31247 | 0 | 0
18 | 0.99217 | -0.14859 | 0 | 0
19 | 0.97741 | -0.43429 | 0.097807 | 0.024513
20 | 0.97548 | -0.4722 | 0.016218 | 0.0040645
21 | 0.97604 | -0.46119 | 0.023597 | 0.0059139
22 | 0.98166 | -0.35109 | 0 | 0
23 | 0.9818 | -0.34829 | 0 | 0
24 | 0.99519 | -0.091067 | 0 | 0
25 | 0.9919 | -0.15375 | 0.0027701 | 0.00069425
26 | 0.99208 | -0.15022 | 0.0024175 | 0.00060589
27 | 1 | 0 | -0.39827 | -0.10229
28 | 0.99416 | -0.111 | 0.0044519 | 0.0011158
29 | 0.9936 | -0.12166 | 0 | 0
30 | 0.99358 | -0.12216 | 0.002949 | 0.00073909
31 | 0.99085 | -0.17349 | 0 | 0
32 | 0.98768 | -0.23466 | 0.024927 | 0.0062473
33 | 0.98884 | -0.21216 | 0 | 0
34 | 0.9882 | -0.22445 | 0 | 0
35 | 0.98615 | -0.26396 | 0.0052959 | 0.0013273
36 | 0.98758 | -0.23602 | 0.027139 | 0.0068018
37 | 0.9919 | -0.15375 | 0.0041316 | 0.0010355
38 | 0.9847 | -0.29204 | 0.005297 | 0.0013276
39 | 0.98291 | -0.32671 | 0.0063599 | 0.0015939
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.042062 | -0.010542 | 0.042192 | 0.010624 | 0.00013033 | 8.2362e-05 | 0.064263 | 0.064262 | 0.064263 | 0.97395 | -0.50139 | 0.97725 | -0.43657 | 17.6546
1 | -0.042192 | -0.010624 | 0.042294 | 0.010688 | 0.00010187 | 6.4372e-05 | 0.064262 | 0.064262 | 0.064262 | 0.97725 | -0.43657 | 0.97982 | -0.3862 | 17.6545
2 | -0.13396 | -0.03381 | 0.13427 | 0.034011 | 0.00031462 | 0.0002011 | 0.20352 | 0.20352 | 0.20352 | 0.97982 | -0.3862 | 0.98234 | -0.33729 | 55.9131
3 | 0.091665 | 0.023122 | -0.091282 | -0.022878 | 0.00038289 | 0.00024439 | 0.13926 | 0.13926 | 0.13926 | 0.97982 | -0.3862 | 0.97536 | -0.47384 | 38.2587
4 | -0.0030054 | -0.00075321 | 0.0030054 | 0.00075313 | 8.2815e-08 | -8.7799e-08 | 0.004504 | 0.004504 | 0.004504 | 0.99289 | -0.13546 | 0.99292 | -0.13488 | 1.2374
5 | -0.010635 | -0.0026656 | 0.010637 | 0.0026666 | 2.1722e-06 | 1.0952e-06 | 0.015938 | 0.015938 | 0.015938 | 0.99292 | -0.13488 | 0.99314 | -0.1306 | 4.3787
6 | 0.0076298 | 0.0019124 | -0.0076282 | -0.0019118 | 1.6455e-06 | 6.1915e-07 | 0.011434 | 0.011434 | 0.011434 | 0.99292 | -0.13488 | 0.99269 | -0.13941 | 3.1413
7 | -0.13427 | -0.034011 | 0.13493 | 0.034431 | 0.00065654 | 0.00041965 | 0.20352 | 0.20352 | 0.20352 | 0.98234 | -0.33729 | 0.98758 | -0.23602 | 55.9131
8 | -0.00532 | -0.0013328 | 0.0053204 | 0.0013329 | 4.2325e-07 | 5.4305e-08 | 0.0080906 | 0.0080905 | 0.0080906 | 0.97842 | -0.41427 | 0.97851 | -0.4126 | 2.2227
9 | 0.0043685 | 0.0010944 | -0.0043678 | -0.0010945 | 7.0797e-07 | -8.3994e-08 | 0.0066436 | 0.0066438 | 0.0066438 | 0.97842 | -0.41427 | 0.97825 | -0.41768 | 1.8252
10 | -0.0053204 | -0.0013329 | 0.0053212 | 0.001333 | 7.9679e-07 | 1.0212e-07 | 0.0080905 | 0.0080904 | 0.0080905 | 0.97851 | -0.4126 | 0.97867 | -0.40946 | 2.2227
11 | 0.0043678 | 0.0010945 | -0.0043673 | -0.0010945 | 5.2613e-07 | -6.2278e-08 | 0.0066438 | 0.0066439 | 0.0066439 | 0.97825 | -0.41768 | 0.97812 | -0.4202 | 1.8253
12 | 0.0043673 | 0.0010945 | -0.0043672 | -0.0010945 | 8.2949e-08 | -9.8074e-09 | 0.0066439 | 0.006644 | 0.006644 | 0.97812 | -0.4202 | 0.9781 | -0.4206 | 1.8253
13 | 0.039921 | 0.010046 | -0.039864 | -0.010009 | 5.7319e-05 | 3.6164e-05 | 0.060713 | 0.060713 | 0.060713 | 0.97867 | -0.40946 | 0.97714 | -0.43955 | 16.6794
14 | -0.045243 | -0.011379 | 0.045296 | 0.011412 | 5.2975e-05 | 3.3528e-05 | 0.068803 | 0.068803 | 0.068803 | 0.97867 | -0.40946 | 0.97992 | -0.38498 | 18.902
15 | 0.039864 | 0.010009 | -0.039823 | -0.0099834 | 4.1115e-05 | 2.5941e-05 | 0.060713 | 0.060713 | 0.060713 | 0.97714 | -0.43955 | 0.97604 | -0.46119 | 16.6794
16 | -0.054184 | -0.01364 | 0.054272 | 0.013696 | 8.7928e-05 | 5.5837e-05 | 0.082301 | 0.0823 | 0.082301 | 0.97992 | -0.38498 | 0.98166 | -0.35109 | 22.61
17 | -0.018256 | -0.004576 | 0.018263 | 0.0045806 | 7.7733e-06 | 4.6162e-06 | 0.027353 | 0.027352 | 0.027353 | 0.99314 | -0.1306 | 0.9936 | -0.12166 | 7.5144
18 | -0.098378 | -0.024877 | 0.099158 | 0.025375 | 0.00078003 | 0.00049802 | 0.1489 | 0.1489 | 0.1489 | 0.98364 | -0.31247 | 0.99217 | -0.14859 | 40.907
19 | 0.098378 | 0.024877 | -0.097807 | -0.024513 | 0.00057121 | 0.00036471 | 0.1489 | 0.1489 | 0.1489 | 0.98364 | -0.31247 | 0.97741 | -0.43429 | 40.907
20 | -0.10848 | -0.027711 | 0.10878 | 0.027904 | 0.0003026 | 0.00019327 | 0.16288 | 0.16288 | 0.16288 | 0.99217 | -0.14859 | 0.99519 | -0.091067 | 44.7473
21 | 0.0069035 | 0.0017303 | -0.0069018 | -0.0017297 | 1.6964e-06 | 5.4086e-07 | 0.010354 | 0.010354 | 0.010354 | 0.99217 | -0.14859 | 0.9919 | -0.15375 | 2.8444
22 | 0.0024177 | 0.00060552 | -0.0024175 | -0.00060589 | 1.8804e-07 | -3.7216e-07 | 0.0036259 | 0.0036261 | 0.0036261 | 0.99217 | -0.14859 | 0.99208 | -0.15022 | 0.99617
23 | -0.016218 | -0.0040645 | 0.016226 | 0.0040695 | 8.5101e-06 | 4.9833e-06 | 0.024739 | 0.024739 | 0.024739 | 0.97548 | -0.4722 | 0.97604 | -0.46119 | 6.7963
24 | -0.054272 | -0.013696 | 0.054279 | 0.0137 | 7.2771e-06 | 4.6211e-06 | 0.0823 | 0.0823 | 0.0823 | 0.98166 | -0.35109 | 0.9818 | -0.34829 | 22.61
25 | -0.054279 | -0.0137 | 0.054336 | 0.013736 | 5.6146e-05 | 3.5653e-05 | 0.0823 | 0.0823 | 0.0823 | 0.9818 | -0.34829 | 0.98291 | -0.32671 | 22.61
26 | -0.13448 | -0.034361 | 0.13508 | 0.034742 | 0.00059508 | 0.00038034 | 0.20131 | 0.20131 | 0.20131 | 0.99519 | -0.091067 | 1 | 0 | 55.3054
27 | 0.0257 | 0.0064569 | -0.025675 | -0.0064419 | 2.442e-05 | 1.5056e-05 | 0.038432 | 0.038432 | 0.038432 | 0.99519 | -0.091067 | 0.99416 | -0.111 | 10.5583
28 | 0.0041316 | 0.0010355 | -0.0041316 | -0.0010355 | 8.5357e-10 | -2.192e-10 | 0.0061982 | 0.0061982 | 0.0061982 | 0.9919 | -0.15375 | 0.9919 | -0.15375 | 1.7028
29 | 0.26154 | 0.067545 | -0.25935 | -0.066143 | 0.0021927 | 0.0014013 | 0.38989 | 0.38989 | 0.38989 | 1 | 0 | 0.99085 | -0.17349 | 53.5566
30 | 0.021223 | 0.0053261 | -0.021213 | -0.0053196 | 1.0792e-05 | 6.5376e-06 | 0.031769 | 0.031769 | 0.031769 | 0.99416 | -0.111 | 0.9936 | -0.12166 | 8.7277
31 | 0.0029491 | 0.00073901 | -0.002949 | -0.00073909 | 7.0216e-08 | -7.9392e-08 | 0.0044165 | 0.0044165 | 0.0044165 | 0.9936 | -0.12166 | 0.99358 | -0.12216 | 1.2133
32 | 0.16256 | 0.041545 | -0.16207 | -0.041233 | 0.00049002 | 0.00031249 | 0.24441 | 0.24441 | 0.24441 | 0.99085 | -0.17349 | 0.98758 | -0.23602 | 33.5734
33 | 0.096791 | 0.024598 | -0.096611 | -0.024483 | 0.00017983 | 0.0001148 | 0.14548 | 0.14548 | 0.14548 | 0.99085 | -0.17349 | 0.98884 | -0.21216 | 39.9664
34 | -0.024927 | -0.0062473 | 0.024954 | 0.0062638 | 2.6757e-05 | 1.6476e-05 | 0.037555 | 0.037554 | 0.037555 | 0.98768 | -0.23466 | 0.98884 | -0.21216 | 10.3172
35 | 0.071657 | 0.018219 | -0.071615 | -0.018192 | 4.2403e-05 | 2.7013e-05 | 0.10792 | 0.10792 | 0.10792 | 0.98884 | -0.21216 | 0.9882 | -0.22445 | 29.6493
36 | 0.071615 | 0.018192 | -0.071479 | -0.018106 | 0.00013593 | 8.6595e-05 | 0.10792 | 0.10792 | 0.10792 | 0.9882 | -0.22445 | 0.98615 | -0.26396 | 29.6494
37 | 0.066183 | 0.016778 | -0.066094 | -0.016722 | 8.9199e-05 | 5.6784e-05 | 0.099933 | 0.099933 | 0.099933 | 0.98615 | -0.26396 | 0.9847 | -0.29204 | 27.4541
38 | 0.060797 | 0.015394 | -0.060695 | -0.01533 | 0.00010103 | 6.4256e-05 | 0.091928 | 0.091928 | 0.091928 | 0.9847 | -0.29204 | 0.98291 | -0.32671 | 25.2551

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39827 | 0.10229

## res_load
| p_mw | q_mvar
0 | 0.042062 | 0.010542
1 | 0.0030054 | 0.00075321
2 | 0.091282 | 0.022878
3 | 0.00095146 | 0.00023846
4 | 0.0043672 | 0.0010945
5 | 0.0088887 | 0.0022277
6 | 0.0076182 | 0.0019093
7 | 0.0076282 | 0.0019118
8 | 0.097807 | 0.024513
9 | 0.016218 | 0.0040645
10 | 0.023597 | 0.0059139
11 | 0.0027701 | 0.00069425
12 | 0.0024175 | 0.00060589
13 | 0.0044519 | 0.0011158
14 | 0.002949 | 0.00073909
15 | 0.024927 | 0.0062473
16 | 0.0052959 | 0.0013273
17 | 0.027139 | 0.0068018
18 | 0.0041316 | 0.0010355
19 | 0.005297 | 0.0013276
20 | 0.0063599 | 0.0015939

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1