## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_199-38_1_3_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_199-38_1_3_node_33 | 0.4 | n |  | TRUE
2 | bus_LV_199-38_1_3_node_35 | 0.4 | n |  | TRUE
3 | bus_LV_199-38_1_3_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_199-38_1_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_199-38_1_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_199-38_1_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_199-38_1_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_199-38_1_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_199-38_1_3_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_199-38_1_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_199-38_1_3_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_199-38_1_3_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_199-38_1_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_199-38_1_3_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_199-38_1_3_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_199-38_1_3_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_199-38_1_3_node_77 | 0.4 | n |  | TRUE
18 | bus_LV_199-38_1_3_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_199-38_1_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_199-38_1_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_199-38_1_3_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_199-38_1_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_199-38_1_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_199-38_1_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_199-38_1_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_199-38_1_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_199-38_1_3_node_164 | 0.4 | n |  | TRUE
28 | bus_LV_199-38_1_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_199-38_1_3_node_165 | 0.4 | n |  | TRUE
30 | bus_LV_199-38_1_3_node_156 | 0.4 | n |  | TRUE
31 | bus_LV_199-38_1_3_node_155 | 0.4 | n |  | TRUE
32 | bus_LV_199-38_1_3_node_91 | 0.4 | n |  | TRUE
33 | bus_LV_199-38_1_3_node_172 | 0.4 | n |  | TRUE
34 | bus_LV_199-38_1_3_node_88 | 0.4 | n |  | TRUE
35 | bus_LV_199-38_1_3_node_90 | 0.4 | n |  | TRUE
36 | bus_LV_199-38_1_3_node_87 | 0.4 | n |  | TRUE
37 | bus_LV_199-38_1_3_node_75 | 0.4 | n |  | TRUE
38 | bus_LV_199-38_1_3_node_73 | 0.4 | n |  | TRUE
39 | bus_LV_199-38_1_3_node_76 | 0.4 | n |  | TRUE
40 | bus_LV_199-38_1_3_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_199-38_1_3_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_199-38_1_3_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_199-38_1_3_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_199-38_1_3_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_199-38_1_3_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_199-38_1_3_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_199-38_1_3_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_199-38_1_3_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_199-38_1_3_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_199-38_1_3_node_62 | 0.4 | n |  | TRUE
51 | bus_LV_199-38_1_3_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_199-38_1_3_node_103 | 0.4 | n |  | TRUE
53 | bus_LV_199-38_1_3_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_199-38_1_3_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_199-38_1_3_node_114 | 0.4 | n |  | TRUE
56 | bus_LV_199-38_1_3_node_113 | 0.4 | n |  | TRUE
57 | bus_LV_199-38_1_3_node_107 | 0.4 | n |  | TRUE
58 | bus_LV_199-38_1_3_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_199-38_1_3_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_199-38_1_3_node_111 | 0.4 | n |  | TRUE
61 | bus_LV_199-38_1_3_node_97 | 0.4 | n |  | TRUE
62 | bus_LV_199-38_1_3_node_99 | 0.4 | n |  | TRUE
63 | bus_LV_199-38_1_3_node_96 | 0.4 | n |  | TRUE
64 | bus_LV_199-38_1_3_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_199-38_1_3_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_199-38_1_3_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_199-38_1_3_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_199-38_1_3_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_199-38_1_3_node_105 | 0.4 | n |  | TRUE
70 | bus_LV_199-38_1_3_node_106 | 0.4 | n |  | TRUE
71 | bus_LV_199-38_1_3_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_199-38_1_3_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_199-38_1_3_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_199-38_1_3_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_199-38_1_3_node_93 | 0.4 | n |  | TRUE
76 | bus_LV_199-38_1_3_node_83 | 0.4 | n |  | TRUE
77 | bus_LV_199-38_1_3_node_94 | 0.4 | n |  | TRUE
78 | bus_LV_199-38_1_3_node_84 | 0.4 | n |  | TRUE
79 | bus_LV_199-38_1_3_node_104 | 0.4 | n |  | TRUE
80 | bus_LV_199-38_1_3_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_199-38_1_3_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_199-38_1_3_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_199-38_1_3_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_199-38_1_3_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_199-38_1_3_node_95 | 0.4 | n |  | TRUE
86 | bus_LV_199-38_1_3_node_68 | 0.4 | n |  | TRUE
87 | bus_LV_199-38_1_3_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_199-38_1_3_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_199-38_1_3_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_199-38_1_3_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_199-38_1_3_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_199-38_1_3_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_199-38_1_3_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_199-38_1_3_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_199-38_1_3_node_82 | 0.4 | n |  | TRUE
96 | bus_LV_199-38_1_3_node_92 | 0.4 | n |  | TRUE
97 | bus_LV_199-38_1_3_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_199-38_1_3_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_199-38_1_3_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_199-38_1_3_node_173 | 0.4 | n |  | TRUE
101 | bus_LV_199-38_1_3_node_109 | 0.4 | n |  | TRUE
102 | bus_LV_199-38_1_3_node_108 | 0.4 | n |  | TRUE
103 | bus_LV_199-38_1_3_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_199-38_1_3_node_112 | 0.4 | n |  | TRUE
105 | bus_LV_199-38_1_3_node_157 | 0.4 | n |  | TRUE
106 | bus_LV_199-38_1_3_node_158 | 0.4 | n |  | TRUE
107 | bus_LV_199-38_1_3_node_159 | 0.4 | n |  | TRUE
108 | bus_LV_199-38_1_3_node_160 | 0.4 | n |  | TRUE
109 | bus_LV_199-38_1_3_node_161 | 0.4 | n |  | TRUE
110 | bus_LV_199-38_1_3_node_162 | 0.4 | n |  | TRUE
111 | bus_LV_199-38_1_3_node_163 | 0.4 | n |  | TRUE
112 | bus_LV_199-38_1_3_node_174 | 0.4 | n |  | TRUE
113 | bus_LV_199-38_1_3_node_175 | 0.4 | n |  | TRUE
114 | bus_MV_502_0_node_79 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_199-38_1_3_load_35 | 2 | 0.00082805 | 0.00020753 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_199-38_1_3_load_24 | 3 | 0.0053417 | 0.0013387 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_199-38_1_3_load_6 | 4 | 0.0030968 | 0.00077612 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_199-38_1_3_load_7 | 5 | 0.0031178 | 0.00078139 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_199-38_1_3_load_13 | 10 | 0.002974 | 0.00074535 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_199-38_1_3_load_14 | 11 | 0.0030267 | 0.00075856 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_199-38_1_3_load_34 | 12 | 0.0012004 | 0.00030086 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_199-38_1_3_load_18 | 13 | 0.0023147 | 0.00058012 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_199-38_1_3_load_15 | 14 | 0.0031199 | 0.00078191 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_199-38_1_3_load_32 | 15 | 0.0030267 | 0.00075856 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_199-38_1_3_load_29 | 16 | 0.0029745 | 0.00074548 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_199-38_1_3_load_77 | 17 | 0.0014596 | 0.00036581 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_199-38_1_3_load_20 | 18 | 0.0014788 | 0.00037063 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_199-38_1_3_load_16 | 19 | 0.0030951 | 0.0007757 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_199-38_1_3_load_25 | 20 | 0.0029738 | 0.00074531 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_199-38_1_3_load_28 | 21 | 0.0030306 | 0.00075953 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_199-38_1_3_load_17 | 22 | 0.0031169 | 0.00078116 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_199-38_1_3_load_22 | 25 | 0.0019532 | 0.00048951 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_199-38_1_3_load_23 | 26 | 0.0021015 | 0.00052669 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_199-38_1_3_load_26 | 28 | 0.0016756 | 0.00041995 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_199-38_1_3_load_165 | 29 | 0.0014932 | 0.00037424 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_199-38_1_3_load_156 | 30 | 0.0020794 | 0.00052115 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_199-38_1_3_load_155 | 31 | 0.0018997 | 0.00047611 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_199-38_1_3_load_172 | 33 | 0.0021228 | 0.00053203 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_199-38_1_3_load_90 | 35 | 0.0010466 | 0.0002623 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_199-38_1_3_load_75 | 37 | 0.0084394 | 0.0021151 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_199-38_1_3_load_73 | 38 | 0.0055827 | 0.0013992 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_199-38_1_3_load_76 | 39 | 0.0014558 | 0.00036485 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_199-38_1_3_load_36 | 40 | 0.0026808 | 0.00067187 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_199-38_1_3_load_37 | 41 | 0.0030944 | 0.00077553 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_199-38_1_3_load_39 | 43 | 0.0009411 | 0.00023586 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_199-38_1_3_load_40 | 44 | 0.0014179 | 0.00035535 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_199-38_1_3_load_50 | 48 | 0.0016333 | 0.00040936 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_199-38_1_3_load_47 | 49 | 0.0017906 | 0.00044877 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_199-38_1_3_load_103 | 52 | 0.00089427 | 0.00022413 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_199-38_1_3_load_52 | 53 | 0.0012388 | 0.00031047 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_199-38_1_3_load_46 | 54 | 0.0031754 | 0.00079583 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_199-38_1_3_load_114 | 55 | 0.0012338 | 0.00030922 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_199-38_1_3_load_113 | 56 | 0.0010159 | 0.00025461 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_199-38_1_3_load_107 | 57 | 0.0045023 | 0.0011284 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_199-38_1_3_load_59 | 58 | 0.0028231 | 0.00070753 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_199-38_1_3_load_55 | 59 | 0.0028475 | 0.00071366 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_199-38_1_3_load_111 | 60 | 0.00059072 | 0.00014805 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_199-38_1_3_load_99 | 62 | 0.0033347 | 0.00083576 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_199-38_1_3_load_96 | 63 | 0.0015505 | 0.00038859 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_199-38_1_3_load_48 | 64 | 0.0022786 | 0.00057107 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_199-38_1_3_load_49 | 65 | 0.0021794 | 0.00054621 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_199-38_1_3_load_51 | 66 | 0.0013149 | 0.00032954 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_199-38_1_3_load_53 | 67 | 0.00082545 | 0.00020688 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_199-38_1_3_load_54 | 68 | 0.0013927 | 0.00034904 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_199-38_1_3_load_105 | 69 | 0.0012201 | 0.00030578 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_199-38_1_3_load_106 | 70 | 0.0016839 | 0.00042202 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_199-38_1_3_load_56 | 71 | 0.0018289 | 0.00045835 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_199-38_1_3_load_58 | 72 | 0.0045142 | 0.0011314 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_199-38_1_3_load_60 | 73 | 0.0037748 | 0.00094605 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_199-38_1_3_load_61 | 74 | 0.004067 | 0.0010193 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_199-38_1_3_load_93 | 75 | 0.0012605 | 0.00031592 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_199-38_1_3_load_83 | 76 | 0.0070376 | 0.0017638 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_199-38_1_3_load_94 | 77 | 0.0047763 | 0.0011971 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_199-38_1_3_load_84 | 78 | 0.0050856 | 0.0012746 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_199-38_1_3_load_104 | 79 | 0.002971 | 0.00074461 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_199-38_1_3_load_63 | 80 | 0.001156 | 0.00028973 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_199-38_1_3_load_64 | 81 | 0.0015432 | 0.00038677 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_199-38_1_3_load_65 | 82 | 0.003078 | 0.00077141 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_199-38_1_3_load_66 | 83 | 0.0036743 | 0.00092087 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_199-38_1_3_load_67 | 84 | 0.0038263 | 0.00095897 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_199-38_1_3_load_95 | 85 | 0.001064 | 0.00026666 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_199-38_1_3_load_68 | 86 | 0.0028278 | 0.00070872 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_199-38_1_3_load_69 | 87 | 0.0087254 | 0.0021868 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_199-38_1_3_load_72 | 89 | 0.0071668 | 0.0017962 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_199-38_1_3_load_74 | 90 | 0.0071744 | 0.0017981 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_199-38_1_3_load_78 | 91 | 0.0014561 | 0.00036492 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_199-38_1_3_load_79 | 92 | 0.0014696 | 0.00036831 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_199-38_1_3_load_80 | 93 | 0.0014776 | 0.00037031 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_199-38_1_3_load_81 | 94 | 0.004415 | 0.0011065 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_199-38_1_3_load_82 | 95 | 0.0043451 | 0.001089 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_199-38_1_3_load_92 | 96 | 0.0012817 | 0.00032123 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_199-38_1_3_load_89 | 97 | 0.0037701 | 0.00094488 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_199-38_1_3_load_85 | 98 | 0.0071693 | 0.0017968 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_199-38_1_3_load_86 | 99 | 0.0045456 | 0.0011392 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_199-38_1_3_load_173 | 100 | 0.0038163 | 0.00095645 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_199-38_1_3_load_109 | 101 | 0.00093928 | 0.0002354 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_199-38_1_3_load_108 | 102 | 0.00059031 | 0.00014795 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_199-38_1_3_load_112 | 104 | 0.0013431 | 0.0003366 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_199-38_1_3_load_157 | 105 | 0.0015556 | 0.00038986 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_199-38_1_3_load_159 | 107 | 0.0011262 | 0.00028225 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_199-38_1_3_load_160 | 108 | 0.0011504 | 0.00028831 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_199-38_1_3_load_161 | 109 | 0.0028042 | 0.0007028 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_199-38_1_3_load_162 | 110 | 0.001838 | 0.00046065 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_199-38_1_3_load_163 | 111 | 0.0027371 | 0.00068597 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_199-38_1_3_load_174 | 112 | 0.0017396 | 0.00043599 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_199-38_1_3_load_175 | 113 | 0.0051105 | 0.0012808 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 98 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_199-38_1_3_line_0 |  | 0 | 1 | 0.13342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_199-38_1_3_line_1 |  | 0 | 2 | 0.040801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_199-38_1_3_line_2 |  | 1 | 3 | 0.028422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_199-38_1_3_line_3 |  | 3 | 24 | 0.0054085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_199-38_1_3_line_4 |  | 4 | 5 | 0.00017942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_199-38_1_3_line_5 |  | 5 | 6 | 0.017823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_199-38_1_3_line_6 |  | 6 | 7 | 0.027967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_199-38_1_3_line_7 |  | 6 | 8 | 0.015277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_199-38_1_3_line_8 |  | 7 | 12 | 0.020852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_199-38_1_3_line_9 |  | 8 | 13 | 0.020411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_199-38_1_3_line_10 |  | 8 | 14 | 0.0031855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_199-38_1_3_line_11 |  | 9 | 10 | 0.0031974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_199-38_1_3_line_12 |  | 9 | 11 | 0.0044432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_199-38_1_3_line_13 |  | 10 | 15 | 0.018123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_199-38_1_3_line_14 |  | 11 | 16 | 0.011727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_199-38_1_3_line_15 |  | 12 | 17 | 0.014798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_199-38_1_3_line_16 |  | 13 | 18 | 0.019159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_199-38_1_3_line_17 |  | 14 | 19 | 0.01795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_199-38_1_3_line_18 |  | 15 | 20 | 0.0077308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_199-38_1_3_line_19 |  | 16 | 21 | 0.0077401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_199-38_1_3_line_20 |  | 17 | 39 | 2.3449e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_199-38_1_3_line_21 |  | 18 | 27 | 0.012057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_199-38_1_3_line_22 |  | 19 | 22 | 0.0082018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_199-38_1_3_line_23 |  | 20 | 24 | 0.016457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_199-38_1_3_line_24 |  | 22 | 23 | 0.02318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_199-38_1_3_line_25 |  | 23 | 24 | 0.024939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_199-38_1_3_line_26 |  | 23 | 25 | 0.038128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_199-38_1_3_line_27 |  | 23 | 26 | 0.015493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_199-38_1_3_line_28 |  | 25 | 28 | 0.009071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_199-38_1_3_line_29 |  | 27 | 29 | 0.0077326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_199-38_1_3_line_30 |  | 28 | 30 | 0.016834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_199-38_1_3_line_31 |  | 30 | 31 | 0.0010316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_199-38_1_3_line_32 |  | 31 | 105 | 0.010774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_199-38_1_3_line_33 |  | 32 | 33 | 0.017334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_199-38_1_3_line_34 |  | 32 | 34 | 0.012607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_199-38_1_3_line_35 |  | 33 | 100 | 0.018625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_199-38_1_3_line_36 |  | 34 | 35 | 0.026664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_199-38_1_3_line_37 |  | 34 | 36 | 0.040302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_199-38_1_3_line_38 |  | 35 | 70 | 0.016986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_199-38_1_3_line_39 |  | 36 | 97 | 0.012169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_199-38_1_3_line_40 |  | 36 | 98 | 0.011855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_199-38_1_3_line_41 |  | 37 | 38 | 0.0029293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_199-38_1_3_line_42 |  | 38 | 88 | 0.01812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_199-38_1_3_line_43 |  | 39 | 91 | 0.0014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_199-38_1_3_line_44 |  | 40 | 41 | 0.012673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_199-38_1_3_line_45 |  | 40 | 42 | 0.013947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_199-38_1_3_line_46 |  | 41 | 43 | 0.011388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_199-38_1_3_line_47 |  | 42 | 44 | 0.022178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_199-38_1_3_line_48 |  | 42 | 45 | 0.029998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_199-38_1_3_line_49 |  | 43 | 46 | 0.01626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_199-38_1_3_line_50 |  | 44 | 47 | 0.019488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_199-38_1_3_line_51 |  | 45 | 48 | 0.0097374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_199-38_1_3_line_52 |  | 45 | 49 | 0.026098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_199-38_1_3_line_53 |  | 46 | 50 | 0.012063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_199-38_1_3_line_54 |  | 46 | 51 | 0.00619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_199-38_1_3_line_55 |  | 47 | 52 | 0.0013915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_199-38_1_3_line_56 |  | 48 | 53 | 0.0052479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_199-38_1_3_line_57 |  | 49 | 54 | 0.0040401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_199-38_1_3_line_58 |  | 50 | 57 | 0.033772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_199-38_1_3_line_59 |  | 51 | 58 | 0.01993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_199-38_1_3_line_60 |  | 51 | 59 | 0.017368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_199-38_1_3_line_61 |  | 52 | 60 | 0.012277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_199-38_1_3_line_62 |  | 53 | 67 | 0.01581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_199-38_1_3_line_63 |  | 54 | 64 | 0.02089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_199-38_1_3_line_64 |  | 55 | 56 | 0.015555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_199-38_1_3_line_65 |  | 56 | 103 | 0.0335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_199-38_1_3_line_66 |  | 57 | 79 | 0.013949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_199-38_1_3_line_67 |  | 58 | 74 | 0.011366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_199-38_1_3_line_68 |  | 59 | 71 | 0.010397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_199-38_1_3_line_69 |  | 60 | 101 | 0.0097983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_199-38_1_3_line_70 |  | 61 | 62 | 0.026849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_199-38_1_3_line_71 |  | 61 | 63 | 0.022488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_199-38_1_3_line_72 |  | 62 | 79 | 0.032126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_199-38_1_3_line_73 |  | 64 | 65 | 0.0088115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_199-38_1_3_line_74 |  | 65 | 66 | 0.018122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_199-38_1_3_line_75 |  | 67 | 68 | 0.0081299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_199-38_1_3_line_76 |  | 68 | 69 | 0.0096576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_199-38_1_3_line_77 |  | 69 | 70 | 0.0037692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_199-38_1_3_line_78 |  | 71 | 72 | 0.0050858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_199-38_1_3_line_79 |  | 72 | 73 | 0.0011775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_199-38_1_3_line_80 |  | 73 | 75 | 0.0079419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_199-38_1_3_line_81 |  | 74 | 76 | 0.019235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_199-38_1_3_line_82 |  | 75 | 77 | 0.011471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_199-38_1_3_line_83 |  | 76 | 78 | 0.014006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_199-38_1_3_line_84 |  | 77 | 85 | 0.006578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_199-38_1_3_line_85 |  | 78 | 90 | 0.045199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_199-38_1_3_line_86 |  | 80 | 81 | 0.00021512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_199-38_1_3_line_87 |  | 80 | 82 | 0.0034252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_199-38_1_3_line_88 |  | 81 | 83 | 0.00058094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_199-38_1_3_line_89 |  | 83 | 84 | 0.029183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_199-38_1_3_line_90 |  | 84 | 85 | 0.0039443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_199-38_1_3_line_91 |  | 86 | 87 | 0.005497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_199-38_1_3_line_92 |  | 87 | 88 | 0.024693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_199-38_1_3_line_93 |  | 88 | 89 | 0.030831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_199-38_1_3_line_94 |  | 88 | 90 | 0.014899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_199-38_1_3_line_95 |  | 91 | 92 | 2.4869e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_199-38_1_3_line_96 |  | 92 | 93 | 0.00019462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_199-38_1_3_line_97 |  | 93 | 94 | 0.018045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_199-38_1_3_line_98 |  | 94 | 95 | 0.022559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_199-38_1_3_line_99 |  | 95 | 96 | 0.018734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_199-38_1_3_line_100 |  | 96 | 97 | 0.0021069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_199-38_1_3_line_101 |  | 98 | 99 | 0.00055302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_199-38_1_3_line_102 |  | 100 | 112 | 0.0078167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_199-38_1_3_line_103 |  | 101 | 102 | 0.00083478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_199-38_1_3_line_104 |  | 102 | 103 | 0.020618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_199-38_1_3_line_105 |  | 103 | 104 | 0.020035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_199-38_1_3_line_106 |  | 105 | 106 | 0.0040653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_199-38_1_3_line_107 |  | 106 | 107 | 0.017738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_199-38_1_3_line_108 |  | 106 | 108 | 0.0052007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_199-38_1_3_line_109 |  | 107 | 109 | 0.020973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_199-38_1_3_line_110 |  | 109 | 110 | 0.0052375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_199-38_1_3_line_111 |  | 110 | 111 | 0.0077844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_199-38_1_3_line_112 |  | 112 | 113 | 0.0034497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_199-38_1_3_trafo_85 | 0.63 MVA 20/0.4 kV | 114 | 98 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2693926.1383 | 1251197.7126 | 2693953.3909 | 1251171.5465 | 2693961.5154 | 1251161.9346 | 2693980.8013 | 1251132.5954 | 2693993.4751 | 1251116.0392 | 2693998.2125 | 1251110.5545 | 2694003.2844 | 1251105.3976 | 2694006.4672 | 1251102.7349 | 2694009.8 | 1251100.6084 | 2694014.0656 | 1251098.6968
1 | 2694014.0656 | 1251098.6968 | 2694019.6854 | 1251098.4969 | 2694025.4523 | 1251099.0221 | 2694030.7323 | 1251100.2624 | 2694041.6499 | 1251103.983 | 2694053.3454 | 1251108.1886
2 | 2693926.1383 | 1251197.7126 | 2693923.3793 | 1251200.3153 | 2693916.0249 | 1251208.0269 | 2693910.3671 | 1251214.9093 | 2693907.2272 | 1251218.881
3 | 2693903.8729 | 1251223.1238 | 2693907.2272 | 1251218.881
4 | 2693947.2092 | 1251276.9803 | 2693947.3184 | 1251276.8379
5 | 2693936.3654 | 1251291.1247 | 2693947.2092 | 1251276.9803
6 | 2693955.5654 | 1251311.4114 | 2693953.1062 | 1251307.9698 | 2693948.8375 | 1251302.9538 | 2693936.3654 | 1251291.1247
7 | 2693925.6298 | 1251280.2239 | 2693936.3654 | 1251291.1247
8 | 2693955.5654 | 1251311.4114 | 2693934.7267 | 1251312.1527
9 | 2693925.6298 | 1251280.2239 | 2693919.8236 | 1251282.6671 | 2693905.7297 | 1251283.3783
10 | 2693925.6298 | 1251280.2239 | 2693923.3876 | 1251277.9612
11 | 2693945.1263 | 1251242.3369 | 2693942.2278 | 1251240.987
12 | 2693945.1263 | 1251242.3369 | 2693949.1371 | 1251244.2488
13 | 2693942.2278 | 1251240.987 | 2693925.7989 | 1251233.3355
14 | 2693959.7229 | 1251249.2949 | 2693949.1371 | 1251244.2488
15 | 2693934.7267 | 1251312.1527 | 2693919.9379 | 1251312.6788
16 | 2693905.7297 | 1251283.3783 | 2693886.5947 | 1251284.344
17 | 2693923.3876 | 1251277.9612 | 2693910.7532 | 1251265.2112
18 | 2693918.7909 | 1251230.0717 | 2693925.7989 | 1251233.3355
19 | 2693966.7111 | 1251252.6225 | 2693961.5348 | 1251250.1587 | 2693959.7229 | 1251249.2949
20 | 2693919.9144 | 1251312.6796 | 2693919.9379 | 1251312.6788
21 | 2693874.5532 | 1251284.9516 | 2693886.5947 | 1251284.344
22 | 2693910.7532 | 1251265.2112 | 2693904.9801 | 1251259.3853
23 | 2693903.8729 | 1251223.1238 | 2693918.7909 | 1251230.0717
24 | 2693888.6645 | 1251242.9204 | 2693904.9801 | 1251259.3853
25 | 2693903.8729 | 1251223.1238 | 2693888.6645 | 1251242.9204
26 | 2693888.6645 | 1251242.9204 | 2693867.1393 | 1251211.4497
27 | 2693888.6645 | 1251242.9204 | 2693877.2213 | 1251253.3647
28 | 2693861.8205 | 1251204.1105 | 2693863.6599 | 1251206.3627 | 2693867.1393 | 1251211.4497
29 | 2693874.5532 | 1251284.9516 | 2693866.8283 | 1251285.2959
30 | 2693861.8205 | 1251204.1105 | 2693855.425 | 1251196.2801 | 2693850.5309 | 1251191.669
31 | 2693849.7801 | 1251190.9616 | 2693850.5309 | 1251191.669
32 | 2693849.7801 | 1251190.9616 | 2693841.9381 | 1251183.5732
33 | 2693837.5579 | 1251269.5316 | 2693840.8218 | 1251267.9376 | 2693844.1724 | 1251270.3925 | 2693845.6572 | 1251269.1151 | 2693839.5102 | 1251264.6637
34 | 2693835.2586 | 1251278.8579 | 2693839.6676 | 1251276.9374 | 2693837.8465 | 1251272.7609 | 2693837.5579 | 1251269.5316
35 | 2693839.5102 | 1251264.6637 | 2693834.7307 | 1251261.2026 | 2693830.8269 | 1251256.9708 | 2693825.5542 | 1251252.4172
36 | 2693835.2586 | 1251278.8579 | 2693828.4415 | 1251280.3067 | 2693821.4239 | 1251281.541 | 2693814.2099 | 1251281.8381 | 2693808.873 | 1251281.4811
37 | 2693835.2586 | 1251278.8579 | 2693837.5733 | 1251283.3314 | 2693839.8257 | 1251285.5354 | 2693843.7538 | 1251287.7549 | 2693844.645 | 1251315.357
38 | 2693808.873 | 1251281.4811 | 2693791.925 | 1251280.3472
39 | 2693844.645 | 1251315.357 | 2693856.8059 | 1251314.9244
40 | 2693844.645 | 1251315.357 | 2693832.7958 | 1251315.7183
41 | 2693892.1581 | 1251373.8773 | 2693889.2947 | 1251373.2598
42 | 2693872.4449 | 1251367.9491 | 2693882.0519 | 1251369.5581 | 2693885.4788 | 1251372.4368 | 2693889.2947 | 1251373.2598
43 | 2693919.9144 | 1251312.6796 | 2693918.4313 | 1251312.7323
44 | 2693736.5943 | 1251322.387 | 2693737.6172 | 1251324.259 | 2693742.8935 | 1251333.3833
45 | 2693729.9065 | 1251310.1483 | 2693736.5943 | 1251322.387
46 | 2693742.8935 | 1251333.3833 | 2693745.3398 | 1251337.6137 | 2693748.7234 | 1251343.165
47 | 2693729.9065 | 1251310.1483 | 2693725.4448 | 1251312.0681 | 2693723.2977 | 1251313.224 | 2693721.1743 | 1251314.7916 | 2693719.1814 | 1251317.173 | 2693714.7123 | 1251325.1431
48 | 2693729.9065 | 1251310.1483 | 2693726.1952 | 1251302.3392 | 2693730.2834 | 1251300.1688 | 2693732.77 | 1251297.595 | 2693735.1624 | 1251294.7751 | 2693738.7212 | 1251290.2835 | 2693741.3149 | 1251287.6225
49 | 2693757.186 | 1251357.0494 | 2693748.7234 | 1251343.165
50 | 2693699.6196 | 1251335.9227 | 2693701.5672 | 1251335.9201 | 2693703.4616 | 1251335.472 | 2693706.1093 | 1251334.1684 | 2693709.3915 | 1251331.8852 | 2693711.7763 | 1251329.5433 | 2693713.5882 | 1251327.1479 | 2693714.7123 | 1251325.1431
51 | 2693741.3149 | 1251287.6225 | 2693744.2707 | 1251285.4564 | 2693747.9117 | 1251283.4013 | 2693749.6856 | 1251282.7434
52 | 2693741.3149 | 1251287.6225 | 2693742.4535 | 1251273.3961 | 2693743.4013 | 1251265.0269 | 2693743.9598 | 1251261.6693
53 | 2693746.3732 | 1251362.4604 | 2693748.8003 | 1251361.2645 | 2693757.186 | 1251357.0494
54 | 2693760.3935 | 1251362.3487 | 2693757.186 | 1251357.0494
55 | 2693699.6196 | 1251335.9227 | 2693698.27 | 1251335.5835
56 | 2693749.6856 | 1251282.7434 | 2693753.0298 | 1251281.503 | 2693754.6873 | 1251281.2223
57 | 2693744.6227 | 1251257.6839 | 2693743.9598 | 1251261.6693
58 | 2693746.3732 | 1251362.4604 | 2693743.9813 | 1251363.3454 | 2693741.4042 | 1251364.0052 | 2693738.6479 | 1251364.5398 | 2693735.0023 | 1251364.9824 | 2693731.2767 | 1251364.7567 | 2693727.8008 | 1251364.0122 | 2693723.4201 | 1251362.7309 | 2693718.0073 | 1251360.8327 | 2693713.9986 | 1251359.4126 | 2693713.7738 | 1251359.3269
59 | 2693760.3935 | 1251362.3487 | 2693765.0587 | 1251359.9651 | 2693776.5923 | 1251353.3759 | 2693777.7154 | 1251352.5263 | 2693777.7154 | 1251352.5263
60 | 2693760.3935 | 1251362.3487 | 2693769.3922 | 1251377.2032
61 | 2693698.27 | 1251335.5835 | 2693697.2585 | 1251335.3293 | 2693695.3341 | 1251334.3426 | 2693690.3303 | 1251330.9275 | 2693688.1633 | 1251328.8333
62 | 2693754.6873 | 1251281.2223 | 2693760.8944 | 1251280.1709 | 2693768.9733 | 1251279.6094 | 2693770.3895 | 1251279.6214
63 | 2693744.6227 | 1251257.6839 | 2693746.3381 | 1251247.3708 | 2693746.5928 | 1251243.6831 | 2693746.4341 | 1251240.3558 | 2693746.0519 | 1251236.9695
64 | 2693672.5981 | 1251267.8985 | 2693671.6452 | 1251263.2354 | 2693670.5138 | 1251259.3589 | 2693668.7882 | 1251255.8178 | 2693667.3164 | 1251253.4149
65 | 2693675.4447 | 1251301.2693 | 2693674.0427 | 1251281.5652 | 2693673.4715 | 1251274.7287 | 2693672.5981 | 1251267.8985 | 2693672.5981 | 1251267.8985
66 | 2693713.7738 | 1251359.3269 | 2693705.4519 | 1251356.1527 | 2693700.6248 | 1251354.695
67 | 2693785.9737 | 1251344.9178 | 2693785.9737 | 1251344.9178 | 2693784.0873 | 1251345.822 | 2693782.5112 | 1251347.1425 | 2693778.6653 | 1251351.6518 | 2693777.7154 | 1251352.5263
68 | 2693769.3922 | 1251377.2032 | 2693770.1264 | 1251378.4152 | 2693774.2868 | 1251386.3735
69 | 2693681.7333 | 1251321.4857 | 2693682.7611 | 1251323.1351 | 2693686.5754 | 1251327.2987 | 2693688.1633 | 1251328.8333
70 | 2693642.2888 | 1251349.0378 | 2693651.021 | 1251348.2084 | 2693659.485 | 1251348.1088 | 2693669.0559 | 1251349.0057
71 | 2693642.2888 | 1251349.0378 | 2693635.5508 | 1251350.2656 | 2693629.0679 | 1251352.0645 | 2693622.0294 | 1251354.6331 | 2693620.7325 | 1251355.2081
72 | 2693700.6248 | 1251354.695 | 2693696.8644 | 1251353.5594 | 2693688.4442 | 1251351.8472 | 2693684.5615 | 1251351.0519 | 2693671.1912 | 1251349.2058 | 2693669.0559 | 1251349.0057
73 | 2693746.0519 | 1251236.9695 | 2693745.0636 | 1251228.2136
74 | 2693745.0636 | 1251228.2136 | 2693745.0636 | 1251228.2136 | 2693745.0477 | 1251222.5423 | 2693745.407 | 1251212.7182 | 2693745.1388 | 1251210.1119
75 | 2693778.5192 | 1251279.6906 | 2693770.3895 | 1251279.6214
76 | 2693778.5192 | 1251279.6906 | 2693782.6353 | 1251279.7256 | 2693788.1642 | 1251280.0956
77 | 2693788.1642 | 1251280.0956 | 2693791.925 | 1251280.3472
78 | 2693776.6166 | 1251390.8937 | 2693776.3397 | 1251390.3004 | 2693774.2868 | 1251386.3735
79 | 2693777.1145 | 1251391.9608 | 2693776.6166 | 1251390.8937
80 | 2693777.1145 | 1251391.9608 | 2693780.4732 | 1251399.1575
81 | 2693785.9737 | 1251344.9178 | 2693788.4115 | 1251344.4782 | 2693790.8162 | 1251344.6942 | 2693792.9932 | 1251345.4626 | 2693794.6813 | 1251346.6013 | 2693796.4484 | 1251348.4641 | 2693797.7607 | 1251349.4968 | 2693799.463 | 1251350.2131 | 2693803.2816 | 1251351.0721
82 | 2693785.2884 | 1251409.5687 | 2693784.2761 | 1251407.3059 | 2693780.4732 | 1251399.1575
83 | 2693803.2816 | 1251351.0721 | 2693816.9464 | 1251354.1457
84 | 2693785.2884 | 1251409.5687 | 2693787.8631 | 1251415.3244 | 2693787.9725 | 1251415.5741
85 | 2693857.7521 | 1251365.4781 | 2693840.7632 | 1251362.621 | 2693841.2638 | 1251359.6155 | 2693816.9464 | 1251354.1457
86 | 2693800.0311 | 1251447.2563 | 2693799.9673 | 1251447.0508
87 | 2693801.0462 | 1251450.5276 | 2693800.0311 | 1251447.2563
88 | 2693799.9673 | 1251447.0508 | 2693799.7951 | 1251446.496
89 | 2693789.5554 | 1251419.1868 | 2693791.7682 | 1251424.2375 | 2693798.1573 | 1251441.2185 | 2693799.7951 | 1251446.496
90 | 2693789.5554 | 1251419.1868 | 2693787.9725 | 1251415.5741
91 | 2693864.0573 | 1251390.5121 | 2693860.8963 | 1251395.0094
92 | 2693872.4449 | 1251367.9491 | 2693870.2336 | 1251381.7247 | 2693864.0573 | 1251390.5121
93 | 2693872.4449 | 1251367.9491 | 2693874.7499 | 1251357.3107 | 2693874.9482 | 1251351.4649 | 2693875.494 | 1251344.6572 | 2693878.6686 | 1251342.9728 | 2693882.3592 | 1251343.0313
94 | 2693872.4449 | 1251367.9491 | 2693857.7521 | 1251365.4781
95 | 2693918.4064 | 1251312.7332 | 2693918.4313 | 1251312.7323
96 | 2693918.2119 | 1251312.7402 | 2693918.4064 | 1251312.7332
97 | 2693900.1782 | 1251313.3816 | 2693918.2119 | 1251312.7402
98 | 2693877.6333 | 1251314.1836 | 2693900.1782 | 1251313.3816
99 | 2693877.6333 | 1251314.1836 | 2693858.9114 | 1251314.8496
100 | 2693856.8059 | 1251314.9244 | 2693858.9114 | 1251314.8496
101 | 2693832.2431 | 1251315.7352 | 2693832.7958 | 1251315.7183
102 | 2693825.5542 | 1251252.4172 | 2693825.5542 | 1251252.4172 | 2693819.3121 | 1251257.122
103 | 2693681.7333 | 1251321.4857 | 2693681.2919 | 1251320.7772
104 | 2693675.4447 | 1251301.2693 | 2693675.6917 | 1251303.7862 | 2693676.4393 | 1251309.0243 | 2693677.7515 | 1251313.8821 | 2693679.7941 | 1251318.3735 | 2693681.2919 | 1251320.7772
105 | 2693675.4447 | 1251301.2693 | 2693688.5297 | 1251292.5249 | 2693687.6 | 1251288.3293
106 | 2693838.9793 | 1251180.7854 | 2693841.9381 | 1251183.5732
107 | 2693838.9793 | 1251180.7854 | 2693825.5557 | 1251192.3807
108 | 2693838.9793 | 1251180.7854 | 2693835.2194 | 1251177.1923
109 | 2693809.6838 | 1251206.0907 | 2693825.5557 | 1251192.3807
110 | 2693809.6838 | 1251206.0907 | 2693805.7203 | 1251209.5144
111 | 2693799.8294 | 1251214.6029 | 2693805.7203 | 1251209.5144
112 | 2693815.8625 | 1251257.1007 | 2693819.3121 | 1251257.122

## bus_geodata
| x | y | coords
0 | 2694014.0656 | 1251098.6968
1 | 2693926.1383 | 1251197.7126
2 | 2694053.3454 | 1251108.1886
3 | 2693907.2272 | 1251218.881
4 | 2693947.3184 | 1251276.8379
5 | 2693947.2092 | 1251276.9803
6 | 2693936.3654 | 1251291.1247
7 | 2693955.5654 | 1251311.4114
8 | 2693925.6298 | 1251280.2239
9 | 2693945.1263 | 1251242.3369
10 | 2693942.2278 | 1251240.987
11 | 2693949.1371 | 1251244.2488
12 | 2693934.7267 | 1251312.1527
13 | 2693905.7297 | 1251283.3783
14 | 2693923.3876 | 1251277.9612
15 | 2693925.7989 | 1251233.3355
16 | 2693959.7229 | 1251249.2949
17 | 2693919.9379 | 1251312.6788
18 | 2693886.5947 | 1251284.344
19 | 2693910.7532 | 1251265.2112
20 | 2693918.7909 | 1251230.0717
21 | 2693966.7111 | 1251252.6225
22 | 2693904.9801 | 1251259.3853
23 | 2693888.6645 | 1251242.9204
24 | 2693903.8729 | 1251223.1238
25 | 2693867.1393 | 1251211.4497
26 | 2693877.2213 | 1251253.3647
27 | 2693874.5532 | 1251284.9516
28 | 2693861.8205 | 1251204.1105
29 | 2693866.8283 | 1251285.2959
30 | 2693850.5309 | 1251191.669
31 | 2693849.7801 | 1251190.9616
32 | 2693837.5579 | 1251269.5316
33 | 2693839.5102 | 1251264.6637
34 | 2693835.2586 | 1251278.8579
35 | 2693808.873 | 1251281.4811
36 | 2693844.645 | 1251315.357
37 | 2693892.1581 | 1251373.8773
38 | 2693889.2947 | 1251373.2598
39 | 2693919.9144 | 1251312.6796
40 | 2693736.5943 | 1251322.387
41 | 2693742.8935 | 1251333.3833
42 | 2693729.9065 | 1251310.1483
43 | 2693748.7234 | 1251343.165
44 | 2693714.7123 | 1251325.1431
45 | 2693741.3149 | 1251287.6225
46 | 2693757.186 | 1251357.0494
47 | 2693699.6196 | 1251335.9227
48 | 2693749.6856 | 1251282.7434
49 | 2693743.9598 | 1251261.6693
50 | 2693746.3732 | 1251362.4604
51 | 2693760.3935 | 1251362.3487
52 | 2693698.27 | 1251335.5835
53 | 2693754.6873 | 1251281.2223
54 | 2693744.6227 | 1251257.6839
55 | 2693667.3164 | 1251253.4149
56 | 2693672.5981 | 1251267.8985
57 | 2693713.7738 | 1251359.3269
58 | 2693777.7154 | 1251352.5263
59 | 2693769.3922 | 1251377.2032
60 | 2693688.1633 | 1251328.8333
61 | 2693642.2888 | 1251349.0378
62 | 2693669.0559 | 1251349.0057
63 | 2693620.7325 | 1251355.2081
64 | 2693746.0519 | 1251236.9695
65 | 2693745.0636 | 1251228.2136
66 | 2693745.1388 | 1251210.1119
67 | 2693770.3895 | 1251279.6214
68 | 2693778.5192 | 1251279.6906
69 | 2693788.1642 | 1251280.0956
70 | 2693791.925 | 1251280.3472
71 | 2693774.2868 | 1251386.3735
72 | 2693776.6166 | 1251390.8937
73 | 2693777.1145 | 1251391.9608
74 | 2693785.9737 | 1251344.9178
75 | 2693780.4732 | 1251399.1575
76 | 2693803.2816 | 1251351.0721
77 | 2693785.2884 | 1251409.5687
78 | 2693816.9464 | 1251354.1457
79 | 2693700.6248 | 1251354.695
80 | 2693800.0311 | 1251447.2563
81 | 2693799.9673 | 1251447.0508
82 | 2693801.0462 | 1251450.5276
83 | 2693799.7951 | 1251446.496
84 | 2693789.5554 | 1251419.1868
85 | 2693787.9725 | 1251415.5741
86 | 2693860.8963 | 1251395.0094
87 | 2693864.0573 | 1251390.5121
88 | 2693872.4449 | 1251367.9491
89 | 2693882.3592 | 1251343.0313
90 | 2693857.7521 | 1251365.4781
91 | 2693918.4313 | 1251312.7323
92 | 2693918.4064 | 1251312.7332
93 | 2693918.2119 | 1251312.7402
94 | 2693900.1782 | 1251313.3816
95 | 2693877.6333 | 1251314.1836
96 | 2693858.9114 | 1251314.8496
97 | 2693856.8059 | 1251314.9244
98 | 2693832.7958 | 1251315.7183
99 | 2693832.2431 | 1251315.7352
100 | 2693825.5542 | 1251252.4172
101 | 2693681.7333 | 1251321.4857
102 | 2693681.2919 | 1251320.7772
103 | 2693675.4447 | 1251301.2693
104 | 2693687.6 | 1251288.3293
105 | 2693841.9381 | 1251183.5732
106 | 2693838.9793 | 1251180.7854
107 | 2693825.5557 | 1251192.3807
108 | 2693835.2194 | 1251177.1923
109 | 2693809.6838 | 1251206.0907
110 | 2693805.7203 | 1251209.5144
111 | 2693799.8294 | 1251214.6029
112 | 2693819.3121 | 1251257.122
113 | 2693815.8625 | 1251257.1007
114 | 2693824.4869 | 1251315.9717

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98536 | -0.28149 | 0 | 0
1 | 0.98546 | -0.2795 | 0 | 0
2 | 0.98533 | -0.2821 | 0.00082805 | 0.00020753
3 | 0.98549 | -0.27907 | 0.0053417 | 0.0013387
4 | 0.98914 | -0.20802 | 0.0030968 | 0.00077612
5 | 0.98914 | -0.20801 | 0.0031178 | 0.00078139
6 | 0.98924 | -0.20604 | 0 | 0
7 | 0.99094 | -0.17324 | 0 | 0
8 | 0.9884 | -0.22231 | 0 | 0
9 | 0.98491 | -0.29031 | 0 | 0
10 | 0.98494 | -0.28979 | 0.002974 | 0.00074535
11 | 0.98487 | -0.29103 | 0.0030267 | 0.00075856
12 | 0.9922 | -0.14887 | 0.0012004 | 0.00030086
13 | 0.98831 | -0.22423 | 0.0023147 | 0.00058012
14 | 0.98825 | -0.2254 | 0.0031199 | 0.00078191
15 | 0.98514 | -0.28588 | 0.0030267 | 0.00075856
16 | 0.98481 | -0.29229 | 0.0029745 | 0.00074548
17 | 0.99312 | -0.13129 | 0.0014596 | 0.00036581
18 | 0.98825 | -0.22525 | 0.0014788 | 0.00037063
19 | 0.9874 | -0.24186 | 0.0030951 | 0.0007757
20 | 0.98524 | -0.28379 | 0.0029738 | 0.00074531
21 | 0.98479 | -0.29272 | 0.0030306 | 0.00075953
22 | 0.98703 | -0.24893 | 0.0031169 | 0.00078116
23 | 0.98607 | -0.26766 | 0 | 0
24 | 0.98552 | -0.27847 | 0 | 0
25 | 0.98541 | -0.28053 | 0.0019532 | 0.00048951
26 | 0.98604 | -0.26824 | 0.0021015 | 0.00052669
27 | 0.98824 | -0.22557 | 0 | 0
28 | 0.98527 | -0.28328 | 0.0016756 | 0.00041995
29 | 0.98823 | -0.22578 | 0.0014932 | 0.00037424
30 | 0.98504 | -0.28787 | 0.0020794 | 0.00052115
31 | 0.98502 | -0.28811 | 0.0018997 | 0.00047611
32 | 0.99569 | -0.081359 | 0 | 0
33 | 0.99549 | -0.085258 | 0.0021228 | 0.00053203
34 | 0.99584 | -0.078525 | 0 | 0
35 | 0.99411 | -0.11119 | 0.0010466 | 0.0002623
36 | 0.99868 | -0.024854 | 0 | 0
37 | 0.97052 | -0.56857 | 0.0084394 | 0.0021151
38 | 0.97054 | -0.56812 | 0.0055827 | 0.0013992
39 | 0.99312 | -0.13126 | 0.0014558 | 0.00036485
40 | 0.98066 | -0.36956 | 0.0026808 | 0.00067187
41 | 0.97937 | -0.39455 | 0.0030944 | 0.00077553
42 | 0.9821 | -0.34145 | 0 | 0
43 | 0.97825 | -0.41643 | 0.0009411 | 0.00023586
44 | 0.98194 | -0.34467 | 0.0014179 | 0.00035535
45 | 0.98544 | -0.27695 | 0 | 0
46 | 0.97667 | -0.44747 | 0 | 0
47 | 0.98182 | -0.347 | 0 | 0
48 | 0.98662 | -0.25423 | 0.0016333 | 0.00040936
49 | 0.98518 | -0.28198 | 0.0017906 | 0.00044877
50 | 0.97653 | -0.4502 | 0 | 0
51 | 0.97613 | -0.45791 | 0 | 0
52 | 0.98181 | -0.34716 | 0.00089427 | 0.00022413
53 | 0.98726 | -0.24186 | 0.0012388 | 0.00031047
54 | 0.98515 | -0.28263 | 0.0031754 | 0.00079583
55 | 0.98154 | -0.35246 | 0.0012338 | 0.00030922
56 | 0.98156 | -0.35211 | 0.0010159 | 0.00025461
57 | 0.97614 | -0.45783 | 0.0045023 | 0.0011284
58 | 0.97504 | -0.47942 | 0.0028231 | 0.00070753
59 | 0.9756 | -0.46851 | 0.0028475 | 0.00071366
60 | 0.98175 | -0.34843 | 0.00059072 | 0.00014805
61 | 0.97585 | -0.46347 | 0 | 0
62 | 0.97589 | -0.46271 | 0.0033347 | 0.00083576
63 | 0.97582 | -0.46411 | 0.0015505 | 0.00038859
64 | 0.98504 | -0.2848 | 0.0022786 | 0.00057107
65 | 0.98501 | -0.28535 | 0.0021794 | 0.00054621
66 | 0.98499 | -0.28578 | 0.0013149 | 0.00032954
67 | 0.98922 | -0.20433 | 0.00082545 | 0.00020688
68 | 0.99023 | -0.18497 | 0.0013927 | 0.00034904
69 | 0.99145 | -0.16178 | 0.0012201 | 0.00030578
70 | 0.99193 | -0.15267 | 0.0016839 | 0.00042202
71 | 0.9753 | -0.47432 | 0.0018289 | 0.00045835
72 | 0.97516 | -0.47699 | 0.0045142 | 0.0011314
73 | 0.97514 | -0.47752 | 0.0037748 | 0.00094605
74 | 0.97444 | -0.49112 | 0.004067 | 0.0010193
75 | 0.97499 | -0.48048 | 0.0012605 | 0.00031592
76 | 0.97351 | -0.50952 | 0.0070376 | 0.0017638
77 | 0.97478 | -0.4845 | 0.0047763 | 0.0011971
78 | 0.97292 | -0.52112 | 0.0050856 | 0.0012746
79 | 0.97604 | -0.45983 | 0.002971 | 0.00074461
80 | 0.97439 | -0.49234 | 0.001156 | 0.00028973
81 | 0.97439 | -0.49232 | 0.0015432 | 0.00038677
82 | 0.97438 | -0.49253 | 0.003078 | 0.00077141
83 | 0.97439 | -0.49226 | 0.0036743 | 0.00092087
84 | 0.97465 | -0.4872 | 0.0038263 | 0.00095897
85 | 0.9747 | -0.48624 | 0.001064 | 0.00026666
86 | 0.9705 | -0.56898 | 0.0028278 | 0.00070872
87 | 0.97051 | -0.56869 | 0.0087254 | 0.0021868
88 | 0.97078 | -0.56342 | 0 | 0
89 | 0.97057 | -0.5675 | 0.0071668 | 0.0017962
90 | 0.97123 | -0.5544 | 0.0071744 | 0.0017981
91 | 0.99322 | -0.12942 | 0.0014561 | 0.00036492
92 | 0.99322 | -0.12939 | 0.0014696 | 0.00036831
93 | 0.99323 | -0.12914 | 0.0014776 | 0.00037031
94 | 0.99447 | -0.10543 | 0.004415 | 0.0011065
95 | 0.9961 | -0.074116 | 0.0043451 | 0.001089
96 | 0.99753 | -0.046765 | 0.0012817 | 0.00032123
97 | 0.9977 | -0.043647 | 0.0037701 | 0.00094488
98 | 1 | 0 | -0.25054 | -0.06397
99 | 1 | -4.3814e-05 | 0.0045456 | 0.0011392
100 | 0.99531 | -0.088753 | 0.0038163 | 0.00095645
101 | 0.9817 | -0.34934 | 0.00093928 | 0.0002354
102 | 0.9817 | -0.3494 | 0.00059031 | 0.00014795
103 | 0.98163 | -0.35075 | 0 | 0
104 | 0.9816 | -0.35123 | 0.0013431 | 0.0003366
105 | 0.98491 | -0.29028 | 0.0015556 | 0.00038986
106 | 0.98488 | -0.29099 | 0 | 0
107 | 0.98474 | -0.2937 | 0.0011262 | 0.00028225
108 | 0.98487 | -0.2911 | 0.0011504 | 0.00028831
109 | 0.98459 | -0.29648 | 0.0028042 | 0.0007028
110 | 0.98457 | -0.29691 | 0.001838 | 0.00046065
111 | 0.98455 | -0.2973 | 0.0027371 | 0.00068597
112 | 0.99526 | -0.089695 | 0.0017396 | 0.00043599
113 | 0.99524 | -0.090005 | 0.0051105 | 0.0012808
114 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00082807 | -0.00020702 | 0.00082815 | 0.00020537 | 7.8178e-08 | -1.6497e-06 | 0.0012503 | 0.0012497 | 0.0012503 | 0.98536 | -0.28149 | 0.98546 | -0.2795 | 0.34349
1 | 0.00082807 | 0.00020702 | -0.00082805 | -0.00020753 | 2.3922e-08 | -5.0439e-07 | 0.0012503 | 0.0012505 | 0.0012505 | 0.98536 | -0.28149 | 0.98533 | -0.2821 | 0.34354
2 | -0.00082815 | -0.00020537 | 0.00082817 | 0.00020502 | 1.6644e-08 | -3.5147e-07 | 0.0012497 | 0.0012496 | 0.0012497 | 0.98546 | -0.2795 | 0.98549 | -0.27907 | 0.34333
3 | -0.0061698 | -0.0015438 | 0.00617 | 0.0015438 | 1.7599e-07 | 4.372e-08 | 0.0093151 | 0.0093151 | 0.0093151 | 0.98549 | -0.27907 | 0.98552 | -0.27847 | 2.5591
4 | -0.0030968 | -0.00077612 | 0.0030968 | 0.00077612 | 1.4609e-09 | -1.3685e-09 | 0.0046586 | 0.0046586 | 0.0046586 | 0.98914 | -0.20802 | 0.98914 | -0.20801 | 1.2798
5 | -0.0062145 | -0.0015575 | 0.0062151 | 0.0015577 | 5.8414e-07 | 1.4505e-07 | 0.0093488 | 0.0093487 | 0.0093488 | 0.98914 | -0.20801 | 0.98924 | -0.20604 | 2.5684
6 | -0.066126 | -0.016641 | 0.06623 | 0.016707 | 0.00010381 | 6.6079e-05 | 0.099491 | 0.09949 | 0.099491 | 0.98924 | -0.20604 | 0.99094 | -0.17324 | 27.3326
7 | 0.059911 | 0.015084 | -0.059864 | -0.015054 | 4.655e-05 | 2.9596e-05 | 0.090142 | 0.090142 | 0.090142 | 0.98924 | -0.20604 | 0.9884 | -0.22231 | 24.7643
8 | -0.06623 | -0.016707 | 0.066307 | 0.016757 | 7.74e-05 | 4.9267e-05 | 0.09949 | 0.09949 | 0.09949 | 0.99094 | -0.17324 | 0.9922 | -0.14887 | 27.3325
9 | 0.0052874 | 0.0013247 | -0.0052869 | -0.0013246 | 4.8497e-07 | 4.8803e-08 | 0.0079599 | 0.00796 | 0.00796 | 0.9884 | -0.22231 | 0.98831 | -0.22423 | 2.1868
10 | 0.054577 | 0.013729 | -0.054569 | -0.013724 | 8.068e-06 | 5.1227e-06 | 0.082182 | 0.082182 | 0.082182 | 0.9884 | -0.22231 | 0.98825 | -0.2254 | 22.5775
11 | -0.0090325 | -0.0022637 | 0.0090327 | 0.0022638 | 2.2329e-07 | 1.0221e-07 | 0.013646 | 0.013646 | 0.013646 | 0.98491 | -0.29031 | 0.98494 | -0.28979 | 3.749
12 | 0.0090325 | 0.0022637 | -0.0090322 | -0.0022636 | 3.1029e-07 | 1.4204e-07 | 0.013646 | 0.013646 | 0.013646 | 0.98491 | -0.29031 | 0.98487 | -0.29103 | 3.749
13 | -0.012007 | -0.0030092 | 0.012009 | 0.0030104 | 2.2362e-06 | 1.2005e-06 | 0.018139 | 0.018139 | 0.018139 | 0.98494 | -0.28979 | 0.98514 | -0.28588 | 4.9834
14 | 0.0060055 | 0.001505 | -0.0060051 | -0.001505 | 3.6205e-07 | 8.2493e-08 | 0.0090735 | 0.0090736 | 0.0090736 | 0.98487 | -0.29103 | 0.98481 | -0.29229 | 2.4927
15 | -0.067508 | -0.017058 | 0.067564 | 0.017094 | 5.6935e-05 | 3.6247e-05 | 0.10129 | 0.10129 | 0.10129 | 0.9922 | -0.14887 | 0.99312 | -0.13129 | 27.8271
16 | 0.0029722 | 0.00074449 | -0.0029721 | -0.00074464 | 1.4388e-07 | -1.5342e-07 | 0.0044749 | 0.004475 | 0.004475 | 0.98831 | -0.22423 | 0.98825 | -0.22525 | 1.2294
17 | 0.051449 | 0.012942 | -0.051408 | -0.012917 | 4.0413e-05 | 2.5634e-05 | 0.077484 | 0.077485 | 0.077485 | 0.98825 | -0.2254 | 0.9874 | -0.24186 | 21.287
18 | -0.015036 | -0.003769 | 0.015037 | 0.0037698 | 1.4953e-06 | 8.5856e-07 | 0.022711 | 0.022711 | 0.022711 | 0.98514 | -0.28588 | 0.98524 | -0.28379 | 6.2393
19 | 0.0030306 | 0.00075947 | -0.0030306 | -0.00075953 | 6.0863e-08 | -5.9528e-08 | 0.0045792 | 0.0045792 | 0.0045792 | 0.98481 | -0.29229 | 0.98479 | -0.29272 | 1.258
20 | -0.069024 | -0.01746 | 0.069024 | 0.01746 | 9.4156e-08 | 5.996e-08 | 0.10348 | 0.10348 | 0.10348 | 0.99312 | -0.13129 | 0.99312 | -0.13126 | 28.4279
21 | 0.0014933 | 0.00037401 | -0.0014933 | -0.00037415 | 2.2856e-08 | -1.3985e-07 | 0.0022483 | 0.0022484 | 0.0022484 | 0.98825 | -0.22525 | 0.98824 | -0.22557 | 0.61769
22 | 0.048313 | 0.012141 | -0.048297 | -0.012131 | 1.631e-05 | 1.0333e-05 | 0.07282 | 0.07282 | 0.07282 | 0.9874 | -0.24186 | 0.98703 | -0.24893 | 20.0056
23 | -0.018011 | -0.0045151 | 0.018016 | 0.0045178 | 4.5665e-06 | 2.7129e-06 | 0.027202 | 0.027202 | 0.027202 | 0.98524 | -0.28379 | 0.98552 | -0.27847 | 7.4732
24 | 0.04518 | 0.01135 | -0.04514 | -0.011324 | 4.0337e-05 | 2.552e-05 | 0.068121 | 0.068121 | 0.068121 | 0.98703 | -0.24893 | 0.98607 | -0.26766 | 18.7147
25 | 0.024198 | 0.0060693 | -0.024186 | -0.0060617 | 1.2471e-05 | 7.6636e-06 | 0.036517 | 0.036517 | 0.036517 | 0.98607 | -0.26766 | 0.98552 | -0.27847 | 10.0323
26 | 0.01884 | 0.0047282 | -0.018829 | -0.0047213 | 1.1559e-05 | 6.9117e-06 | 0.028433 | 0.028433 | 0.028433 | 0.98607 | -0.26766 | 0.98541 | -0.28053 | 7.8113
27 | 0.0021016 | 0.00052653 | -0.0021015 | -0.00052669 | 5.8431e-08 | -1.6023e-07 | 0.0031713 | 0.0031713 | 0.0031713 | 0.98607 | -0.26766 | 0.98604 | -0.26824 | 0.87125
28 | 0.016876 | 0.0042318 | -0.016873 | -0.0042305 | 2.2091e-06 | 1.2983e-06 | 0.025484 | 0.025484 | 0.025484 | 0.98541 | -0.28053 | 0.98527 | -0.28328 | 7.001
29 | 0.0014933 | 0.00037415 | -0.0014932 | -0.00037424 | 1.4659e-08 | -8.9691e-08 | 0.0022484 | 0.0022484 | 0.0022484 | 0.98824 | -0.22557 | 0.98823 | -0.22578 | 0.6177
30 | 0.015198 | 0.0038106 | -0.015194 | -0.0038086 | 3.3259e-06 | 1.9143e-06 | 0.022953 | 0.022953 | 0.022953 | 0.98527 | -0.28328 | 0.98504 | -0.28787 | 6.3058
31 | 0.013115 | 0.0032875 | -0.013115 | -0.0032874 | 1.5184e-07 | 8.4045e-08 | 0.019812 | 0.019812 | 0.019812 | 0.98504 | -0.28787 | 0.98502 | -0.28811 | 5.4429
32 | 0.011215 | 0.0028113 | -0.011214 | -0.0028107 | 1.1597e-06 | 6.051e-07 | 0.016942 | 0.016942 | 0.016942 | 0.98502 | -0.28811 | 0.98491 | -0.29028 | 4.6545
33 | 0.012794 | 0.0032076 | -0.012791 | -0.0032063 | 2.3764e-06 | 1.2955e-06 | 0.01912 | 0.01912 | 0.01912 | 0.99569 | -0.081359 | 0.99549 | -0.085258 | 5.2528
34 | -0.012794 | -0.0032076 | 0.012796 | 0.0032085 | 1.7284e-06 | 9.4217e-07 | 0.01912 | 0.01912 | 0.01912 | 0.99569 | -0.081359 | 0.99584 | -0.078525 | 5.2528
35 | 0.010669 | 0.0026743 | -0.010667 | -0.0026734 | 1.7762e-06 | 8.9469e-07 | 0.015947 | 0.015947 | 0.015947 | 0.99549 | -0.085258 | 0.99531 | -0.088753 | 4.3811
36 | 0.14174 | 0.036522 | -0.14152 | -0.036379 | 0.00022502 | 0.00014332 | 0.21216 | 0.21216 | 0.21216 | 0.99584 | -0.078525 | 0.99411 | -0.11119 | 29.1422
37 | -0.15454 | -0.03973 | 0.15494 | 0.039988 | 0.00040419 | 0.00025763 | 0.23128 | 0.23127 | 0.23128 | 0.99584 | -0.078525 | 0.99868 | -0.024854 | 31.7686
38 | 0.14047 | 0.036116 | -0.14019 | -0.035936 | 0.00028248 | 0.00018057 | 0.21059 | 0.21059 | 0.21059 | 0.99411 | -0.11119 | 0.99193 | -0.15267 | 57.8541
39 | 0.089111 | 0.022655 | -0.08903 | -0.022603 | 8.0581e-05 | 5.1413e-05 | 0.13289 | 0.13289 | 0.13289 | 0.99868 | -0.024854 | 0.9977 | -0.043647 | 36.5074
40 | -0.24405 | -0.062643 | 0.24435 | 0.062831 | 0.00029477 | 0.00018834 | 0.36416 | 0.36416 | 0.36416 | 0.99868 | -0.024854 | 1 | 0 | 50.0221
41 | -0.0084394 | -0.0021151 | 0.0084396 | 0.0021152 | 1.8392e-07 | 8.1509e-08 | 0.012939 | 0.012939 | 0.012939 | 0.97052 | -0.56857 | 0.97054 | -0.56812 | 3.5548
42 | -0.014022 | -0.0035144 | 0.014025 | 0.0035161 | 3.1406e-06 | 1.786e-06 | 0.021499 | 0.021499 | 0.021499 | 0.97054 | -0.56812 | 0.97078 | -0.56342 | 5.9062
43 | -0.07048 | -0.017825 | 0.070486 | 0.017828 | 6.213e-06 | 3.9571e-06 | 0.10566 | 0.10566 | 0.10566 | 0.99312 | -0.13126 | 0.99322 | -0.12942 | 29.0271
44 | 0.10941 | 0.027703 | -0.10928 | -0.027619 | 0.00013114 | 8.3771e-05 | 0.16611 | 0.16612 | 0.16612 | 0.98066 | -0.36956 | 0.97937 | -0.39455 | 45.636
45 | -0.11209 | -0.028375 | 0.11224 | 0.028471 | 0.00015147 | 9.6766e-05 | 0.17018 | 0.17018 | 0.17018 | 0.98066 | -0.36956 | 0.9821 | -0.34145 | 46.7535
46 | 0.10618 | 0.026844 | -0.10607 | -0.026772 | 0.00011126 | 7.1066e-05 | 0.16141 | 0.16141 | 0.16141 | 0.97937 | -0.39455 | 0.97825 | -0.41643 | 44.3444
47 | 0.0080283 | 0.0020113 | -0.008027 | -0.0020108 | 1.2305e-06 | 5.0693e-07 | 0.012164 | 0.012164 | 0.012164 | 0.9821 | -0.34145 | 0.98194 | -0.34467 | 3.3417
48 | -0.12027 | -0.030483 | 0.12064 | 0.030722 | 0.00037404 | 0.00023901 | 0.18235 | 0.18235 | 0.18235 | 0.9821 | -0.34145 | 0.98544 | -0.27695 | 50.0951
49 | 0.10513 | 0.026537 | -0.10497 | -0.026437 | 0.00015606 | 9.9677e-05 | 0.15998 | 0.15998 | 0.15998 | 0.97825 | -0.41643 | 0.97667 | -0.44747 | 43.9512
50 | 0.0066092 | 0.0016554 | -0.0066084 | -0.0016552 | 7.3302e-07 | 2.2264e-07 | 0.010015 | 0.010015 | 0.010015 | 0.98194 | -0.34467 | 0.98182 | -0.347 | 2.7514
51 | -0.13139 | -0.033414 | 0.13153 | 0.033506 | 0.00014398 | 9.202e-05 | 0.19857 | 0.19857 | 0.19857 | 0.98544 | -0.27695 | 0.98662 | -0.25423 | 54.5515
52 | 0.010742 | 0.0026927 | -0.01074 | -0.0026914 | 2.5752e-06 | 1.3157e-06 | 0.016221 | 0.016221 | 0.016221 | 0.98544 | -0.27695 | 0.98518 | -0.28198 | 4.4564
53 | 0.012366 | 0.0031004 | -0.012364 | -0.0030996 | 1.6058e-06 | 8.7678e-07 | 0.018841 | 0.018841 | 0.018841 | 0.97667 | -0.44747 | 0.97653 | -0.4502 | 5.1761
54 | 0.092609 | 0.023336 | -0.092563 | -0.023307 | 4.6241e-05 | 2.9517e-05 | 0.14114 | 0.14114 | 0.14114 | 0.97667 | -0.44747 | 0.97613 | -0.45791 | 38.7751
55 | 0.0066084 | 0.0016552 | -0.0066084 | -0.0016552 | 5.2339e-08 | 1.59e-08 | 0.010015 | 0.010015 | 0.010015 | 0.98182 | -0.347 | 0.98181 | -0.34716 | 2.7514
56 | -0.13316 | -0.033916 | 0.13324 | 0.033967 | 7.9532e-05 | 5.0833e-05 | 0.20103 | 0.20103 | 0.20103 | 0.98662 | -0.25423 | 0.98726 | -0.24186 | 55.2282
57 | 0.0089493 | 0.0022426 | -0.008949 | -0.0022425 | 2.7681e-07 | 1.2571e-07 | 0.013517 | 0.013517 | 0.013517 | 0.98518 | -0.28198 | 0.98515 | -0.28263 | 3.7134
58 | 0.012364 | 0.0030996 | -0.01236 | -0.0030971 | 4.4957e-06 | 2.4549e-06 | 0.018841 | 0.018841 | 0.018841 | 0.97653 | -0.4502 | 0.97614 | -0.45783 | 5.1762
59 | 0.059178 | 0.014926 | -0.059117 | -0.014887 | 6.0868e-05 | 3.8707e-05 | 0.090245 | 0.090245 | 0.090245 | 0.97613 | -0.45791 | 0.97504 | -0.47942 | 24.7926
60 | 0.033384 | 0.0083814 | -0.033367 | -0.0083708 | 1.6871e-05 | 1.058e-05 | 0.050896 | 0.050896 | 0.050896 | 0.97613 | -0.45791 | 0.9756 | -0.46851 | 13.9825
61 | 0.0057141 | 0.0014311 | -0.0057138 | -0.001431 | 3.4527e-07 | 6.5719e-08 | 0.0086598 | 0.0086599 | 0.0086599 | 0.98181 | -0.34716 | 0.98175 | -0.34843 | 2.3791
62 | -0.13448 | -0.034277 | 0.13473 | 0.034433 | 0.00024408 | 0.00015601 | 0.2029 | 0.2029 | 0.2029 | 0.98726 | -0.24186 | 0.98922 | -0.20433 | 55.7411
63 | 0.0057736 | 0.0014467 | -0.005773 | -0.0014466 | 5.9576e-07 | 1.1533e-07 | 0.0087206 | 0.0087207 | 0.0087207 | 0.98515 | -0.28263 | 0.98504 | -0.2848 | 2.3958
64 | -0.0012338 | -0.00030922 | 0.0012338 | 0.00030904 | 2.0407e-08 | -1.8355e-07 | 0.0018705 | 0.0018704 | 0.0018705 | 0.98154 | -0.35246 | 0.98156 | -0.35211 | 0.51386
65 | -0.0022497 | -0.00056365 | 0.0022499 | 0.00056332 | 1.4611e-07 | -3.2995e-07 | 0.0034105 | 0.0034103 | 0.0034105 | 0.98156 | -0.35211 | 0.98163 | -0.35075 | 0.93695
66 | 0.0078577 | 0.0019687 | -0.007857 | -0.0019684 | 7.505e-07 | 3.0596e-07 | 0.011978 | 0.011978 | 0.011978 | 0.97614 | -0.45783 | 0.97604 | -0.45983 | 3.2907
67 | 0.056294 | 0.014179 | -0.056263 | -0.014159 | 3.1477e-05 | 2.0004e-05 | 0.085937 | 0.085937 | 0.085937 | 0.97504 | -0.47942 | 0.97444 | -0.49112 | 23.609
68 | 0.03052 | 0.0076571 | -0.030512 | -0.0076518 | 8.4498e-06 | 5.2781e-06 | 0.046553 | 0.046553 | 0.046553 | 0.9756 | -0.46851 | 0.9753 | -0.47432 | 12.7893
69 | 0.005123 | 0.0012829 | -0.0051228 | -0.0012829 | 2.2152e-07 | 1.7883e-08 | 0.0077645 | 0.0077646 | 0.0077646 | 0.98175 | -0.34843 | 0.9817 | -0.34934 | 2.1331
70 | -0.0015505 | -0.00038834 | 0.0015506 | 0.00038804 | 5.6275e-08 | -2.9943e-07 | 0.0023642 | 0.0023641 | 0.0023642 | 0.97585 | -0.46347 | 0.97589 | -0.46271 | 0.64951
71 | 0.0015505 | 0.00038834 | -0.0015505 | -0.00038859 | 4.7139e-08 | -2.5077e-07 | 0.0023642 | 0.0023643 | 0.0023643 | 0.97585 | -0.46347 | 0.97582 | -0.46411 | 0.64954
72 | -0.0048853 | -0.0012238 | 0.004886 | 0.0012238 | 6.6841e-07 | 2.6335e-08 | 0.0074488 | 0.0074486 | 0.0074488 | 0.97589 | -0.46271 | 0.97604 | -0.45983 | 2.0464
73 | 0.0034944 | 0.00087549 | -0.0034943 | -0.00087554 | 9.2071e-08 | -5.3238e-08 | 0.0052786 | 0.0052787 | 0.0052787 | 0.98504 | -0.2848 | 0.98501 | -0.28535 | 1.4502
74 | 0.0013149 | 0.00032933 | -0.0013149 | -0.00032954 | 2.6813e-08 | -2.1351e-07 | 0.0019863 | 0.0019864 | 0.0019864 | 0.98501 | -0.28535 | 0.98499 | -0.28578 | 0.54571
75 | -0.13555 | -0.03464 | 0.13568 | 0.034721 | 0.00012705 | 8.1207e-05 | 0.20414 | 0.20414 | 0.20414 | 0.98922 | -0.20433 | 0.99023 | -0.18497 | 56.0822
76 | -0.13707 | -0.03507 | 0.13722 | 0.035169 | 0.00015403 | 9.8456e-05 | 0.20623 | 0.20623 | 0.20623 | 0.99023 | -0.18497 | 0.99145 | -0.16178 | 56.6571
77 | -0.13844 | -0.035475 | 0.13851 | 0.035514 | 6.1188e-05 | 3.9112e-05 | 0.20806 | 0.20806 | 0.20806 | 0.99145 | -0.16178 | 0.99193 | -0.15267 | 57.1602
78 | 0.028683 | 0.0071935 | -0.028679 | -0.0071912 | 3.6526e-06 | 2.2742e-06 | 0.043763 | 0.043763 | 0.043763 | 0.9753 | -0.47432 | 0.97516 | -0.47699 | 12.0228
79 | 0.024165 | 0.0060599 | -0.024164 | -0.0060595 | 6.0043e-07 | 3.6958e-07 | 0.036875 | 0.036875 | 0.036875 | 0.97516 | -0.47699 | 0.97514 | -0.47752 | 10.1304
80 | 0.020389 | 0.0051134 | -0.020387 | -0.0051117 | 2.8832e-06 | 1.7462e-06 | 0.031114 | 0.031115 | 0.031115 | 0.97514 | -0.47752 | 0.97499 | -0.48048 | 8.5479
81 | 0.052196 | 0.01314 | -0.05215 | -0.013111 | 4.5848e-05 | 2.9103e-05 | 0.079726 | 0.079726 | 0.079726 | 0.97444 | -0.49112 | 0.97351 | -0.50952 | 21.9029
82 | 0.019126 | 0.0047958 | -0.019122 | -0.0047936 | 3.6654e-06 | 2.2028e-06 | 0.029191 | 0.029191 | 0.029191 | 0.97499 | -0.48048 | 0.97478 | -0.4845 | 8.0194
83 | 0.045112 | 0.011347 | -0.045087 | -0.011331 | 2.4984e-05 | 1.5816e-05 | 0.068969 | 0.068969 | 0.068969 | 0.97351 | -0.50952 | 0.97292 | -0.52112 | 18.9477
84 | 0.014346 | 0.0035965 | -0.014345 | -0.0035958 | 1.183e-06 | 6.7515e-07 | 0.0219 | 0.0219 | 0.0219 | 0.97478 | -0.4845 | 0.9747 | -0.48624 | 6.0164
85 | 0.040002 | 0.010057 | -0.039938 | -0.010017 | 6.3467e-05 | 4.0058e-05 | 0.061191 | 0.061192 | 0.061192 | 0.97292 | -0.52112 | 0.97123 | -0.5544 | 16.8109
86 | -0.004234 | -0.0010611 | 0.004234 | 0.0010611 | 3.3726e-09 | -5.2062e-10 | 0.0064659 | 0.0064659 | 0.0064659 | 0.97439 | -0.49234 | 0.97439 | -0.49232 | 1.7764
87 | 0.003078 | 0.00077139 | -0.003078 | -0.00077141 | 2.838e-08 | -2.45e-08 | 0.0047005 | 0.0047005 | 0.0047005 | 0.97439 | -0.49234 | 0.97438 | -0.49253 | 1.2914
88 | -0.0057773 | -0.0014479 | 0.0057773 | 0.0014479 | 1.6957e-08 | 3.6165e-09 | 0.0088226 | 0.0088226 | 0.0088226 | 0.97439 | -0.49232 | 0.97439 | -0.49226 | 2.4238
89 | -0.0094516 | -0.0023688 | 0.0094539 | 0.0023699 | 2.2799e-06 | 1.0955e-06 | 0.014434 | 0.014434 | 0.014434 | 0.97439 | -0.49226 | 0.97465 | -0.4872 | 3.9653
90 | -0.01328 | -0.0033288 | 0.013281 | 0.0033292 | 6.0804e-07 | 3.3999e-07 | 0.020275 | 0.020275 | 0.020275 | 0.97465 | -0.4872 | 0.9747 | -0.48624 | 5.5702
91 | -0.0028278 | -0.00070872 | 0.0028279 | 0.00070867 | 3.8751e-08 | -4.3125e-08 | 0.0043357 | 0.0043357 | 0.0043357 | 0.9705 | -0.56898 | 0.97051 | -0.56869 | 1.1911
92 | -0.011553 | -0.0028955 | 0.011556 | 0.002897 | 2.9055e-06 | 1.5543e-06 | 0.017714 | 0.017714 | 0.017714 | 0.97051 | -0.56869 | 0.97078 | -0.56342 | 4.8664
93 | 0.0071682 | 0.0017967 | -0.0071668 | -0.0017962 | 1.3958e-06 | 5.1221e-07 | 0.010988 | 0.010988 | 0.010988 | 0.97078 | -0.56342 | 0.97057 | -0.5675 | 3.0186
94 | -0.03275 | -0.0082098 | 0.032764 | 0.0082187 | 1.408e-05 | 8.8268e-06 | 0.0502 | 0.0502 | 0.0502 | 0.97078 | -0.56342 | 0.97123 | -0.5544 | 13.7912
95 | -0.071942 | -0.018193 | 0.071942 | 0.018193 | 1.0845e-07 | 6.9089e-08 | 0.10784 | 0.10784 | 0.10784 | 0.99322 | -0.12942 | 0.99322 | -0.12939 | 29.6264
96 | -0.073412 | -0.018562 | 0.073413 | 0.018562 | 8.8377e-07 | 5.631e-07 | 0.11004 | 0.11004 | 0.11004 | 0.99322 | -0.12939 | 0.99323 | -0.12914 | 30.2313
97 | -0.07489 | -0.018933 | 0.074976 | 0.018987 | 8.5272e-05 | 5.434e-05 | 0.11226 | 0.11226 | 0.11226 | 0.99323 | -0.12914 | 0.99447 | -0.10543 | 30.8394
98 | -0.079391 | -0.020093 | 0.07951 | 0.02017 | 0.00011952 | 7.6199e-05 | 0.11886 | 0.11886 | 0.11886 | 0.99447 | -0.10543 | 0.9961 | -0.074116 | 32.6543
99 | -0.083855 | -0.021259 | 0.083966 | 0.021329 | 0.00011039 | 7.0404e-05 | 0.12535 | 0.12535 | 0.12535 | 0.9961 | -0.074116 | 0.99753 | -0.046765 | 34.4374
100 | -0.085247 | -0.02165 | 0.08526 | 0.021658 | 1.2796e-05 | 8.162e-06 | 0.12726 | 0.12726 | 0.12726 | 0.99753 | -0.046765 | 0.9977 | -0.043647 | 34.9627
101 | 0.0045456 | 0.0011392 | -0.0045456 | -0.0011392 | 9.4879e-09 | -1.1833e-09 | 0.0067639 | 0.0067639 | 0.0067639 | 1 | 0 | 1 | -4.3814e-05 | 1.8582
102 | 0.0068505 | 0.0017169 | -0.0068502 | -0.0017168 | 3.0747e-07 | 9.5198e-08 | 0.010242 | 0.010242 | 0.010242 | 0.99531 | -0.088753 | 0.99526 | -0.089695 | 2.8137
103 | 0.0041835 | 0.0010475 | -0.0041835 | -0.0010475 | 1.2587e-08 | -2.4991e-09 | 0.0063409 | 0.0063409 | 0.0063409 | 0.9817 | -0.34934 | 0.9817 | -0.3494 | 1.742
104 | 0.0035932 | 0.00089958 | -0.003593 | -0.00089969 | 2.2933e-07 | -1.139e-07 | 0.0054461 | 0.0054462 | 0.0054462 | 0.9817 | -0.3494 | 0.98163 | -0.35075 | 1.4962
105 | 0.0013431 | 0.00033637 | -0.0013431 | -0.0003366 | 3.1142e-08 | -2.3334e-07 | 0.0020359 | 0.002036 | 0.002036 | 0.98163 | -0.35075 | 0.9816 | -0.35123 | 0.55933
106 | 0.0096584 | 0.0024208 | -0.0096581 | -0.0024207 | 3.2461e-07 | 1.5601e-07 | 0.014592 | 0.014592 | 0.014592 | 0.98491 | -0.29028 | 0.98488 | -0.29099 | 4.0088
107 | 0.0085077 | 0.0021324 | -0.0085066 | -0.002132 | 1.0991e-06 | 4.7771e-07 | 0.012854 | 0.012854 | 0.012854 | 0.98488 | -0.29099 | 0.98474 | -0.2937 | 3.5314
108 | 0.0011504 | 0.00028825 | -0.0011504 | -0.00028831 | 5.8915e-09 | -6.2411e-08 | 0.001738 | 0.0017381 | 0.0017381 | 0.98488 | -0.29099 | 0.98487 | -0.2911 | 0.47749
109 | 0.0073804 | 0.0018497 | -0.0073794 | -0.0018494 | 9.7823e-07 | 3.5929e-07 | 0.011152 | 0.011153 | 0.011153 | 0.98474 | -0.2937 | 0.98459 | -0.29648 | 3.0639
110 | 0.0045752 | 0.0011466 | -0.0045751 | -0.0011466 | 9.3903e-08 | -6.5118e-09 | 0.0069145 | 0.0069145 | 0.0069145 | 0.98459 | -0.29648 | 0.98457 | -0.29691 | 1.8996
111 | 0.0027371 | 0.00068591 | -0.0027371 | -0.00068597 | 4.9953e-08 | -6.7027e-08 | 0.0041367 | 0.0041367 | 0.0041367 | 0.98457 | -0.29691 | 0.98455 | -0.2973 | 1.1365
112 | 0.0051106 | 0.0012808 | -0.0051105 | -0.0012808 | 7.5526e-08 | 3.5082e-09 | 0.0076409 | 0.0076409 | 0.0076409 | 0.99526 | -0.089695 | 0.99524 | -0.090005 | 2.0991

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25771 | 0.065767

## res_load
| p_mw | q_mvar
0 | 0.00082805 | 0.00020753
1 | 0.0053417 | 0.0013387
2 | 0.0030968 | 0.00077612
3 | 0.0031178 | 0.00078139
4 | 0.002974 | 0.00074535
5 | 0.0030267 | 0.00075856
6 | 0.0012004 | 0.00030086
7 | 0.0023147 | 0.00058012
8 | 0.0031199 | 0.00078191
9 | 0.0030267 | 0.00075856
10 | 0.0029745 | 0.00074548
11 | 0.0014596 | 0.00036581
12 | 0.0014788 | 0.00037063
13 | 0.0030951 | 0.0007757
14 | 0.0029738 | 0.00074531
15 | 0.0030306 | 0.00075953
16 | 0.0031169 | 0.00078116
17 | 0.0019532 | 0.00048951
18 | 0.0021015 | 0.00052669
19 | 0.0016756 | 0.00041995
20 | 0.0014932 | 0.00037424
21 | 0.0020794 | 0.00052115
22 | 0.0018997 | 0.00047611
23 | 0.0021228 | 0.00053203
24 | 0.0010466 | 0.0002623
25 | 0.0084394 | 0.0021151
26 | 0.0055827 | 0.0013992
27 | 0.0014558 | 0.00036485
28 | 0.0026808 | 0.00067187
29 | 0.0030944 | 0.00077553
30 | 0.0009411 | 0.00023586
31 | 0.0014179 | 0.00035535
32 | 0.0016333 | 0.00040936
33 | 0.0017906 | 0.00044877
34 | 0.00089427 | 0.00022413
35 | 0.0012388 | 0.00031047
36 | 0.0031754 | 0.00079583
37 | 0.0012338 | 0.00030922
38 | 0.0010159 | 0.00025461
39 | 0.0045023 | 0.0011284
40 | 0.0028231 | 0.00070753
41 | 0.0028475 | 0.00071366
42 | 0.00059072 | 0.00014805
43 | 0.0033347 | 0.00083576
44 | 0.0015505 | 0.00038859
45 | 0.0022786 | 0.00057107
46 | 0.0021794 | 0.00054621
47 | 0.0013149 | 0.00032954
48 | 0.00082545 | 0.00020688
49 | 0.0013927 | 0.00034904
50 | 0.0012201 | 0.00030578
51 | 0.0016839 | 0.00042202
52 | 0.0018289 | 0.00045835
53 | 0.0045142 | 0.0011314
54 | 0.0037748 | 0.00094605
55 | 0.004067 | 0.0010193
56 | 0.0012605 | 0.00031592
57 | 0.0070376 | 0.0017638
58 | 0.0047763 | 0.0011971
59 | 0.0050856 | 0.0012746
60 | 0.002971 | 0.00074461
61 | 0.001156 | 0.00028973
62 | 0.0015432 | 0.00038677
63 | 0.003078 | 0.00077141
64 | 0.0036743 | 0.00092087
65 | 0.0038263 | 0.00095897
66 | 0.001064 | 0.00026666
67 | 0.0028278 | 0.00070872
68 | 0.0087254 | 0.0021868
69 | 0.0071668 | 0.0017962
70 | 0.0071744 | 0.0017981
71 | 0.0014561 | 0.00036492
72 | 0.0014696 | 0.00036831
73 | 0.0014776 | 0.00037031
74 | 0.004415 | 0.0011065
75 | 0.0043451 | 0.001089
76 | 0.0012817 | 0.00032123
77 | 0.0037701 | 0.00094488
78 | 0.0071693 | 0.0017968
79 | 0.0045456 | 0.0011392
80 | 0.0038163 | 0.00095645
81 | 0.00093928 | 0.0002354
82 | 0.00059031 | 0.00014795
83 | 0.0013431 | 0.0003366
84 | 0.0015556 | 0.00038986
85 | 0.0011262 | 0.00028225
86 | 0.0011504 | 0.00028831
87 | 0.0028042 | 0.0007028
88 | 0.001838 | 0.00046065
89 | 0.0027371 | 0.00068597
90 | 0.0017396 | 0.00043599
91 | 0.0051105 | 0.0012808

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1