## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2-14_1_3_node_25 | 0.4 | n |  | TRUE
1 | bus_LV_2-14_1_3_node_27 | 0.4 | n |  | TRUE
2 | bus_LV_2-14_1_3_node_28 | 0.4 | n |  | TRUE
3 | bus_LV_2-14_1_3_node_35 | 0.4 | n |  | TRUE
4 | bus_LV_2-14_1_3_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_2-14_1_3_node_79 | 0.4 | n |  | TRUE
6 | bus_LV_2-14_1_3_node_48 | 0.4 | n |  | TRUE
7 | bus_LV_2-14_1_3_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_2-14_1_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_2-14_1_3_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_2-14_1_3_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_2-14_1_3_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_2-14_1_3_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_2-14_1_3_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_2-14_1_3_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_2-14_1_3_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_2-14_1_3_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_2-14_1_3_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_2-14_1_3_node_69 | 0.4 | n |  | TRUE
19 | bus_LV_2-14_1_3_node_68 | 0.4 | n |  | TRUE
20 | bus_LV_2-14_1_3_node_41 | 0.4 | n |  | TRUE
21 | bus_LV_2-14_1_3_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_2-14_1_3_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_2-14_1_3_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_2-14_1_3_node_46 | 0.4 | n |  | TRUE
25 | bus_LV_2-14_1_3_node_47 | 0.4 | n |  | TRUE
26 | bus_LV_2-14_1_3_node_49 | 0.4 | n |  | TRUE
27 | bus_LV_2-14_1_3_node_76 | 0.4 | n |  | TRUE
28 | bus_LV_2-14_1_3_node_75 | 0.4 | n |  | TRUE
29 | bus_LV_2-14_1_3_node_70 | 0.4 | n |  | TRUE
30 | bus_LV_2-14_1_3_node_71 | 0.4 | n |  | TRUE
31 | bus_LV_2-14_1_3_node_72 | 0.4 | n |  | TRUE
32 | bus_LV_2-14_1_3_node_73 | 0.4 | n |  | TRUE
33 | bus_MV_349_0_node_200 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2-14_1_3_load_25 | 0 | 0.047209 | 0.011832 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2-14_1_3_load_35 | 3 | 0.0012623 | 0.00031636 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2-14_1_3_load_79 | 5 | 0.041313 | 0.010354 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2-14_1_3_load_33 | 7 | 0.002459 | 0.00061628 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2-14_1_3_load_30 | 8 | 0.00056674 | 0.00014204 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2-14_1_3_load_36 | 9 | 0.00059198 | 0.00014836 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2-14_1_3_load_31 | 10 | 0.001451 | 0.00036364 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2-14_1_3_load_32 | 11 | 0.00078222 | 0.00019604 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2-14_1_3_load_34 | 12 | 0.0033542 | 0.00084064 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2-14_1_3_load_74 | 17 | 0.0009023 | 0.00022614 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2-14_1_3_load_68 | 19 | 0.00091704 | 0.00022983 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2-14_1_3_load_41 | 20 | 0.0039532 | 0.00099076 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2-14_1_3_load_43 | 22 | 0.020979 | 0.0052579 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2-14_1_3_load_45 | 23 | 0.020652 | 0.0051758 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2-14_1_3_load_46 | 24 | 0.033882 | 0.0084917 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2-14_1_3_load_76 | 27 | 0.032889 | 0.0082428 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2-14_1_3_load_75 | 28 | 0.00572 | 0.0014336 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2-14_1_3_load_70 | 29 | 0.065845 | 0.016502 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2-14_1_3_load_71 | 30 | 0.0064742 | 0.0016226 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2-14_1_3_line_0 |  | 0 | 1 | 0.032385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2-14_1_3_line_1 |  | 1 | 2 | 0.030246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2-14_1_3_line_2 |  | 2 | 3 | 0.011403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2-14_1_3_line_3 |  | 3 | 11 | 0.03643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2-14_1_3_line_4 |  | 4 | 5 | 0.022836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2-14_1_3_line_5 |  | 4 | 6 | 0.040421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2-14_1_3_line_6 |  | 4 | 7 | 0.035105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2-14_1_3_line_7 |  | 5 | 21 | 0.052224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2-14_1_3_line_8 |  | 6 | 27 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2-14_1_3_line_9 |  | 6 | 24 | 0.028121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2-14_1_3_line_10 |  | 7 | 11 | 0.025048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2-14_1_3_line_11 |  | 8 | 9 | 0.031326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2-14_1_3_line_12 |  | 9 | 14 | 0.028975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2-14_1_3_line_13 |  | 10 | 11 | 0.032716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2-14_1_3_line_14 |  | 10 | 12 | 0.0361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2-14_1_3_line_15 |  | 12 | 13 | 0.019252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2-14_1_3_line_16 |  | 13 | 14 | 0.073065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2-14_1_3_line_17 |  | 15 | 16 | 0.10558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2-14_1_3_line_18 |  | 15 | 17 | 0.019239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2-14_1_3_line_19 |  | 16 | 18 | 0.058723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2-14_1_3_line_20 |  | 16 | 19 | 0.025616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2-14_1_3_line_21 |  | 17 | 32 | 0.0099834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2-14_1_3_line_22 |  | 18 | 27 | 0.022749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2-14_1_3_line_23 |  | 20 | 21 | 0.033686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2-14_1_3_line_24 |  | 21 | 22 | 0.12709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2-14_1_3_line_25 |  | 23 | 24 | 0.033836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2-14_1_3_line_26 |  | 23 | 25 | 0.018124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2-14_1_3_line_27 |  | 25 | 26 | 0.008629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2-14_1_3_line_28 |  | 26 | 28 | 0.10828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2-14_1_3_line_29 |  | 29 | 30 | 0.032584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2-14_1_3_line_30 |  | 30 | 31 | 0.020965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2-14_1_3_line_31 |  | 31 | 32 | 0.046775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2-14_1_3_trafo_48 | 0.63 MVA 20/0.4 kV | 33 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2675958.8209 | 1236256.4433 | 2675976.3447 | 1236283.6769
1 | 2675937.7798 | 1236275.0316 | 2675937.4976 | 1236270.4693 | 2675941.6209 | 1236266.4081 | 2675949.6674 | 1236262.0968 | 2675958.8209 | 1236256.4433
2 | 2675937.7798 | 1236275.0316 | 2675931.788 | 1236284.7332
3 | 2675931.788 | 1236284.7332 | 2675901.2496 | 1236264.8707
4 | 2675941.1372 | 1236198.3104 | 2675943.1595 | 1236199.9485 | 2675943.5953 | 1236203.1563 | 2675935.0976 | 1236217.8912
5 | 2675909.7936 | 1236194.6296 | 2675931.9554 | 1236207.9553 | 2675928.4302 | 1236213.7698 | 2675935.0976 | 1236217.8912
6 | 2675935.0976 | 1236217.8912 | 2675912.5651 | 1236244.8108
7 | 2675941.1372 | 1236198.3104 | 2675987.0509 | 1236173.4247
8 | 2675909.7936 | 1236194.6296 | 2675896.3539 | 1236186.2583
9 | 2675909.7936 | 1236194.6296 | 2675924.1751 | 1236170.4643
10 | 2675912.5651 | 1236244.8108 | 2675914.1367 | 1236249.7343 | 2675901.2496 | 1236264.8707
11 | 2675801.5848 | 1236279.896 | 2675809.7308 | 1236279.6331 | 2675816.0797 | 1236278.4688 | 2675822.9835 | 1236281.2589 | 2675830.9606 | 1236285.9896
12 | 2675783.3985 | 1236258.6605 | 2675788.9075 | 1236264.6015 | 2675792.6678 | 1236274.1561 | 2675801.5848 | 1236279.896
13 | 2675886.9035 | 1236293.6709 | 2675893.6003 | 1236273.8553 | 2675901.2496 | 1236264.8707
14 | 2675850.8734 | 1236291.4263 | 2675886.9035 | 1236293.6709
15 | 2675834.5858 | 1236281.1624 | 2675850.8734 | 1236291.4263
16 | 2675783.3985 | 1236258.6605 | 2675787.3848 | 1236253.4633 | 2675795.7823 | 1236258.4072 | 2675794.9237 | 1236260.4532 | 2675794.4874 | 1236262.6269 | 2675794.4817 | 1236264.8506 | 2675794.908 | 1236267.0242 | 2675795.752 | 1236269.0808 | 2675796.9846 | 1236270.9311 | 2675798.5461 | 1236272.5077 | 2675800.3919 | 1236273.7432 | 2675802.4393 | 1236274.6033 | 2675804.4694 | 1236275.0406 | 2675806.5423 | 1236275.0893 | 2675808.5896 | 1236274.7707 | 2675810.5508 | 1236274.0842 | 2675812.3498 | 1236273.062 | 2675813.9258 | 1236271.7256 | 2675815.2404 | 1236270.119 | 2675822.188 | 1236274.2216 | 2675834.5858 | 1236281.1624
17 | 2675767.7637 | 1236196.9963 | 2675773.4885 | 1236204.4189 | 2675804.6498 | 1236222.9736 | 2675822.8511 | 1236230.5889 | 2675827.8914 | 1236242.4169 | 2675838.3319 | 1236236.7129 | 2675846.7537 | 1236223.7559
18 | 2675767.7637 | 1236196.9963 | 2675751.1316 | 1236187.3265
19 | 2675877.0441 | 1236174.2306 | 2675869.5576 | 1236192.1585 | 2675861.1256 | 1236205.9048 | 2675857.061 | 1236211.8904 | 2675851.4415 | 1236216.3773 | 2675846.7537 | 1236223.7559
20 | 2675846.7537 | 1236223.7559 | 2675868.7449 | 1236236.8917
21 | 2675742.5009 | 1236182.3086 | 2675751.1316 | 1236187.3265
22 | 2675877.0441 | 1236174.2306 | 2675896.3539 | 1236186.2583
23 | 2675987.0509 | 1236173.4247 | 2675992.5412 | 1236205.0612 | 2675993.0352 | 1236206.558
24 | 2675987.0509 | 1236173.4247 | 2676005.7925 | 1236173.1086 | 2676022.6374 | 1236178.4945 | 2676065.943 | 1236229.6395 | 2676047.7543 | 1236244.7399
25 | 2675922.2318 | 1236143.6357 | 2675929.9416 | 1236148.2439 | 2675932.4306 | 1236156.5926 | 2675924.1751 | 1236170.4643
26 | 2675906.6745 | 1236134.3371 | 2675922.2318 | 1236143.6357
27 | 2675898.0297 | 1236133.9375 | 2675906.6745 | 1236134.3371
28 | 2675898.0297 | 1236133.9375 | 2675864.6062 | 1236030.9421
29 | 2675800.2107 | 1236118.7804 | 2675783.2158 | 1236146.5818
30 | 2675766.5863 | 1236142.1768 | 2675780.8828 | 1236150.3981 | 2675783.2158 | 1236146.5818
31 | 2675766.5863 | 1236142.1768 | 2675742.5009 | 1236182.3086

## bus_geodata
| x | y | coords
0 | 2675976.3447 | 1236283.6769
1 | 2675958.8209 | 1236256.4433
2 | 2675937.7798 | 1236275.0316
3 | 2675931.788 | 1236284.7332
4 | 2675935.0976 | 1236217.8912
5 | 2675941.1372 | 1236198.3104
6 | 2675909.7936 | 1236194.6296
7 | 2675912.5651 | 1236244.8108
8 | 2675830.9606 | 1236285.9896
9 | 2675801.5848 | 1236279.896
10 | 2675886.9035 | 1236293.6709
11 | 2675901.2496 | 1236264.8707
12 | 2675850.8734 | 1236291.4263
13 | 2675834.5858 | 1236281.1624
14 | 2675783.3985 | 1236258.6605
15 | 2675767.7637 | 1236196.9963
16 | 2675846.7537 | 1236223.7559
17 | 2675751.1316 | 1236187.3265
18 | 2675877.0441 | 1236174.2306
19 | 2675868.7449 | 1236236.8917
20 | 2675993.0352 | 1236206.558
21 | 2675987.0509 | 1236173.4247
22 | 2676047.7543 | 1236244.7399
23 | 2675922.2318 | 1236143.6357
24 | 2675924.1751 | 1236170.4643
25 | 2675906.6745 | 1236134.3371
26 | 2675898.0297 | 1236133.9375
27 | 2675896.3539 | 1236186.2583
28 | 2675864.6062 | 1236030.9421
29 | 2675800.2107 | 1236118.7804
30 | 2675783.2158 | 1236146.5818
31 | 2675766.5863 | 1236142.1768
32 | 2675742.5009 | 1236182.3086
33 | 2675877.0441 | 1236174.2306

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98745 | -0.24145 | 0.047209 | 0.011832
1 | 0.98886 | -0.21416 | 0 | 0
2 | 0.99017 | -0.18874 | 0 | 0
3 | 0.99066 | -0.17918 | 0.0012623 | 0.00031636
4 | 0.99541 | -0.087722 | 0 | 0
5 | 0.99403 | -0.11437 | 0.041313 | 0.010354
6 | 1 | 0 | -0.29563 | -0.074743
7 | 0.99355 | -0.12341 | 0.002459 | 0.00061628
8 | 0.99181 | -0.15703 | 0.00056674 | 0.00014204
9 | 0.99183 | -0.15671 | 0.00059198 | 0.00014836
10 | 0.99211 | -0.15133 | 0.001451 | 0.00036364
11 | 0.99228 | -0.14787 | 0.00078222 | 0.00019604
12 | 0.99196 | -0.15422 | 0.0033542 | 0.00084064
13 | 0.99194 | -0.15461 | 0 | 0
14 | 0.99186 | -0.15612 | 0 | 0
15 | 0.98564 | -0.27351 | 0 | 0
16 | 0.99282 | -0.13581 | 0 | 0
17 | 0.98434 | -0.29882 | 0.0009023 | 0.00022614
18 | 0.99687 | -0.059126 | 0 | 0
19 | 0.9928 | -0.13622 | 0.00091704 | 0.00022983
20 | 0.99272 | -0.13973 | 0.0039532 | 0.00099076
21 | 0.99284 | -0.13737 | 0 | 0
22 | 0.9904 | -0.18464 | 0.020979 | 0.0052579
23 | 0.99765 | -0.045197 | 0.020652 | 0.0051758
24 | 0.99846 | -0.029581 | 0.033882 | 0.0084917
25 | 0.99756 | -0.047014 | 0 | 0
26 | 0.99751 | -0.047879 | 0 | 0
27 | 0.99844 | -0.029586 | 0.032889 | 0.0082428
28 | 0.99695 | -0.058738 | 0.00572 | 0.0014336
29 | 0.97713 | -0.43956 | 0.065845 | 0.016502
30 | 0.97912 | -0.40047 | 0.0064742 | 0.0016226
31 | 0.98053 | -0.37294 | 0 | 0
32 | 0.98367 | -0.31181 | 0 | 0
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.047209 | -0.011832 | 0.04727 | 0.011871 | 6.1461e-05 | 3.892e-05 | 0.07114 | 0.07114 | 0.07114 | 0.98745 | -0.24145 | 0.98886 | -0.21416 | 19.544
1 | -0.04727 | -0.011871 | 0.047328 | 0.011907 | 5.7402e-05 | 3.6349e-05 | 0.07114 | 0.07114 | 0.07114 | 0.98886 | -0.21416 | 0.99017 | -0.18874 | 19.544
2 | -0.047328 | -0.011907 | 0.04735 | 0.011921 | 2.1641e-05 | 1.3703e-05 | 0.07114 | 0.07114 | 0.07114 | 0.99017 | -0.18874 | 0.99066 | -0.17918 | 19.544
3 | -0.048612 | -0.012237 | 0.048685 | 0.012283 | 7.2871e-05 | 4.6168e-05 | 0.073036 | 0.073036 | 0.073036 | 0.99066 | -0.17918 | 0.99228 | -0.14787 | 20.0648
4 | 0.066405 | 0.016702 | -0.066321 | -0.016648 | 8.4421e-05 | 5.3733e-05 | 0.099288 | 0.099289 | 0.099289 | 0.99541 | -0.087722 | 0.99403 | -0.11437 | 27.2771
5 | -0.12446 | -0.031395 | 0.12499 | 0.03173 | 0.00052511 | 0.00033554 | 0.18612 | 0.18612 | 0.18612 | 0.99541 | -0.087722 | 1 | 0 | 51.1332
6 | 0.058056 | 0.014693 | -0.057956 | -0.01463 | 9.9268e-05 | 6.3076e-05 | 0.086836 | 0.086837 | 0.086837 | 0.99541 | -0.087722 | 0.99355 | -0.12341 | 23.8562
7 | 0.025008 | 0.0062941 | -0.02498 | -0.0062772 | 2.7459e-05 | 1.6898e-05 | 0.037445 | 0.037445 | 0.037445 | 0.99403 | -0.11437 | 0.99284 | -0.13737 | 10.2871
8 | 0.10863 | 0.027845 | -0.10848 | -0.027745 | 0.00015557 | 9.9354e-05 | 0.16186 | 0.16186 | 0.16186 | 1 | 0 | 0.99844 | -0.029586 | 44.4681
9 | 0.060362 | 0.015168 | -0.060277 | -0.015114 | 8.5103e-05 | 5.4097e-05 | 0.089834 | 0.089834 | 0.089834 | 1 | 0 | 0.99846 | -0.029581 | 24.6797
10 | 0.055497 | 0.014013 | -0.055433 | -0.013972 | 6.4948e-05 | 4.1243e-05 | 0.083154 | 0.083154 | 0.083154 | 0.99355 | -0.12341 | 0.99228 | -0.14787 | 22.8445
11 | -0.00056674 | -0.00014204 | 0.00056674 | 0.00014164 | 8.4913e-09 | -3.9884e-07 | 0.00085027 | 0.00085013 | 0.00085027 | 0.99181 | -0.15703 | 0.99183 | -0.15671 | 0.23359
12 | -0.0011587 | -0.00029 | 0.0011588 | 0.00028965 | 3.2828e-08 | -3.5294e-07 | 0.0017383 | 0.0017381 | 0.0017383 | 0.99183 | -0.15671 | 0.99186 | -0.15612 | 0.47754
13 | -0.0059646 | -0.0014927 | 0.0059656 | 0.0014929 | 9.8171e-07 | 2.0575e-07 | 0.0089453 | 0.0089452 | 0.0089453 | 0.99211 | -0.15133 | 0.99228 | -0.14787 | 2.4575
14 | 0.0045137 | 0.0011291 | -0.0045131 | -0.0011292 | 6.2031e-07 | -6.9088e-08 | 0.0067691 | 0.0067693 | 0.0067693 | 0.99211 | -0.15133 | 0.99196 | -0.15422 | 1.8597
15 | 0.0011589 | 0.00028852 | -0.0011588 | -0.00028876 | 2.1801e-08 | -2.3457e-07 | 0.0017377 | 0.0017378 | 0.0017378 | 0.99196 | -0.15422 | 0.99194 | -0.15461 | 0.47742
16 | 0.0011588 | 0.00028876 | -0.0011588 | -0.00028965 | 8.276e-08 | -8.9012e-07 | 0.0017378 | 0.0017381 | 0.0017381 | 0.99194 | -0.15461 | 0.99186 | -0.15612 | 0.47751
17 | -0.073788 | -0.018712 | 0.07428 | 0.019025 | 0.00049199 | 0.00031352 | 0.11147 | 0.11147 | 0.11147 | 0.98564 | -0.27351 | 0.99282 | -0.13581 | 30.6249
18 | 0.073788 | 0.018712 | -0.073698 | -0.018654 | 8.9652e-05 | 5.7132e-05 | 0.11147 | 0.11147 | 0.11147 | 0.98564 | -0.27351 | 0.98434 | -0.29882 | 30.6249
19 | -0.075197 | -0.019255 | 0.075477 | 0.019433 | 0.00028043 | 0.00017871 | 0.11285 | 0.11285 | 0.11285 | 0.99282 | -0.13581 | 0.99687 | -0.059126 | 31.0023
20 | 0.00091706 | 0.00022951 | -0.00091704 | -0.00022983 | 1.8145e-08 | -3.1963e-07 | 0.0013743 | 0.0013745 | 0.0013745 | 0.99282 | -0.13581 | 0.9928 | -0.13622 | 0.3776
21 | 0.072796 | 0.018428 | -0.07275 | -0.018399 | 4.5391e-05 | 2.8923e-05 | 0.11011 | 0.11011 | 0.11011 | 0.98434 | -0.29882 | 0.98367 | -0.31181 | 30.2502
22 | -0.075477 | -0.019433 | 0.075586 | 0.019503 | 0.00010864 | 6.9232e-05 | 0.11285 | 0.11285 | 0.11285 | 0.99687 | -0.059126 | 0.99844 | -0.029586 | 31.0022
23 | -0.0039532 | -0.00099076 | 0.0039536 | 0.00099061 | 4.4353e-07 | -1.5171e-07 | 0.0059255 | 0.0059254 | 0.0059255 | 0.99272 | -0.13973 | 0.99284 | -0.13737 | 1.6279
24 | 0.021027 | 0.0052866 | -0.020979 | -0.0052579 | 4.7348e-05 | 2.8663e-05 | 0.03152 | 0.03152 | 0.03152 | 0.99284 | -0.13737 | 0.9904 | -0.18464 | 8.6594
25 | -0.026375 | -0.0066099 | 0.026395 | 0.0066221 | 1.9636e-05 | 1.2125e-05 | 0.039339 | 0.039339 | 0.039339 | 0.99765 | -0.045197 | 0.99846 | -0.029581 | 10.8075
26 | 0.0057237 | 0.0014342 | -0.0057232 | -0.0014341 | 4.9534e-07 | 8.0378e-08 | 0.008537 | 0.008537 | 0.008537 | 0.99765 | -0.045197 | 0.99756 | -0.047014 | 2.3453
27 | 0.0057232 | 0.0014341 | -0.005723 | -0.0014341 | 2.3583e-07 | 3.8286e-08 | 0.008537 | 0.0085371 | 0.0085371 | 0.99756 | -0.047014 | 0.99751 | -0.047879 | 2.3453
28 | 0.005723 | 0.0014341 | -0.00572 | -0.0014336 | 2.9596e-06 | 4.8142e-07 | 0.0085371 | 0.0085376 | 0.0085376 | 0.99751 | -0.047879 | 0.99695 | -0.058738 | 2.3455
29 | -0.065845 | -0.016502 | 0.065968 | 0.016581 | 0.00012286 | 7.822e-05 | 0.10027 | 0.10027 | 0.10027 | 0.97713 | -0.43956 | 0.97912 | -0.40047 | 27.5473
30 | -0.072442 | -0.018203 | 0.072538 | 0.018264 | 9.532e-05 | 6.0741e-05 | 0.11011 | 0.11011 | 0.11011 | 0.97912 | -0.40047 | 0.98053 | -0.37294 | 30.2503
31 | -0.072538 | -0.018264 | 0.07275 | 0.018399 | 0.00021267 | 0.00013552 | 0.11011 | 0.11011 | 0.11011 | 0.98053 | -0.37294 | 0.98367 | -0.31181 | 30.2503

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29563 | 0.074743

## res_load
| p_mw | q_mvar
0 | 0.047209 | 0.011832
1 | 0.0012623 | 0.00031636
2 | 0.041313 | 0.010354
3 | 0.002459 | 0.00061628
4 | 0.00056674 | 0.00014204
5 | 0.00059198 | 0.00014836
6 | 0.001451 | 0.00036364
7 | 0.00078222 | 0.00019604
8 | 0.0033542 | 0.00084064
9 | 0.0009023 | 0.00022614
10 | 0.00091704 | 0.00022983
11 | 0.0039532 | 0.00099076
12 | 0.020979 | 0.0052579
13 | 0.020652 | 0.0051758
14 | 0.033882 | 0.0084917
15 | 0.032889 | 0.0082428
16 | 0.00572 | 0.0014336
17 | 0.065845 | 0.016502
18 | 0.0064742 | 0.0016226

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1