## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2-5_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2-5_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2-5_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2-5_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2-5_0_7_node_127 | 0.4 | n |  | TRUE
5 | bus_LV_2-5_0_7_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2-5_0_7_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2-5_0_7_node_125 | 0.4 | n |  | TRUE
8 | bus_LV_2-5_0_7_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2-5_0_7_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_2-5_0_7_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_2-5_0_7_node_135 | 0.4 | n |  | TRUE
12 | bus_LV_2-5_0_7_node_136 | 0.4 | n |  | TRUE
13 | bus_LV_2-5_0_7_node_137 | 0.4 | n |  | TRUE
14 | bus_LV_2-5_0_7_node_131 | 0.4 | n |  | TRUE
15 | bus_LV_2-5_0_7_node_138 | 0.4 | n |  | TRUE
16 | bus_LV_2-5_0_7_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2-5_0_7_node_92 | 0.4 | n |  | TRUE
18 | bus_LV_2-5_0_7_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_2-5_0_7_node_126 | 0.4 | n |  | TRUE
20 | bus_LV_2-5_0_7_node_128 | 0.4 | n |  | TRUE
21 | bus_LV_2-5_0_7_node_129 | 0.4 | n |  | TRUE
22 | bus_LV_2-5_0_7_node_130 | 0.4 | n |  | TRUE
23 | bus_LV_2-5_0_7_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2-5_0_7_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_2-5_0_7_node_7 | 0.4 | n |  | TRUE
26 | bus_LV_2-5_0_7_node_8 | 0.4 | n |  | TRUE
27 | bus_LV_2-5_0_7_node_9 | 0.4 | n |  | TRUE
28 | bus_LV_2-5_0_7_node_11 | 0.4 | n |  | TRUE
29 | bus_LV_2-5_0_7_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_2-5_0_7_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2-5_0_7_node_13 | 0.4 | n |  | TRUE
32 | bus_LV_2-5_0_7_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2-5_0_7_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_2-5_0_7_node_109 | 0.4 | n |  | TRUE
35 | bus_LV_2-5_0_7_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_2-5_0_7_node_108 | 0.4 | n |  | TRUE
37 | bus_LV_2-5_0_7_node_139 | 0.4 | n |  | TRUE
38 | bus_LV_2-5_0_7_node_140 | 0.4 | n |  | TRUE
39 | bus_LV_2-5_0_7_node_144 | 0.4 | n |  | TRUE
40 | bus_LV_2-5_0_7_node_148 | 0.4 | n |  | TRUE
41 | bus_LV_2-5_0_7_node_145 | 0.4 | n |  | TRUE
42 | bus_LV_2-5_0_7_node_146 | 0.4 | n |  | TRUE
43 | bus_LV_2-5_0_7_node_147 | 0.4 | n |  | TRUE
44 | bus_LV_2-5_0_7_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_2-5_0_7_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_2-5_0_7_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_2-5_0_7_node_118 | 0.4 | n |  | TRUE
48 | bus_LV_2-5_0_7_node_110 | 0.4 | n |  | TRUE
49 | bus_LV_2-5_0_7_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_2-5_0_7_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_2-5_0_7_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_2-5_0_7_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_2-5_0_7_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_2-5_0_7_node_106 | 0.4 | n |  | TRUE
55 | bus_LV_2-5_0_7_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_2-5_0_7_node_72 | 0.4 | n |  | TRUE
57 | bus_LV_2-5_0_7_node_60 | 0.4 | n |  | TRUE
58 | bus_LV_2-5_0_7_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_2-5_0_7_node_111 | 0.4 | n |  | TRUE
60 | bus_LV_2-5_0_7_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_2-5_0_7_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_2-5_0_7_node_69 | 0.4 | n |  | TRUE
63 | bus_LV_2-5_0_7_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_2-5_0_7_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_2-5_0_7_node_35 | 0.4 | n |  | TRUE
66 | bus_LV_2-5_0_7_node_37 | 0.4 | n |  | TRUE
67 | bus_LV_2-5_0_7_node_39 | 0.4 | n |  | TRUE
68 | bus_LV_2-5_0_7_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_2-5_0_7_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_2-5_0_7_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_2-5_0_7_node_103 | 0.4 | n |  | TRUE
72 | bus_LV_2-5_0_7_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_2-5_0_7_node_104 | 0.4 | n |  | TRUE
74 | bus_LV_2-5_0_7_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_2-5_0_7_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_2-5_0_7_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_2-5_0_7_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_2-5_0_7_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_2-5_0_7_node_73 | 0.4 | n |  | TRUE
80 | bus_LV_2-5_0_7_node_48 | 0.4 | n |  | TRUE
81 | bus_LV_2-5_0_7_node_49 | 0.4 | n |  | TRUE
82 | bus_LV_2-5_0_7_node_51 | 0.4 | n |  | TRUE
83 | bus_LV_2-5_0_7_node_50 | 0.4 | n |  | TRUE
84 | bus_LV_2-5_0_7_node_52 | 0.4 | n |  | TRUE
85 | bus_LV_2-5_0_7_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_2-5_0_7_node_55 | 0.4 | n |  | TRUE
87 | bus_LV_2-5_0_7_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_2-5_0_7_node_57 | 0.4 | n |  | TRUE
89 | bus_LV_2-5_0_7_node_61 | 0.4 | n |  | TRUE
90 | bus_LV_2-5_0_7_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_2-5_0_7_node_90 | 0.4 | n |  | TRUE
92 | bus_LV_2-5_0_7_node_132 | 0.4 | n |  | TRUE
93 | bus_LV_2-5_0_7_node_133 | 0.4 | n |  | TRUE
94 | bus_LV_2-5_0_7_node_141 | 0.4 | n |  | TRUE
95 | bus_LV_2-5_0_7_node_142 | 0.4 | n |  | TRUE
96 | bus_LV_2-5_0_7_node_143 | 0.4 | n |  | TRUE
97 | bus_LV_2-5_0_7_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_2-5_0_7_node_115 | 0.4 | n |  | TRUE
99 | bus_LV_2-5_0_7_node_113 | 0.4 | n |  | TRUE
100 | bus_LV_2-5_0_7_node_64 | 0.4 | n |  | TRUE
101 | bus_LV_2-5_0_7_node_65 | 0.4 | n |  | TRUE
102 | bus_LV_2-5_0_7_node_66 | 0.4 | n |  | TRUE
103 | bus_LV_2-5_0_7_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_2-5_0_7_node_68 | 0.4 | n |  | TRUE
105 | bus_LV_2-5_0_7_node_70 | 0.4 | n |  | TRUE
106 | bus_LV_2-5_0_7_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_2-5_0_7_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_2-5_0_7_node_152 | 0.4 | n |  | TRUE
109 | bus_LV_2-5_0_7_node_151 | 0.4 | n |  | TRUE
110 | bus_LV_2-5_0_7_node_74 | 0.4 | n |  | TRUE
111 | bus_LV_2-5_0_7_node_76 | 0.4 | n |  | TRUE
112 | bus_LV_2-5_0_7_node_79 | 0.4 | n |  | TRUE
113 | bus_LV_2-5_0_7_node_80 | 0.4 | n |  | TRUE
114 | bus_LV_2-5_0_7_node_78 | 0.4 | n |  | TRUE
115 | bus_LV_2-5_0_7_node_84 | 0.4 | n |  | TRUE
116 | bus_LV_2-5_0_7_node_82 | 0.4 | n |  | TRUE
117 | bus_LV_2-5_0_7_node_83 | 0.4 | n |  | TRUE
118 | bus_LV_2-5_0_7_node_81 | 0.4 | n |  | TRUE
119 | bus_LV_2-5_0_7_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_2-5_0_7_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_2-5_0_7_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_2-5_0_7_node_85 | 0.4 | n |  | TRUE
123 | bus_LV_2-5_0_7_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_2-5_0_7_node_122 | 0.4 | n |  | TRUE
125 | bus_LV_2-5_0_7_node_86 | 0.4 | n |  | TRUE
126 | bus_LV_2-5_0_7_node_87 | 0.4 | n |  | TRUE
127 | bus_LV_2-5_0_7_node_89 | 0.4 | n |  | TRUE
128 | bus_LV_2-5_0_7_node_91 | 0.4 | n |  | TRUE
129 | bus_LV_2-5_0_7_node_150 | 0.4 | n |  | TRUE
130 | bus_LV_2-5_0_7_node_149 | 0.4 | n |  | TRUE
131 | bus_LV_2-5_0_7_node_93 | 0.4 | n |  | TRUE
132 | bus_LV_2-5_0_7_node_94 | 0.4 | n |  | TRUE
133 | bus_LV_2-5_0_7_node_95 | 0.4 | n |  | TRUE
134 | bus_LV_2-5_0_7_node_96 | 0.4 | n |  | TRUE
135 | bus_LV_2-5_0_7_node_97 | 0.4 | n |  | TRUE
136 | bus_LV_2-5_0_7_node_98 | 0.4 | n |  | TRUE
137 | bus_LV_2-5_0_7_node_99 | 0.4 | n |  | TRUE
138 | bus_LV_2-5_0_7_node_100 | 0.4 | n |  | TRUE
139 | bus_LV_2-5_0_7_node_101 | 0.4 | n |  | TRUE
140 | bus_LV_2-5_0_7_node_102 | 0.4 | n |  | TRUE
141 | bus_LV_2-5_0_7_node_116 | 0.4 | n |  | TRUE
142 | bus_LV_2-5_0_7_node_117 | 0.4 | n |  | TRUE
143 | bus_LV_2-5_0_7_node_124 | 0.4 | n |  | TRUE
144 | bus_MV_349_0_node_141 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2-5_0_7_load_0 | 0 | 0.0052132 | 0.0013065 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2-5_0_7_load_1 | 1 | 0.0021025 | 0.00052694 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2-5_0_7_load_2 | 2 | 0.0027203 | 0.00068176 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2-5_0_7_load_3 | 3 | 0.0049528 | 0.0012413 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2-5_0_7_load_4 | 5 | 0.0016632 | 0.00041684 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2-5_0_7_load_125 | 7 | 0.0018099 | 0.00045361 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2-5_0_7_load_31 | 9 | 0.0014439 | 0.00036188 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2-5_0_7_load_27 | 10 | 0.001525 | 0.0003822 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2-5_0_7_load_135 | 11 | 0.0024928 | 0.00062474 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2-5_0_7_load_136 | 12 | 0.0018137 | 0.00045456 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2-5_0_7_load_137 | 13 | 0.0015043 | 0.00037702 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2-5_0_7_load_131 | 14 | 0.00064248 | 0.00016102 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2-5_0_7_load_92 | 17 | 0.00144 | 0.00036089 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2-5_0_7_load_26 | 18 | 0.013856 | 0.0034727 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2-5_0_7_load_128 | 20 | 0.0006482 | 0.00016245 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2-5_0_7_load_129 | 21 | 0.0020607 | 0.00051646 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2-5_0_7_load_130 | 22 | 0.0024571 | 0.00061582 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2-5_0_7_load_18 | 23 | 0.038013 | 0.0095271 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2-5_0_7_load_10 | 24 | 0.012375 | 0.0031015 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2-5_0_7_load_7 | 25 | 0.021663 | 0.0054294 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2-5_0_7_load_8 | 26 | 0.063551 | 0.015927 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2-5_0_7_load_11 | 28 | 0.016427 | 0.004117 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2-5_0_7_load_12 | 29 | 0.0086476 | 0.0021673 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2-5_0_7_load_16 | 30 | 0.0043859 | 0.0010992 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2-5_0_7_load_13 | 31 | 0.0055462 | 0.00139 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2-5_0_7_load_21 | 33 | 0.0012873 | 0.00032262 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2-5_0_7_load_109 | 34 | 0.0038393 | 0.00096222 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2-5_0_7_load_22 | 35 | 0.013402 | 0.0033588 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2-5_0_7_load_108 | 36 | 0.0049285 | 0.0012352 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2-5_0_7_load_144 | 39 | 0.0023785 | 0.00059612 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2-5_0_7_load_148 | 40 | 0.001007 | 0.00025237 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2-5_0_7_load_145 | 41 | 0.0016704 | 0.00041865 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2-5_0_7_load_146 | 42 | 0.001004 | 0.00025162 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2-5_0_7_load_147 | 43 | 0.0010242 | 0.0002567 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2-5_0_7_load_23 | 44 | 0.0021032 | 0.00052711 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2-5_0_7_load_24 | 45 | 0.0016229 | 0.00040673 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2-5_0_7_load_25 | 46 | 0.0038495 | 0.00096477 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2-5_0_7_load_118 | 47 | 0.0022524 | 0.0005645 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2-5_0_7_load_110 | 48 | 0.002195 | 0.00055013 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2-5_0_7_load_29 | 50 | 0.0026031 | 0.0006524 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2-5_0_7_load_30 | 52 | 0.0059062 | 0.0014802 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2-5_0_7_load_106 | 54 | 0.0025805 | 0.00064674 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2-5_0_7_load_72 | 56 | 0.00528 | 0.0013233 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2-5_0_7_load_60 | 57 | 0.0048882 | 0.0012251 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2-5_0_7_load_54 | 58 | 0.0014565 | 0.00036502 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2-5_0_7_load_111 | 59 | 0.0011569 | 0.00028994 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2-5_0_7_load_41 | 60 | 0.0017039 | 0.00042703 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2-5_0_7_load_69 | 62 | 0.0038035 | 0.00095323 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2-5_0_7_load_59 | 63 | 0.0043358 | 0.0010867 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2-5_0_7_load_34 | 64 | 0.0012305 | 0.0003084 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2-5_0_7_load_35 | 65 | 0.0030041 | 0.00075289 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2-5_0_7_load_37 | 66 | 0.0011488 | 0.00028793 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2-5_0_7_load_39 | 67 | 0.0078664 | 0.0019715 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2-5_0_7_load_40 | 68 | 0.0011512 | 0.00028852 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2-5_0_7_load_42 | 69 | 0.0046351 | 0.0011617 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2-5_0_7_load_44 | 70 | 0.0011587 | 0.00029041 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2-5_0_7_load_103 | 71 | 0.0016351 | 0.00040979 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2-5_0_7_load_43 | 72 | 0.0016288 | 0.00040822 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2-5_0_7_load_104 | 73 | 0.0016483 | 0.00041311 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2-5_0_7_load_45 | 74 | 0.0011526 | 0.00028887 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2-5_0_7_load_46 | 75 | 0.0015881 | 0.00039801 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2-5_0_7_load_47 | 76 | 0.0040773 | 0.0010219 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2-5_0_7_load_77 | 78 | 0.004342 | 0.0010882 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2-5_0_7_load_73 | 79 | 0.0042387 | 0.0010623 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2-5_0_7_load_48 | 80 | 0.0042897 | 0.0010751 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2-5_0_7_load_49 | 81 | 0.001492 | 0.00037394 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2-5_0_7_load_51 | 82 | 0.0014496 | 0.00036331 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2-5_0_7_load_53 | 85 | 0.0042302 | 0.0010602 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2-5_0_7_load_55 | 86 | 0.001424 | 0.00035689 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2-5_0_7_load_56 | 87 | 0.0043367 | 0.0010869 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2-5_0_7_load_57 | 88 | 0.0052608 | 0.0013185 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2-5_0_7_load_61 | 89 | 0.0013897 | 0.0003483 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2-5_0_7_load_58 | 90 | 0.0031524 | 0.00079007 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2-5_0_7_load_90 | 91 | 0.0013659 | 0.00034233 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2-5_0_7_load_132 | 92 | 0.0020983 | 0.00052589 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2-5_0_7_load_133 | 93 | 0.0013134 | 0.00032917 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2-5_0_7_load_141 | 94 | 0.0020698 | 0.00051873 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2-5_0_7_load_142 | 95 | 0.0022585 | 0.00056604 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2-5_0_7_load_143 | 96 | 0.0038977 | 0.00097687 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2-5_0_7_load_88 | 97 | 0.001419 | 0.00035562 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2-5_0_7_load_115 | 98 | 0.0018911 | 0.00047395 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2-5_0_7_load_64 | 100 | 0.0017185 | 0.00043071 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2-5_0_7_load_65 | 101 | 0.0016497 | 0.00041346 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2-5_0_7_load_67 | 103 | 0.0017096 | 0.00042847 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2-5_0_7_load_68 | 104 | 0.0016343 | 0.00040959 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2-5_0_7_load_70 | 105 | 0.0016565 | 0.00041517 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2-5_0_7_load_71 | 106 | 0.0016532 | 0.00041432 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2-5_0_7_load_105 | 107 | 0.0016379 | 0.0004105 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2-5_0_7_load_152 | 108 | 0.0013867 | 0.00034754 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2-5_0_7_load_151 | 109 | 0.0014276 | 0.00035779 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2-5_0_7_load_74 | 110 | 0.0045898 | 0.0011503 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2-5_0_7_load_79 | 112 | 0.0074169 | 0.0018588 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2-5_0_7_load_82 | 116 | 0.0046027 | 0.0011536 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2-5_0_7_load_83 | 117 | 0.005146 | 0.0012897 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2-5_0_7_load_81 | 118 | 0.004245 | 0.0010639 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2-5_0_7_load_121 | 119 | 0.0057444 | 0.0014397 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2-5_0_7_load_119 | 120 | 0.0025906 | 0.00064926 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2-5_0_7_load_114 | 121 | 0.00098404 | 0.00024662 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2-5_0_7_load_85 | 122 | 0.0068386 | 0.0017139 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2-5_0_7_load_107 | 123 | 0.0037194 | 0.00093217 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2-5_0_7_load_122 | 124 | 0.0022607 | 0.00056659 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2-5_0_7_load_86 | 125 | 0.0014181 | 0.0003554 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2-5_0_7_load_87 | 126 | 0.0013926 | 0.00034902 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2-5_0_7_load_89 | 127 | 0.0013943 | 0.00034944 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2-5_0_7_load_91 | 128 | 0.0013789 | 0.00034558 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2-5_0_7_load_150 | 129 | 0.0013865 | 0.00034749 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2-5_0_7_load_149 | 130 | 0.0013773 | 0.00034519 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2-5_0_7_load_93 | 131 | 0.0024148 | 0.00060521 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2-5_0_7_load_94 | 132 | 0.0050391 | 0.0012629 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2-5_0_7_load_95 | 133 | 0.0014749 | 0.00036965 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2-5_0_7_load_96 | 134 | 0.0022369 | 0.00056062 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2-5_0_7_load_97 | 135 | 0.0011575 | 0.0002901 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2-5_0_7_load_98 | 136 | 0.0045712 | 0.0011456 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2-5_0_7_load_99 | 137 | 0.0011547 | 0.00028939 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2-5_0_7_load_100 | 138 | 0.0019068 | 0.00047788 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2-5_0_7_load_101 | 139 | 0.0012776 | 0.00032019 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2-5_0_7_load_102 | 140 | 0.0015113 | 0.00037877 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2-5_0_7_load_117 | 142 | 0.00088378 | 0.0002215 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2-5_0_7_load_124 | 143 | 0.0014324 | 0.000359 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2-5_0_7_line_0 |  | 0 | 1 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2-5_0_7_line_1 |  | 0 | 2 | 0.002568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2-5_0_7_line_2 |  | 1 | 3 | 0.011157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2-5_0_7_line_3 |  | 1 | 4 | 0.13138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2-5_0_7_line_4 |  | 2 | 5 | 0.028318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2-5_0_7_line_5 |  | 3 | 6 | 0.04963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2-5_0_7_line_6 |  | 4 | 7 | 0.031656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2-5_0_7_line_7 |  | 5 | 8 | 0.016173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2-5_0_7_line_8 |  | 6 | 9 | 0.026383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2-5_0_7_line_9 |  | 6 | 10 | 0.025161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2-5_0_7_line_10 |  | 7 | 19 | 0.002851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2-5_0_7_line_11 |  | 8 | 16 | 0.03317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2-5_0_7_line_12 |  | 9 | 17 | 0.0053826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2-5_0_7_line_13 |  | 10 | 18 | 0.015941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2-5_0_7_line_14 |  | 11 | 12 | 0.011832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2-5_0_7_line_15 |  | 11 | 13 | 0.0040841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2-5_0_7_line_16 |  | 12 | 14 | 0.0091042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2-5_0_7_line_17 |  | 13 | 15 | 0.031241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2-5_0_7_line_18 |  | 14 | 21 | 0.00074893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2-5_0_7_line_19 |  | 15 | 37 | 0.030528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2-5_0_7_line_20 |  | 15 | 38 | 0.060079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2-5_0_7_line_21 |  | 16 | 23 | 0.11381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2-5_0_7_line_22 |  | 16 | 24 | 0.042182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2-5_0_7_line_23 |  | 17 | 58 | 0.005398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2-5_0_7_line_24 |  | 18 | 49 | 0.040778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2-5_0_7_line_25 |  | 19 | 20 | 0.027809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2-5_0_7_line_26 |  | 19 | 21 | 0.019712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2-5_0_7_line_27 |  | 20 | 22 | 0.013203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2-5_0_7_line_28 |  | 22 | 92 | 0.0010335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2-5_0_7_line_29 |  | 24 | 26 | 0.023111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2-5_0_7_line_30 |  | 25 | 26 | 0.014348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2-5_0_7_line_31 |  | 25 | 27 | 0.031432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2-5_0_7_line_32 |  | 27 | 28 | 0.05919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2-5_0_7_line_33 |  | 29 | 30 | 0.006308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2-5_0_7_line_34 |  | 30 | 33 | 0.0014084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2-5_0_7_line_35 |  | 31 | 32 | 0.03483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2-5_0_7_line_36 |  | 32 | 34 | 0.049473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2-5_0_7_line_37 |  | 33 | 35 | 0.011559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2-5_0_7_line_38 |  | 34 | 36 | 0.022533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2-5_0_7_line_39 |  | 35 | 44 | 0.0048296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2-5_0_7_line_40 |  | 36 | 123 | 0.013247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2-5_0_7_line_41 |  | 37 | 39 | 0.026498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2-5_0_7_line_42 |  | 38 | 94 | 0.037275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2-5_0_7_line_43 |  | 39 | 40 | 0.0037593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2-5_0_7_line_44 |  | 40 | 43 | 0.0056485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2-5_0_7_line_45 |  | 41 | 42 | 0.0042906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2-5_0_7_line_46 |  | 42 | 43 | 0.0051027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2-5_0_7_line_47 |  | 44 | 45 | 0.038957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2-5_0_7_line_48 |  | 45 | 46 | 0.0097323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2-5_0_7_line_49 |  | 46 | 47 | 0.017431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2-5_0_7_line_50 |  | 47 | 48 | 0.0088257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2-5_0_7_line_51 |  | 48 | 136 | 0.010994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2-5_0_7_line_52 |  | 49 | 50 | 0.018053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2-5_0_7_line_53 |  | 50 | 51 | 0.017287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2-5_0_7_line_54 |  | 51 | 54 | 0.015764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2-5_0_7_line_55 |  | 51 | 55 | 0.008955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_2-5_0_7_line_56 |  | 52 | 53 | 0.0083606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2-5_0_7_line_57 |  | 53 | 56 | 0.0093337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2-5_0_7_line_58 |  | 53 | 57 | 0.017374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2-5_0_7_line_59 |  | 54 | 59 | 0.016443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2-5_0_7_line_60 |  | 55 | 60 | 0.017766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2-5_0_7_line_61 |  | 55 | 61 | 0.038026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2-5_0_7_line_62 |  | 56 | 62 | 0.014686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2-5_0_7_line_63 |  | 57 | 63 | 0.005121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2-5_0_7_line_64 |  | 58 | 82 | 0.0054149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2-5_0_7_line_65 |  | 59 | 140 | 0.0033147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2-5_0_7_line_66 |  | 60 | 71 | 0.0022719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2-5_0_7_line_67 |  | 61 | 67 | 0.011303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2-5_0_7_line_68 |  | 61 | 64 | 0.020806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_2-5_0_7_line_69 |  | 62 | 102 | 0.0095533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2-5_0_7_line_70 |  | 63 | 90 | 0.013984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2-5_0_7_line_71 |  | 64 | 65 | 0.013999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2-5_0_7_line_72 |  | 65 | 66 | 0.0028802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2-5_0_7_line_73 |  | 66 | 68 | 0.0069269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2-5_0_7_line_74 |  | 67 | 69 | 0.022713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2-5_0_7_line_75 |  | 68 | 70 | 0.025548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2-5_0_7_line_76 |  | 70 | 72 | 0.0010344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2-5_0_7_line_77 |  | 71 | 73 | 0.019324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2-5_0_7_line_78 |  | 72 | 74 | 0.005847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2-5_0_7_line_79 |  | 73 | 107 | 0.0053789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2-5_0_7_line_80 |  | 74 | 75 | 0.018742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2-5_0_7_line_81 |  | 75 | 76 | 0.014852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2-5_0_7_line_82 |  | 76 | 77 | 0.019296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2-5_0_7_line_83 |  | 77 | 78 | 0.003511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2-5_0_7_line_84 |  | 77 | 79 | 0.021971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2-5_0_7_line_85 |  | 78 | 113 | 0.027685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2-5_0_7_line_86 |  | 79 | 110 | 0.017332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2-5_0_7_line_87 |  | 80 | 81 | 0.019901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2-5_0_7_line_88 |  | 81 | 82 | 0.0054933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2-5_0_7_line_89 |  | 83 | 84 | 0.00997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2-5_0_7_line_90 |  | 83 | 85 | 0.046397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2-5_0_7_line_91 |  | 84 | 86 | 0.023308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2-5_0_7_line_92 |  | 84 | 87 | 0.017067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2-5_0_7_line_93 |  | 85 | 88 | 0.014296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2-5_0_7_line_94 |  | 86 | 89 | 0.0054948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2-5_0_7_line_95 |  | 87 | 90 | 0.014034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2-5_0_7_line_96 |  | 89 | 91 | 0.0059668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2-5_0_7_line_97 |  | 91 | 97 | 0.0054438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2-5_0_7_line_98 |  | 92 | 93 | 0.045809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2-5_0_7_line_99 |  | 94 | 95 | 0.0018853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2-5_0_7_line_100 |  | 95 | 96 | 0.012118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2-5_0_7_line_101 |  | 97 | 125 | 0.0076856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2-5_0_7_line_102 |  | 98 | 99 | 0.083788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2-5_0_7_line_103 |  | 99 | 121 | 0.072429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2-5_0_7_line_104 |  | 99 | 112 | 0.023287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2-5_0_7_line_105 |  | 100 | 101 | 0.0017756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2-5_0_7_line_106 |  | 100 | 102 | 0.0019541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2-5_0_7_line_107 |  | 101 | 103 | 0.019012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2-5_0_7_line_108 |  | 102 | 104 | 0.02741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2-5_0_7_line_109 |  | 103 | 105 | 0.005518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2-5_0_7_line_110 |  | 104 | 106 | 0.0053656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2-5_0_7_line_111 |  | 105 | 107 | 0.0053944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2-5_0_7_line_112 |  | 106 | 108 | 0.0054009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2-5_0_7_line_113 |  | 108 | 109 | 0.0054988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2-5_0_7_line_114 |  | 110 | 111 | 0.029558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2-5_0_7_line_115 |  | 111 | 112 | 0.0019999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2-5_0_7_line_116 |  | 113 | 117 | 0.0095676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2-5_0_7_line_117 |  | 113 | 118 | 0.01958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2-5_0_7_line_118 |  | 114 | 115 | 0.029522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2-5_0_7_line_119 |  | 114 | 116 | 0.029666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2-5_0_7_line_120 |  | 115 | 119 | 0.0062609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2-5_0_7_line_121 |  | 115 | 120 | 0.022186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2-5_0_7_line_122 |  | 116 | 118 | 0.01735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2-5_0_7_line_123 |  | 117 | 122 | 0.021788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2-5_0_7_line_124 |  | 119 | 124 | 0.028565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2-5_0_7_line_125 |  | 121 | 141 | 0.029706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2-5_0_7_line_126 |  | 122 | 123 | 0.032582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2-5_0_7_line_127 |  | 125 | 126 | 0.0054839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2-5_0_7_line_128 |  | 126 | 127 | 0.0054293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2-5_0_7_line_129 |  | 127 | 128 | 0.005403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2-5_0_7_line_130 |  | 128 | 129 | 0.0053935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2-5_0_7_line_131 |  | 129 | 130 | 0.0053945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2-5_0_7_line_132 |  | 130 | 143 | 0.0054815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2-5_0_7_line_133 |  | 131 | 132 | 0.0029076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2-5_0_7_line_134 |  | 131 | 133 | 0.018144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2-5_0_7_line_135 |  | 132 | 134 | 0.016037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2-5_0_7_line_136 |  | 133 | 135 | 0.0096161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2-5_0_7_line_137 |  | 134 | 136 | 0.020943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2-5_0_7_line_138 |  | 135 | 137 | 0.0052105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2-5_0_7_line_139 |  | 137 | 138 | 0.0039795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2-5_0_7_line_140 |  | 138 | 139 | 0.0072026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2-5_0_7_line_141 |  | 139 | 140 | 0.0037696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2-5_0_7_line_142 |  | 141 | 142 | 0.039253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2-5_0_7_trafo_1 | 0.63 MVA 20/0.4 kV | 144 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2677108.0466 | 1236822.0315 | 2677118.2116 | 1236810.2439
1 | 2677108.0466 | 1236822.0315 | 2677106.3695 | 1236823.9763
2 | 2677118.2116 | 1236810.2439 | 2677125.4978 | 1236801.7945
3 | 2677118.2116 | 1236810.2439 | 2677220.1591 | 1236893.1097
4 | 2677106.3695 | 1236823.9763 | 2677089.4188 | 1236843.6331 | 2677088.0439 | 1236845.5535
5 | 2677161.46 | 1236767.5933 | 2677125.6115 | 1236801.6626 | 2677125.4978 | 1236801.7945
6 | 2677220.1591 | 1236893.1097 | 2677231.7512 | 1236886.7337 | 2677249.4391 | 1236881.5716
7 | 2677078.6295 | 1236858.7036 | 2677088.0439 | 1236845.5535
8 | 2677161.46 | 1236767.5933 | 2677180.4027 | 1236749.2287
9 | 2677161.46 | 1236767.5933 | 2677155.0266 | 1236758.9704 | 2677150.326 | 1236745.3566
10 | 2677252.1759 | 1236880.7729 | 2677249.4391 | 1236881.5716
11 | 2677078.6295 | 1236858.7036 | 2677075.5414 | 1236869.2598 | 2677075.4099 | 1236881.133 | 2677077.2458 | 1236891.2638
12 | 2677184.2673 | 1236745.4821 | 2677180.4027 | 1236749.2287
13 | 2677150.326 | 1236745.3566 | 2677145.1233 | 1236730.2885
14 | 2677263.3052 | 1236920.6454 | 2677260.1244 | 1236909.2493
15 | 2677263.3052 | 1236920.6454 | 2677264.4032 | 1236924.5791
16 | 2677257.6767 | 1236900.4804 | 2677260.1244 | 1236909.2493
17 | 2677272.8024 | 1236954.6703 | 2677264.4032 | 1236924.5791
18 | 2677257.6767 | 1236900.4804 | 2677257.4754 | 1236899.759
19 | 2677272.8024 | 1236954.6703 | 2677251.5012 | 1236957.6398 | 2677242.4665 | 1236958.8009
20 | 2677272.8024 | 1236954.6703 | 2677317.0337 | 1236946.251 | 2677331.8182 | 1236943.4192
21 | 2677077.2458 | 1236891.2638 | 2677077.9493 | 1237005.0668
22 | 2677077.2458 | 1236891.2638 | 2677035.3645 | 1236886.2361
23 | 2677188.1429 | 1236741.7247 | 2677184.2673 | 1236745.4821
24 | 2677133.5087 | 1236691.1995 | 2677145.1233 | 1236730.2885
25 | 2677252.1759 | 1236880.7729 | 2677278.9426 | 1236873.2297
26 | 2677252.1759 | 1236880.7729 | 2677257.4754 | 1236899.759
27 | 2677291.6504 | 1236869.6485 | 2677278.9426 | 1236873.2297
28 | 2677291.6504 | 1236869.6485 | 2677292.6452 | 1236869.3681
29 | 2677012.4185 | 1236883.4816 | 2677035.3645 | 1236886.2361
30 | 2676998.1728 | 1236881.7714 | 2677012.4185 | 1236883.4816
31 | 2676966.9646 | 1236878.025 | 2676998.1728 | 1236881.7714
32 | 2676966.9646 | 1236878.025 | 2676957.6889 | 1236936.4836
33 | 2676989.8557 | 1236817.6185 | 2676991.0823 | 1236811.4309
34 | 2676991.0823 | 1236811.4309 | 2676991.3562 | 1236810.0494 | 2676991.3562 | 1236810.0494
35 | 2676903.0648 | 1236797.2415 | 2676935.5926 | 1236809.6935
36 | 2676903.0648 | 1236797.2415 | 2676912.6759 | 1236769.113 | 2676917.2161 | 1236749.8945
37 | 2676991.3562 | 1236810.0494 | 2676992.6812 | 1236798.5669
38 | 2676917.2161 | 1236749.8945 | 2676918.9687 | 1236742.476 | 2676921.7867 | 1236736.9754 | 2676925.8156 | 1236729.231
39 | 2676993.2349 | 1236793.7691 | 2676992.6812 | 1236798.5669
40 | 2676932.1026 | 1236717.582 | 2676931.0603 | 1236719.1497 | 2676925.8156 | 1236729.231
41 | 2677242.4665 | 1236958.8009 | 2677238.7209 | 1236949.5013 | 2677237.2757 | 1236945.4241 | 2677235.5394 | 1236943.3668 | 2677233.1829 | 1236941.8684 | 2677229.7802 | 1236941.6908 | 2677226.615 | 1236942.4501
42 | 2677331.8182 | 1236943.4192 | 2677323.4962 | 1236907.085
43 | 2677226.615 | 1236942.4501 | 2677226.615 | 1236942.4501 | 2677223.7429 | 1236944.8757
44 | 2677223.7429 | 1236944.8757 | 2677219.4275 | 1236948.5202
45 | 2677212.7446 | 1236955.0769 | 2677215.529 | 1236951.8126
46 | 2677219.4275 | 1236948.5202 | 2677215.529 | 1236951.8126 | 2677215.529 | 1236951.8126
47 | 2677001.122 | 1236755.6474 | 2676999.7581 | 1236760.8352 | 2676993.8199 | 1236788.6998 | 2676993.2349 | 1236793.7691
48 | 2677003.5967 | 1236746.2349 | 2677001.122 | 1236755.6474
49 | 2677003.5967 | 1236746.2349 | 2677008.0288 | 1236729.3769
50 | 2677008.0288 | 1236729.3769 | 2677008.6729 | 1236726.9272 | 2677012.261 | 1236721.7577
51 | 2677019.7612 | 1236713.8847 | 2677015.2659 | 1236717.4283 | 2677012.261 | 1236721.7577
52 | 2677133.5087 | 1236691.1995 | 2677129.8225 | 1236673.527
53 | 2677126.2927 | 1236656.604 | 2677129.8225 | 1236673.527
54 | 2677126.2927 | 1236656.604 | 2677110.7259 | 1236659.0901
55 | 2677126.2927 | 1236656.604 | 2677125.4777 | 1236647.6873
56 | 2677181.5961 | 1236672.0996 | 2677180.4653 | 1236680.3834
57 | 2677181.5961 | 1236672.0996 | 2677182.8587 | 1236662.8517
58 | 2677181.5961 | 1236672.0996 | 2677188.8703 | 1236673.0948 | 2677198.8113 | 1236674.4461
59 | 2677094.9329 | 1236663.5488 | 2677097.4837 | 1236662.5009 | 2677108.5867 | 1236659.4318 | 2677110.7259 | 1236659.0901
60 | 2677125.4777 | 1236647.6873 | 2677143.0185 | 1236644.869
61 | 2677118.0514 | 1236611.21 | 2677122.2749 | 1236616.9577 | 2677123.1005 | 1236625.6411 | 2677125.4777 | 1236647.6873
62 | 2677182.8587 | 1236662.8517 | 2677184.8452 | 1236648.301
63 | 2677198.8113 | 1236674.4461 | 2677199.2718 | 1236674.5087 | 2677203.8856 | 1236675.1359
64 | 2677192.0307 | 1236737.9556 | 2677188.1429 | 1236741.7247
65 | 2677094.9329 | 1236663.5488 | 2677091.8669 | 1236664.8083
66 | 2677145.2617 | 1236644.5086 | 2677143.0185 | 1236644.869
67 | 2677118.0514 | 1236611.21 | 2677128.3944 | 1236606.6522
68 | 2677118.0514 | 1236611.21 | 2677112.3062 | 1236609.0117 | 2677102.4969 | 1236610.352 | 2677097.7666 | 1236610.8306
69 | 2677186.1375 | 1236638.8355 | 2677184.8452 | 1236648.301
70 | 2677203.8856 | 1236675.1359 | 2677217.7418 | 1236677.0197
71 | 2677097.7666 | 1236610.8306 | 2677085.1604 | 1236612.1061 | 2677083.8439 | 1236612.2812
72 | 2677080.9888 | 1236612.661 | 2677083.8439 | 1236612.2812
73 | 2677080.9888 | 1236612.661 | 2677074.1225 | 1236613.5746
74 | 2677128.3944 | 1236606.6522 | 2677148.2422 | 1236603.2297 | 2677150.791 | 1236602.8826
75 | 2677049.3269 | 1236619.5225 | 2677050.4198 | 1236619.0825 | 2677068.2564 | 1236614.355 | 2677074.1225 | 1236613.5746
76 | 2677048.3672 | 1236619.9088 | 2677049.3269 | 1236619.5225
77 | 2677158.657 | 1236636.5282 | 2677148.6739 | 1236647.466 | 2677145.2617 | 1236644.5086 | 2677145.2617 | 1236644.5086
78 | 2677048.3672 | 1236619.9088 | 2677042.9432 | 1236622.0923
79 | 2677162.2831 | 1236632.5553 | 2677158.657 | 1236636.5282
80 | 2677026.087 | 1236630.183 | 2677033.6694 | 1236625.8255 | 2677042.9432 | 1236622.0923
81 | 2677026.087 | 1236630.183 | 2677016.584 | 1236635.6442 | 2677013.4952 | 1236638.0113
82 | 2676998.1794 | 1236649.7488 | 2677013.4952 | 1236638.0113
83 | 2676998.1794 | 1236649.7488 | 2676995.5383 | 1236652.0621
84 | 2676998.1794 | 1236649.7488 | 2676986.9068 | 1236630.8896
85 | 2676974.7121 | 1236670.3034 | 2676995.5383 | 1236652.0621
86 | 2676986.9068 | 1236630.8896 | 2676984.3395 | 1236632.2128 | 2676981.4686 | 1236626.6051 | 2676983.7084 | 1236625.4444 | 2676981.0636 | 1236620.4845
87 | 2677195.9748 | 1236734.1319 | 2677210.2631 | 1236720.2797
88 | 2677195.9748 | 1236734.1319 | 2677192.0307 | 1236737.9556
89 | 2677241.4989 | 1236688.267 | 2677248.56 | 1236681.2095
90 | 2677241.4989 | 1236688.267 | 2677281 | 1236702.7241 | 2677284.431 | 1236705.3715
91 | 2677248.56 | 1236681.2095 | 2677265.0483 | 1236664.7358
92 | 2677248.56 | 1236681.2095 | 2677231.6483 | 1236678.9103
93 | 2677284.431 | 1236705.3715 | 2677293.7661 | 1236712.5748 | 2677295.4901 | 1236710.7572
94 | 2677265.0483 | 1236664.7358 | 2677268.9354 | 1236660.8522
95 | 2677217.7418 | 1236677.0197 | 2677231.6483 | 1236678.9103
96 | 2677273.0663 | 1236656.5472 | 2677270.0039 | 1236659.7846 | 2677268.9354 | 1236660.8522
97 | 2677276.8074 | 1236652.5925 | 2677273.0663 | 1236656.5472
98 | 2677292.6452 | 1236869.3681 | 2677303.8048 | 1236866.2232 | 2677322.0053 | 1236863.725 | 2677337.8473 | 1236863.4977
99 | 2677323.4962 | 1236907.085 | 2677323.0753 | 1236905.2473
100 | 2677320.3699 | 1236893.4355 | 2677323.0753 | 1236905.2473
101 | 2677282.089 | 1236647.0091 | 2677276.8074 | 1236652.5925
102 | 2676985.8831 | 1236588.4469 | 2677034.9424 | 1236570.2813 | 2677059.8612 | 1236563.8778 | 2677065.6039 | 1236563.6965
103 | 2676985.8831 | 1236588.4469 | 2676986.0732 | 1236578.4536 | 2677024.2776 | 1236540.1444 | 2677030.2612 | 1236534.3484
104 | 2676985.8831 | 1236588.4469 | 2676968.1242 | 1236598.2681 | 2676965.8535 | 1236600.2183
105 | 2677183.424 | 1236636.2766 | 2677184.7158 | 1236637.4948
106 | 2677186.1375 | 1236638.8355 | 2677184.7158 | 1236637.4948
107 | 2677183.424 | 1236636.2766 | 2677170.237 | 1236623.8408 | 2677169.6396 | 1236624.4953
108 | 2677186.1375 | 1236638.8355 | 2677193.7453 | 1236646.1839 | 2677205.215 | 1236633.8638
109 | 2677169.6396 | 1236624.4953 | 2677165.9197 | 1236628.571
110 | 2677208.8711 | 1236629.9366 | 2677205.215 | 1236633.8638
111 | 2677165.9197 | 1236628.571 | 2677162.2831 | 1236632.5553
112 | 2677212.5513 | 1236625.9836 | 2677208.8711 | 1236629.9366
113 | 2677216.2981 | 1236621.959 | 2677212.5513 | 1236625.9836
114 | 2676964.3363 | 1236601.5213 | 2676977.052 | 1236622.9009 | 2676981.0636 | 1236620.4845 | 2676981.0636 | 1236620.4845
115 | 2676964.3363 | 1236601.5213 | 2676965.8535 | 1236600.2183
116 | 2676974.7121 | 1236670.3034 | 2676967.4794 | 1236676.5665
117 | 2676974.7121 | 1236670.3034 | 2676972.8123 | 1236661.5839 | 2676964.8835 | 1236654.4651
118 | 2676915.7272 | 1236656.2409 | 2676934.5243 | 1236633.4351
119 | 2676934.5243 | 1236633.4351 | 2676952.7046 | 1236649.4706 | 2676956.3436 | 1236645.4482
120 | 2676915.7272 | 1236656.2409 | 2676913.3943 | 1236661.0807 | 2676913.009 | 1236661.881
121 | 2676915.7272 | 1236656.2409 | 2676903.748 | 1236639.3297 | 2676902.9031 | 1236638.1371
122 | 2676964.8835 | 1236654.4651 | 2676963.2452 | 1236655.9227 | 2676958.0962 | 1236651.5085 | 2676960.0962 | 1236648.9993 | 2676956.3436 | 1236645.4482
123 | 2676967.4794 | 1236676.5665 | 2676962.0235 | 1236681.2911 | 2676951.9779 | 1236691.8459
124 | 2676913.009 | 1236661.881 | 2676900.6158 | 1236687.6179
125 | 2677051.5984 | 1236513.6802 | 2677030.2612 | 1236534.3484
126 | 2676932.1026 | 1236717.582 | 2676939.3643 | 1236706.6597 | 2676948.8207 | 1236695.1631 | 2676951.9779 | 1236691.8459
127 | 2677282.089 | 1236647.0091 | 2677285.8575 | 1236643.0253
128 | 2677289.5886 | 1236639.081 | 2677285.8575 | 1236643.0253
129 | 2677293.3016 | 1236635.156 | 2677289.5886 | 1236639.081
130 | 2677297.008 | 1236631.2378 | 2677293.3016 | 1236635.156
131 | 2677300.7151 | 1236627.3189 | 2677297.008 | 1236631.2378
132 | 2677304.482 | 1236623.3368 | 2677300.7151 | 1236627.3189
133 | 2677052.4853 | 1236691.8117 | 2677050.1782 | 1236693.5812
134 | 2677052.4853 | 1236691.8117 | 2677066.8823 | 1236680.7689
135 | 2677050.1782 | 1236693.5812 | 2677037.4537 | 1236703.3412
136 | 2677066.8823 | 1236680.7689 | 2677074.5124 | 1236674.9164
137 | 2677037.4537 | 1236703.3412 | 2677035.3747 | 1236704.9359 | 2677028.6986 | 1236706.8395 | 2677019.7612 | 1236713.8847
138 | 2677078.8086 | 1236671.9762 | 2677076.044 | 1236673.7417 | 2677074.5124 | 1236674.9164
139 | 2677078.8086 | 1236671.9762 | 2677082.1626 | 1236669.8344
140 | 2677082.1626 | 1236669.8344 | 2677086.7265 | 1236666.92 | 2677088.38 | 1236666.2407
141 | 2677091.8669 | 1236664.8083 | 2677088.38 | 1236666.2407
142 | 2677051.5984 | 1236513.6802 | 2677079.4056 | 1236485.8994

## bus_geodata
| x | y | coords
0 | 2677108.0466 | 1236822.0315
1 | 2677118.2116 | 1236810.2439
2 | 2677106.3695 | 1236823.9763
3 | 2677125.4978 | 1236801.7945
4 | 2677220.1591 | 1236893.1097
5 | 2677088.0439 | 1236845.5535
6 | 2677161.46 | 1236767.5933
7 | 2677249.4391 | 1236881.5716
8 | 2677078.6295 | 1236858.7036
9 | 2677180.4027 | 1236749.2287
10 | 2677150.326 | 1236745.3566
11 | 2677263.3052 | 1236920.6454
12 | 2677260.1244 | 1236909.2493
13 | 2677264.4032 | 1236924.5791
14 | 2677257.6767 | 1236900.4804
15 | 2677272.8024 | 1236954.6703
16 | 2677077.2458 | 1236891.2638
17 | 2677184.2673 | 1236745.4821
18 | 2677145.1233 | 1236730.2885
19 | 2677252.1759 | 1236880.7729
20 | 2677278.9426 | 1236873.2297
21 | 2677257.4754 | 1236899.759
22 | 2677291.6504 | 1236869.6485
23 | 2677077.9493 | 1237005.0668
24 | 2677035.3645 | 1236886.2361
25 | 2676998.1728 | 1236881.7714
26 | 2677012.4185 | 1236883.4816
27 | 2676966.9646 | 1236878.025
28 | 2676957.6889 | 1236936.4836
29 | 2676989.8557 | 1236817.6185
30 | 2676991.0823 | 1236811.4309
31 | 2676935.5926 | 1236809.6935
32 | 2676903.0648 | 1236797.2415
33 | 2676991.3562 | 1236810.0494
34 | 2676917.2161 | 1236749.8945
35 | 2676992.6812 | 1236798.5669
36 | 2676925.8156 | 1236729.231
37 | 2677242.4665 | 1236958.8009
38 | 2677331.8182 | 1236943.4192
39 | 2677226.615 | 1236942.4501
40 | 2677223.7429 | 1236944.8757
41 | 2677212.7446 | 1236955.0769
42 | 2677215.529 | 1236951.8126
43 | 2677219.4275 | 1236948.5202
44 | 2676993.2349 | 1236793.7691
45 | 2677001.122 | 1236755.6474
46 | 2677003.5967 | 1236746.2349
47 | 2677008.0288 | 1236729.3769
48 | 2677012.261 | 1236721.7577
49 | 2677133.5087 | 1236691.1995
50 | 2677129.8225 | 1236673.527
51 | 2677126.2927 | 1236656.604
52 | 2677180.4653 | 1236680.3834
53 | 2677181.5961 | 1236672.0996
54 | 2677110.7259 | 1236659.0901
55 | 2677125.4777 | 1236647.6873
56 | 2677182.8587 | 1236662.8517
57 | 2677198.8113 | 1236674.4461
58 | 2677188.1429 | 1236741.7247
59 | 2677094.9329 | 1236663.5488
60 | 2677143.0185 | 1236644.869
61 | 2677118.0514 | 1236611.21
62 | 2677184.8452 | 1236648.301
63 | 2677203.8856 | 1236675.1359
64 | 2677097.7666 | 1236610.8306
65 | 2677083.8439 | 1236612.2812
66 | 2677080.9888 | 1236612.661
67 | 2677128.3944 | 1236606.6522
68 | 2677074.1225 | 1236613.5746
69 | 2677150.791 | 1236602.8826
70 | 2677049.3269 | 1236619.5225
71 | 2677145.2617 | 1236644.5086
72 | 2677048.3672 | 1236619.9088
73 | 2677158.657 | 1236636.5282
74 | 2677042.9432 | 1236622.0923
75 | 2677026.087 | 1236630.183
76 | 2677013.4952 | 1236638.0113
77 | 2676998.1794 | 1236649.7488
78 | 2676995.5383 | 1236652.0621
79 | 2676986.9068 | 1236630.8896
80 | 2677210.2631 | 1236720.2797
81 | 2677195.9748 | 1236734.1319
82 | 2677192.0307 | 1236737.9556
83 | 2677241.4989 | 1236688.267
84 | 2677248.56 | 1236681.2095
85 | 2677284.431 | 1236705.3715
86 | 2677265.0483 | 1236664.7358
87 | 2677231.6483 | 1236678.9103
88 | 2677295.4901 | 1236710.7572
89 | 2677268.9354 | 1236660.8522
90 | 2677217.7418 | 1236677.0197
91 | 2677273.0663 | 1236656.5472
92 | 2677292.6452 | 1236869.3681
93 | 2677337.8473 | 1236863.4977
94 | 2677323.4962 | 1236907.085
95 | 2677323.0753 | 1236905.2473
96 | 2677320.3699 | 1236893.4355
97 | 2677276.8074 | 1236652.5925
98 | 2677065.6039 | 1236563.6965
99 | 2676985.8831 | 1236588.4469
100 | 2677184.7158 | 1236637.4948
101 | 2677183.424 | 1236636.2766
102 | 2677186.1375 | 1236638.8355
103 | 2677169.6396 | 1236624.4953
104 | 2677205.215 | 1236633.8638
105 | 2677165.9197 | 1236628.571
106 | 2677208.8711 | 1236629.9366
107 | 2677162.2831 | 1236632.5553
108 | 2677212.5513 | 1236625.9836
109 | 2677216.2981 | 1236621.959
110 | 2676981.0636 | 1236620.4845
111 | 2676964.3363 | 1236601.5213
112 | 2676965.8535 | 1236600.2183
113 | 2676974.7121 | 1236670.3034
114 | 2676934.5243 | 1236633.4351
115 | 2676915.7272 | 1236656.2409
116 | 2676956.3436 | 1236645.4482
117 | 2676967.4794 | 1236676.5665
118 | 2676964.8835 | 1236654.4651
119 | 2676913.009 | 1236661.881
120 | 2676902.9031 | 1236638.1371
121 | 2677030.2612 | 1236534.3484
122 | 2676951.9779 | 1236691.8459
123 | 2676932.1026 | 1236717.582
124 | 2676900.6158 | 1236687.6179
125 | 2677282.089 | 1236647.0091
126 | 2677285.8575 | 1236643.0253
127 | 2677289.5886 | 1236639.081
128 | 2677293.3016 | 1236635.156
129 | 2677297.008 | 1236631.2378
130 | 2677300.7151 | 1236627.3189
131 | 2677052.4853 | 1236691.8116
132 | 2677050.1782 | 1236693.5812
133 | 2677066.8823 | 1236680.7689
134 | 2677037.4537 | 1236703.3412
135 | 2677074.5124 | 1236674.9164
136 | 2677019.7612 | 1236713.8847
137 | 2677078.8086 | 1236671.9762
138 | 2677082.1626 | 1236669.8344
139 | 2677088.38 | 1236666.2407
140 | 2677091.8669 | 1236664.8083
141 | 2677051.5984 | 1236513.6802
142 | 2677079.4056 | 1236485.8994
143 | 2677304.482 | 1236623.3368
144 | 2677161.46 | 1236767.5933

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99923 | -0.014629 | 0.0052132 | 0.0013065
1 | 1 | 0 | -0.48188 | -0.12313
2 | 0.99911 | -0.016967 | 0.0027203 | 0.00068176
3 | 0.99904 | -0.018121 | 0.0049528 | 0.0012413
4 | 0.99615 | -0.07394 | 0 | 0
5 | 0.99778 | -0.042334 | 0.0016632 | 0.00041684
6 | 0.99483 | -0.097711 | 0 | 0
7 | 0.99522 | -0.09184 | 0.0018099 | 0.00045361
8 | 0.99702 | -0.056694 | 0 | 0
9 | 0.99455 | -0.10309 | 0.0014439 | 0.00036188
10 | 0.99278 | -0.1366 | 0.001525 | 0.0003822
11 | 0.99431 | -0.10934 | 0.0024928 | 0.00062474
12 | 0.99452 | -0.10531 | 0.0018137 | 0.00045456
13 | 0.99425 | -0.11055 | 0.0015043 | 0.00037702
14 | 0.9947 | -0.10192 | 0.00064248 | 0.00016102
15 | 0.99381 | -0.11899 | 0 | 0
16 | 0.99471 | -0.10101 | 0 | 0
17 | 0.9945 | -0.10405 | 0.00144 | 0.00036089
18 | 0.99149 | -0.16118 | 0.013856 | 0.0034727
19 | 0.99514 | -0.093363 | 0 | 0
20 | 0.99497 | -0.096555 | 0.0006482 | 0.00016245
21 | 0.99471 | -0.10164 | 0.0020607 | 0.00051646
22 | 0.9949 | -0.097919 | 0.0024571 | 0.00061582
23 | 0.99075 | -0.17752 | 0.038013 | 0.0095271
24 | 0.9903 | -0.18611 | 0.012375 | 0.0031015
25 | 0.98764 | -0.23771 | 0.021663 | 0.0054294
26 | 0.98814 | -0.22795 | 0.063551 | 0.015927
27 | 0.98716 | -0.24695 | 0 | 0
28 | 0.98627 | -0.26435 | 0.016427 | 0.004117
29 | 0.97636 | -0.45478 | 0.0086476 | 0.0021673
30 | 0.97641 | -0.45379 | 0.0043859 | 0.0010992
31 | 0.97128 | -0.55408 | 0.0055462 | 0.00139
32 | 0.97146 | -0.55051 | 0 | 0
33 | 0.97643 | -0.45345 | 0.0012873 | 0.00032262
34 | 0.97172 | -0.54544 | 0.0038393 | 0.00096222
35 | 0.97658 | -0.45043 | 0.013402 | 0.0033588
36 | 0.97192 | -0.54154 | 0.0049285 | 0.0012352
37 | 0.99362 | -0.12281 | 0 | 0
38 | 0.99336 | -0.12772 | 0 | 0
39 | 0.99344 | -0.12612 | 0.0023785 | 0.00059612
40 | 0.99343 | -0.12644 | 0.001007 | 0.00025237
41 | 0.99339 | -0.12717 | 0.0016704 | 0.00041865
42 | 0.9934 | -0.12705 | 0.001004 | 0.00025162
43 | 0.99341 | -0.12681 | 0.0010242 | 0.0002567
44 | 0.9767 | -0.44798 | 0.0021032 | 0.00052711
45 | 0.97778 | -0.42677 | 0.0016229 | 0.00040673
46 | 0.97807 | -0.42119 | 0.0038495 | 0.00096477
47 | 0.97864 | -0.40999 | 0.0022524 | 0.0005645
48 | 0.97895 | -0.40396 | 0.002195 | 0.00055013
49 | 0.98837 | -0.22098 | 0 | 0
50 | 0.98699 | -0.24758 | 0.0026031 | 0.0006524
51 | 0.98568 | -0.27285 | 0 | 0
52 | 0.97836 | -0.41544 | 0.0059062 | 0.0014802
53 | 0.9784 | -0.41454 | 0 | 0
54 | 0.98471 | -0.2916 | 0.0025805 | 0.00064674
55 | 0.98518 | -0.28241 | 0 | 0
56 | 0.97881 | -0.40647 | 0.00528 | 0.0013233
57 | 0.97773 | -0.42771 | 0.0048882 | 0.0012251
58 | 0.99445 | -0.10488 | 0.0014565 | 0.00036502
59 | 0.98374 | -0.31043 | 0.0011569 | 0.00028994
60 | 0.98393 | -0.30671 | 0.0017039 | 0.00042703
61 | 0.98397 | -0.30577 | 0 | 0
62 | 0.97953 | -0.39238 | 0.0038035 | 0.00095323
63 | 0.97756 | -0.43113 | 0.0043358 | 0.0010867
64 | 0.9831 | -0.32263 | 0.0012305 | 0.0003084
65 | 0.98194 | -0.34506 | 0.0030041 | 0.00075289
66 | 0.98171 | -0.34953 | 0.0011488 | 0.00028793
67 | 0.98384 | -0.30831 | 0.0078664 | 0.0019715
68 | 0.98117 | -0.36013 | 0.0011512 | 0.00028852
69 | 0.98375 | -0.31021 | 0.0046351 | 0.0011617
70 | 0.97918 | -0.3988 | 0.0011587 | 0.00029041
71 | 0.98377 | -0.30975 | 0.0016351 | 0.00040979
72 | 0.9791 | -0.40035 | 0.0016288 | 0.00040822
73 | 0.98247 | -0.33508 | 0.0016483 | 0.00041311
74 | 0.97866 | -0.40893 | 0.0011526 | 0.00028887
75 | 0.97728 | -0.43608 | 0.0015881 | 0.00039801
76 | 0.9762 | -0.45722 | 0.0040773 | 0.0010219
77 | 0.97487 | -0.48331 | 0 | 0
78 | 0.97469 | -0.48678 | 0.004342 | 0.0010882
79 | 0.97446 | -0.49138 | 0.0042387 | 0.0010623
80 | 0.99431 | -0.10763 | 0.0042897 | 0.0010751
81 | 0.99439 | -0.10613 | 0.001492 | 0.00037394
82 | 0.99442 | -0.10557 | 0.0014496 | 0.00036331
83 | 0.97627 | -0.45637 | 0 | 0
84 | 0.97636 | -0.45464 | 0 | 0
85 | 0.97587 | -0.46443 | 0.0042302 | 0.0010602
86 | 0.97603 | -0.46119 | 0.001424 | 0.00035689
87 | 0.97676 | -0.44688 | 0.0043367 | 0.0010869
88 | 0.9758 | -0.4658 | 0.0052608 | 0.0013185
89 | 0.97596 | -0.4626 | 0.0013897 | 0.0003483
90 | 0.97714 | -0.43939 | 0.0031524 | 0.00079007
91 | 0.97589 | -0.46397 | 0.0013659 | 0.00034233
92 | 0.9949 | -0.097982 | 0.0020983 | 0.00052589
93 | 0.99485 | -0.099042 | 0.0013134 | 0.00032917
94 | 0.99308 | -0.13314 | 0.0020698 | 0.00051873
95 | 0.99307 | -0.13334 | 0.0022585 | 0.00056604
96 | 0.99303 | -0.13418 | 0.0038977 | 0.00097687
97 | 0.97583 | -0.46509 | 0.001419 | 0.00035562
98 | 0.97365 | -0.50741 | 0.0018911 | 0.00047395
99 | 0.9738 | -0.50449 | 0 | 0
100 | 0.98015 | -0.38035 | 0.0017185 | 0.00043071
101 | 0.98026 | -0.37827 | 0.0016497 | 0.00041346
102 | 0.98004 | -0.38257 | 0 | 0
103 | 0.98142 | -0.35552 | 0.0017096 | 0.00042847
104 | 0.97988 | -0.3856 | 0.0016343 | 0.00040959
105 | 0.98177 | -0.34876 | 0.0016565 | 0.00041517
106 | 0.97986 | -0.38604 | 0.0016532 | 0.00041432
107 | 0.98211 | -0.34199 | 0.0016379 | 0.0004105
108 | 0.97984 | -0.38632 | 0.0013867 | 0.00034754
109 | 0.97984 | -0.38646 | 0.0014276 | 0.00035779
110 | 0.97421 | -0.4964 | 0.0045898 | 0.0011503
111 | 0.9739 | -0.50247 | 0 | 0
112 | 0.97388 | -0.50288 | 0.0074169 | 0.0018588
113 | 0.97342 | -0.51194 | 0 | 0
114 | 0.97252 | -0.52959 | 0 | 0
115 | 0.97223 | -0.53536 | 0 | 0
116 | 0.97282 | -0.5238 | 0.0046027 | 0.0011536
117 | 0.97315 | -0.51722 | 0.005146 | 0.0012897
118 | 0.97306 | -0.51894 | 0.004245 | 0.0010639
119 | 0.97218 | -0.53628 | 0.0057444 | 0.0014397
120 | 0.97218 | -0.53642 | 0.0025906 | 0.00064926
121 | 0.97367 | -0.50698 | 0.00098404 | 0.00024662
122 | 0.97264 | -0.5272 | 0.0068386 | 0.0017139
123 | 0.9721 | -0.53804 | 0.0037194 | 0.00093217
124 | 0.97212 | -0.53748 | 0.0022607 | 0.00056659
125 | 0.97576 | -0.46646 | 0.0014181 | 0.0003554
126 | 0.97572 | -0.4673 | 0.0013926 | 0.00034902
127 | 0.97568 | -0.46799 | 0.0013943 | 0.00034944
128 | 0.97566 | -0.46855 | 0.0013789 | 0.00034558
129 | 0.97563 | -0.46896 | 0.0013865 | 0.00034749
130 | 0.97562 | -0.46924 | 0.0013773 | 0.00034519
131 | 0.98104 | -0.36291 | 0.0024148 | 0.00060521
132 | 0.98091 | -0.36563 | 0.0050391 | 0.0012629
133 | 0.98195 | -0.34518 | 0.0014749 | 0.00036965
134 | 0.98021 | -0.37916 | 0.0022369 | 0.00056062
135 | 0.98245 | -0.33554 | 0.0011575 | 0.0002901
136 | 0.97935 | -0.39601 | 0.0045712 | 0.0011456
137 | 0.98272 | -0.33021 | 0.0011547 | 0.00028939
138 | 0.98293 | -0.32606 | 0.0019068 | 0.00047788
139 | 0.98333 | -0.31831 | 0.0012776 | 0.00032019
140 | 0.98355 | -0.31416 | 0.0015113 | 0.00037877
141 | 0.97365 | -0.50747 | 0 | 0
142 | 0.97361 | -0.50811 | 0.00088378 | 0.0002215
143 | 0.97561 | -0.46938 | 0.0014324 | 0.000359
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.16311 | -0.041452 | 0.16323 | 0.041525 | 0.00011499 | 7.2979e-05 | 0.2431 | 0.2431 | 0.2431 | 0.99923 | -0.014629 | 1 | 0 | 22.2622
1 | 0.1579 | 0.040146 | -0.15788 | -0.040134 | 1.7779e-05 | 1.1278e-05 | 0.23534 | 0.23534 | 0.23534 | 0.99923 | -0.014629 | 0.99911 | -0.016967 | 21.5513
2 | 0.28468 | 0.073444 | -0.28443 | -0.073284 | 0.00025114 | 0.00016029 | 0.42435 | 0.42435 | 0.42435 | 1 | 0 | 0.99904 | -0.018121 | 38.8599
3 | 0.032329 | 0.0081648 | -0.032215 | -0.0080935 | 0.00011412 | 7.1318e-05 | 0.048128 | 0.048128 | 0.048128 | 1 | 0 | 0.99615 | -0.07394 | 13.2221
4 | 0.15516 | 0.039453 | -0.15497 | -0.039332 | 0.00018936 | 0.00012008 | 0.23129 | 0.23129 | 0.23129 | 0.99911 | -0.016967 | 0.99778 | -0.042334 | 21.1804
5 | 0.27947 | 0.072042 | -0.27839 | -0.071354 | 0.0010786 | 0.00068838 | 0.41697 | 0.41697 | 0.41697 | 0.99904 | -0.018121 | 0.99483 | -0.097711 | 38.1845
6 | 0.032215 | 0.0080935 | -0.032187 | -0.0080763 | 2.7497e-05 | 1.7186e-05 | 0.048128 | 0.048128 | 0.048128 | 0.99615 | -0.07394 | 0.99522 | -0.09184 | 13.2221
7 | 0.15331 | 0.038916 | -0.1532 | -0.038849 | 0.00010584 | 6.7103e-05 | 0.22881 | 0.22881 | 0.22881 | 0.99778 | -0.042334 | 0.99702 | -0.056694 | 20.9532
8 | 0.011576 | 0.0029021 | -0.011573 | -0.0029006 | 2.9664e-06 | 1.556e-06 | 0.017315 | 0.017316 | 0.017316 | 0.99483 | -0.097711 | 0.99455 | -0.10309 | 4.757
9 | 0.26682 | 0.068452 | -0.26632 | -0.068131 | 0.00050236 | 0.00032053 | 0.39966 | 0.39966 | 0.39966 | 0.99483 | -0.097711 | 0.99278 | -0.1366 | 36.5989
10 | 0.030377 | 0.0076227 | -0.030375 | -0.0076213 | 2.2058e-06 | 1.3747e-06 | 0.045422 | 0.045422 | 0.045422 | 0.99522 | -0.09184 | 0.99514 | -0.093363 | 12.4787
11 | 0.1532 | 0.038849 | -0.15288 | -0.038641 | 0.00032561 | 0.00020753 | 0.22881 | 0.22881 | 0.22881 | 0.99702 | -0.056694 | 0.99471 | -0.10101 | 31.4299
12 | 0.010129 | 0.0025387 | -0.010129 | -0.0025385 | 4.636e-07 | 2.2686e-07 | 0.015155 | 0.015155 | 0.015155 | 0.99455 | -0.10309 | 0.9945 | -0.10405 | 4.1635
13 | 0.26479 | 0.067749 | -0.26448 | -0.067548 | 0.00031465 | 0.00020076 | 0.39737 | 0.39737 | 0.39737 | 0.99278 | -0.1366 | 0.99149 | -0.16118 | 36.3896
14 | -0.019323 | -0.0048459 | 0.019326 | 0.0048481 | 3.7104e-06 | 2.2211e-06 | 0.028918 | 0.028918 | 0.028918 | 0.99431 | -0.10934 | 0.99452 | -0.10531 | 7.9445
15 | 0.01683 | 0.0042211 | -0.016829 | -0.0042206 | 9.7164e-07 | 5.6888e-07 | 0.025188 | 0.025188 | 0.025188 | 0.99431 | -0.10934 | 0.99425 | -0.11055 | 6.9197
16 | -0.02114 | -0.0053027 | 0.021144 | 0.0053047 | 3.416e-06 | 2.0681e-06 | 0.031632 | 0.031632 | 0.031632 | 0.99452 | -0.10531 | 0.9947 | -0.10192 | 8.6901
17 | 0.015325 | 0.0038436 | -0.015319 | -0.00384 | 6.1633e-06 | 3.5395e-06 | 0.022936 | 0.022936 | 0.022936 | 0.99425 | -0.11055 | 0.99381 | -0.11899 | 6.3012
18 | -0.021786 | -0.0054658 | 0.021786 | 0.0054659 | 2.9835e-07 | 1.8122e-07 | 0.032593 | 0.032593 | 0.032593 | 0.9947 | -0.10192 | 0.99471 | -0.10164 | 8.9541
19 | 0.0070867 | 0.0017761 | -0.0070854 | -0.0017757 | 1.2889e-06 | 4.2944e-07 | 0.010611 | 0.010611 | 0.010611 | 0.99381 | -0.11899 | 0.99362 | -0.12281 | 2.9151
20 | 0.0082318 | 0.0020639 | -0.0082284 | -0.0020625 | 3.4228e-06 | 1.4125e-06 | 0.012326 | 0.012326 | 0.012326 | 0.99381 | -0.11899 | 0.99336 | -0.12772 | 3.3862
21 | 0.038153 | 0.0096146 | -0.038013 | -0.0095271 | 0.00013911 | 8.7557e-05 | 0.057092 | 0.057093 | 0.057093 | 0.99471 | -0.10101 | 0.99075 | -0.17752 | 15.6848
22 | 0.11473 | 0.029026 | -0.11426 | -0.028728 | 0.00046643 | 0.00029797 | 0.17172 | 0.17172 | 0.17172 | 0.99471 | -0.10101 | 0.9903 | -0.18611 | 47.1752
23 | 0.0086888 | 0.0021776 | -0.0086885 | -0.0021774 | 3.4213e-07 | 1.4893e-07 | 0.013001 | 0.013001 | 0.013001 | 0.9945 | -0.10405 | 0.99445 | -0.10488 | 3.5716
24 | 0.25062 | 0.064076 | -0.2499 | -0.063614 | 0.00072285 | 0.00046105 | 0.37658 | 0.37658 | 0.37658 | 0.99149 | -0.16118 | 0.98837 | -0.22098 | 34.4853
25 | 0.0065185 | 0.0016331 | -0.0065175 | -0.0016328 | 9.9073e-07 | 2.7283e-07 | 0.0097468 | 0.009747 | 0.009747 | 0.99514 | -0.093363 | 0.99497 | -0.096555 | 2.6777
26 | 0.023856 | 0.0059882 | -0.023847 | -0.0059824 | 9.408e-06 | 5.7652e-06 | 0.035675 | 0.035676 | 0.035676 | 0.99514 | -0.093363 | 0.99471 | -0.10164 | 9.801
27 | 0.0058693 | 0.0014704 | -0.0058689 | -0.0014703 | 3.8146e-07 | 7.2671e-08 | 0.0087776 | 0.0087776 | 0.0087776 | 0.99497 | -0.096555 | 0.9949 | -0.097919 | 2.4114
28 | 0.0034118 | 0.0008545 | -0.0034118 | -0.00085451 | 1.0091e-08 | -6.9629e-09 | 0.0051026 | 0.0051026 | 0.0051026 | 0.9949 | -0.097919 | 0.9949 | -0.097982 | 1.4018
29 | 0.10188 | 0.025627 | -0.10168 | -0.025497 | 0.0002032 | 0.00012975 | 0.15312 | 0.15312 | 0.15312 | 0.9903 | -0.18611 | 0.98814 | -0.22795 | 42.0668
30 | -0.038112 | -0.0095586 | 0.038129 | 0.0095698 | 1.7741e-05 | 1.1171e-05 | 0.057423 | 0.057423 | 0.057423 | 0.98764 | -0.23771 | 0.98814 | -0.22795 | 15.7755
31 | 0.016448 | 0.0041292 | -0.016441 | -0.004125 | 7.2402e-06 | 4.2317e-06 | 0.024784 | 0.024784 | 0.024784 | 0.98764 | -0.23771 | 0.98716 | -0.24695 | 6.8088
32 | 0.016441 | 0.004125 | -0.016427 | -0.004117 | 1.3634e-05 | 7.9698e-06 | 0.024784 | 0.024784 | 0.024784 | 0.98716 | -0.24695 | 0.98627 | -0.26435 | 6.8089
33 | -0.0086476 | -0.0021673 | 0.008648 | 0.0021675 | 4.1087e-07 | 1.8407e-07 | 0.013179 | 0.013179 | 0.013179 | 0.97636 | -0.45478 | 0.97641 | -0.45379 | 3.6207
34 | -0.013034 | -0.0032667 | 0.013034 | 0.0032668 | 2.0838e-07 | 1.1575e-07 | 0.019863 | 0.019863 | 0.019863 | 0.97641 | -0.45379 | 0.97643 | -0.45345 | 5.4569
35 | -0.0055462 | -0.00139 | 0.0055471 | 0.0013902 | 9.4294e-07 | 1.7233e-07 | 0.0084968 | 0.0084966 | 0.0084968 | 0.97128 | -0.55408 | 0.97146 | -0.55051 | 2.3343
36 | -0.0055471 | -0.0013902 | 0.0055485 | 0.0013904 | 1.3393e-06 | 2.4446e-07 | 0.0084966 | 0.0084964 | 0.0084966 | 0.97146 | -0.55051 | 0.97172 | -0.54544 | 2.3342
37 | -0.014321 | -0.0035894 | 0.014323 | 0.0035906 | 2.0646e-06 | 1.1768e-06 | 0.021825 | 0.021825 | 0.021825 | 0.97643 | -0.45345 | 0.97658 | -0.45043 | 5.9959
38 | -0.0093878 | -0.0023526 | 0.0093895 | 0.0023535 | 1.7462e-06 | 8.3839e-07 | 0.014376 | 0.014376 | 0.014376 | 0.97172 | -0.54544 | 0.97192 | -0.54154 | 3.9493
39 | -0.027725 | -0.0069494 | 0.027728 | 0.0069514 | 3.2321e-06 | 2.0081e-06 | 0.042245 | 0.042245 | 0.042245 | 0.97658 | -0.45043 | 0.9767 | -0.44798 | 11.6058
40 | -0.014318 | -0.0035887 | 0.01432 | 0.00359 | 2.387e-06 | 1.3635e-06 | 0.021921 | 0.021921 | 0.021921 | 0.97192 | -0.54154 | 0.9721 | -0.53804 | 6.0223
41 | 0.0070854 | 0.0017757 | -0.0070843 | -0.0017753 | 1.1188e-06 | 3.729e-07 | 0.010611 | 0.010611 | 0.010611 | 0.99362 | -0.12281 | 0.99344 | -0.12612 | 2.9151
42 | 0.0082284 | 0.0020625 | -0.0082263 | -0.0020616 | 2.1237e-06 | 8.7675e-07 | 0.012326 | 0.012326 | 0.012326 | 0.99336 | -0.12772 | 0.99308 | -0.13314 | 3.3863
43 | 0.0047058 | 0.0011792 | -0.0047057 | -0.0011792 | 7.0036e-08 | -3.8505e-09 | 0.0070484 | 0.0070485 | 0.0070485 | 0.99344 | -0.12612 | 0.99343 | -0.12644 | 1.9364
44 | 0.0036987 | 0.00092684 | -0.0036987 | -0.00092687 | 6.5014e-08 | -3.1523e-08 | 0.0055401 | 0.0055402 | 0.0055402 | 0.99343 | -0.12644 | 0.99341 | -0.12681 | 1.522
45 | -0.0016704 | -0.00041865 | 0.0016704 | 0.0004186 | 1.0073e-08 | -4.9101e-08 | 0.0025022 | 0.0025021 | 0.0025022 | 0.99339 | -0.12717 | 0.9934 | -0.12705 | 0.68741
46 | -0.0026744 | -0.00067022 | 0.0026744 | 0.00067017 | 3.0708e-08 | -4.641e-08 | 0.004006 | 0.004006 | 0.004006 | 0.9934 | -0.12705 | 0.99341 | -0.12681 | 1.1006
47 | -0.029831 | -0.0074785 | 0.029862 | 0.0074973 | 3.0177e-05 | 1.8825e-05 | 0.045449 | 0.045449 | 0.045449 | 0.9767 | -0.44798 | 0.97778 | -0.42677 | 12.486
48 | -0.031485 | -0.007904 | 0.031493 | 0.0079093 | 8.3803e-06 | 5.2413e-06 | 0.047919 | 0.047919 | 0.047919 | 0.97778 | -0.42677 | 0.97807 | -0.42119 | 13.1645
49 | -0.035342 | -0.008874 | 0.035361 | 0.0088859 | 1.8902e-05 | 1.1879e-05 | 0.053775 | 0.053775 | 0.053775 | 0.97807 | -0.42119 | 0.97864 | -0.40999 | 14.7734
50 | -0.037614 | -0.0094504 | 0.037624 | 0.0094572 | 1.0829e-05 | 6.8193e-06 | 0.0572 | 0.0572 | 0.0572 | 0.97864 | -0.40999 | 0.97895 | -0.40396 | 15.7143
51 | -0.03982 | -0.010007 | 0.039835 | 0.010017 | 1.5109e-05 | 9.5312e-06 | 0.060536 | 0.060536 | 0.060536 | 0.97895 | -0.40396 | 0.97935 | -0.39601 | 16.6309
52 | 0.2499 | 0.063614 | -0.24958 | -0.06341 | 0.00032002 | 0.00020412 | 0.37658 | 0.37658 | 0.37658 | 0.98837 | -0.22098 | 0.98699 | -0.24758 | 34.4853
53 | 0.24697 | 0.062758 | -0.24667 | -0.062567 | 0.00030009 | 0.00019139 | 0.37266 | 0.37266 | 0.37266 | 0.98699 | -0.24758 | 0.98568 | -0.27285 | 34.126
54 | 0.066651 | 0.016866 | -0.066591 | -0.016828 | 5.9917e-05 | 3.8146e-05 | 0.10068 | 0.10068 | 0.10068 | 0.98568 | -0.27285 | 0.98471 | -0.2916 | 27.6583
55 | 0.18002 | 0.045701 | -0.17994 | -0.045648 | 8.2803e-05 | 5.2652e-05 | 0.27198 | 0.27198 | 0.27198 | 0.98568 | -0.27285 | 0.98518 | -0.28241 | 24.9065
56 | -0.0059062 | -0.0014802 | 0.0059065 | 0.0014803 | 2.5299e-07 | 5.6921e-08 | 0.008983 | 0.0089829 | 0.008983 | 0.97836 | -0.41544 | 0.9784 | -0.41454 | 2.4678
57 | -0.047567 | -0.011949 | 0.047586 | 0.011961 | 1.8323e-05 | 1.161e-05 | 0.072353 | 0.072353 | 0.072353 | 0.9784 | -0.41454 | 0.97881 | -0.40647 | 19.8773
58 | 0.041661 | 0.010469 | -0.041635 | -0.010452 | 2.6164e-05 | 1.6527e-05 | 0.06337 | 0.06337 | 0.06337 | 0.9784 | -0.41454 | 0.97773 | -0.42771 | 17.4094
59 | 0.06401 | 0.016181 | -0.063952 | -0.016144 | 5.7752e-05 | 3.6752e-05 | 0.096777 | 0.096777 | 0.096777 | 0.98471 | -0.2916 | 0.98374 | -0.31043 | 26.5871
60 | 0.076536 | 0.019372 | -0.076446 | -0.019315 | 8.9133e-05 | 5.6819e-05 | 0.11567 | 0.11567 | 0.11567 | 0.98518 | -0.28241 | 0.98393 | -0.30671 | 31.7768
61 | 0.10341 | 0.026276 | -0.10329 | -0.026203 | 0.00011614 | 7.2878e-05 | 0.15631 | 0.15631 | 0.15631 | 0.98518 | -0.28241 | 0.98397 | -0.30577 | 14.3143
62 | -0.052866 | -0.013284 | 0.052901 | 0.013307 | 3.5581e-05 | 2.2587e-05 | 0.08038 | 0.08038 | 0.08038 | 0.97881 | -0.40647 | 0.97953 | -0.39238 | 22.0824
63 | 0.036746 | 0.0092272 | -0.03674 | -0.0092234 | 6.0075e-06 | 3.7806e-06 | 0.055931 | 0.055931 | 0.055931 | 0.97773 | -0.42771 | 0.97756 | -0.43113 | 15.3657
64 | 0.007232 | 0.0018124 | -0.0072318 | -0.0018123 | 2.3779e-07 | 8.1933e-08 | 0.010821 | 0.010821 | 0.010821 | 0.99445 | -0.10488 | 0.99442 | -0.10557 | 2.9729
65 | 0.062796 | 0.015854 | -0.062784 | -0.015847 | 1.1225e-05 | 7.1417e-06 | 0.095027 | 0.095027 | 0.095027 | 0.98374 | -0.31043 | 0.98355 | -0.31416 | 26.1063
66 | 0.074743 | 0.018888 | -0.074732 | -0.018881 | 1.0896e-05 | 6.9448e-06 | 0.11309 | 0.11309 | 0.11309 | 0.98393 | -0.30671 | 0.98377 | -0.30975 | 31.0689
67 | 0.012503 | 0.003134 | -0.012502 | -0.0031331 | 1.5154e-06 | 8.263e-07 | 0.018908 | 0.018908 | 0.018908 | 0.98397 | -0.30577 | 0.98384 | -0.30831 | 5.1946
68 | 0.090786 | 0.023069 | -0.090712 | -0.023022 | 7.3654e-05 | 4.6611e-05 | 0.1374 | 0.1374 | 0.1374 | 0.98397 | -0.30577 | 0.9831 | -0.32263 | 18.8742
69 | -0.056705 | -0.01426 | 0.056731 | 0.014277 | 2.6593e-05 | 1.6899e-05 | 0.086158 | 0.086158 | 0.086158 | 0.97953 | -0.39238 | 0.98004 | -0.38257 | 23.6697
70 | 0.032405 | 0.0081368 | -0.032392 | -0.0081288 | 1.2761e-05 | 7.992e-06 | 0.049331 | 0.049331 | 0.049331 | 0.97756 | -0.43113 | 0.97714 | -0.43939 | 13.5525
71 | 0.089482 | 0.022714 | -0.089385 | -0.022652 | 9.6442e-05 | 6.1546e-05 | 0.13554 | 0.13554 | 0.13554 | 0.9831 | -0.32263 | 0.98194 | -0.34506 | 37.2368
72 | 0.086381 | 0.021899 | -0.086362 | -0.021888 | 1.8532e-05 | 1.1824e-05 | 0.13099 | 0.13099 | 0.13099 | 0.98194 | -0.34506 | 0.98171 | -0.34953 | 35.9862
73 | 0.085214 | 0.0216 | -0.08517 | -0.021572 | 4.3393e-05 | 2.7684e-05 | 0.12925 | 0.12925 | 0.12925 | 0.98171 | -0.34953 | 0.98117 | -0.36013 | 35.5078
74 | 0.0046355 | 0.0011616 | -0.0046351 | -0.0011617 | 4.1866e-07 | -2.0456e-08 | 0.0070109 | 0.007011 | 0.007011 | 0.98384 | -0.30831 | 0.98375 | -0.31021 | 1.9261
75 | 0.084019 | 0.021283 | -0.083863 | -0.021184 | 0.00015575 | 9.9359e-05 | 0.1275 | 0.1275 | 0.1275 | 0.98117 | -0.36013 | 0.97918 | -0.3988 | 35.0282
76 | 0.082705 | 0.020894 | -0.082698 | -0.02089 | 6.1334e-06 | 3.9123e-06 | 0.12574 | 0.12574 | 0.12574 | 0.97918 | -0.3988 | 0.9791 | -0.40035 | 34.5445
77 | 0.073097 | 0.018472 | -0.073008 | -0.018415 | 8.8671e-05 | 5.6505e-05 | 0.11062 | 0.11062 | 0.11062 | 0.98377 | -0.30975 | 0.98247 | -0.33508 | 30.3895
78 | 0.08107 | 0.020482 | -0.081036 | -0.02046 | 3.3316e-05 | 2.1249e-05 | 0.12327 | 0.12327 | 0.12327 | 0.9791 | -0.40035 | 0.97866 | -0.40893 | 33.8644
79 | 0.07136 | 0.018002 | -0.071336 | -0.017987 | 2.358e-05 | 1.5023e-05 | 0.10812 | 0.10812 | 0.10812 | 0.98247 | -0.33508 | 0.98211 | -0.34199 | 29.7036
80 | 0.079884 | 0.020171 | -0.07978 | -0.020105 | 0.00010378 | 6.6183e-05 | 0.12151 | 0.12151 | 0.12151 | 0.97866 | -0.40893 | 0.97728 | -0.43608 | 33.383
81 | 0.078192 | 0.019707 | -0.078113 | -0.019657 | 7.8997e-05 | 5.0372e-05 | 0.1191 | 0.1191 | 0.1191 | 0.97728 | -0.43608 | 0.9762 | -0.45722 | 32.7187
82 | 0.074035 | 0.018635 | -0.073943 | -0.018576 | 9.2203e-05 | 5.8769e-05 | 0.11288 | 0.11288 | 0.11288 | 0.9762 | -0.45722 | 0.97487 | -0.48331 | 31.0113
83 | 0.053923 | 0.013557 | -0.053914 | -0.013551 | 8.9226e-06 | 5.6667e-06 | 0.082322 | 0.082322 | 0.082322 | 0.97487 | -0.48331 | 0.97469 | -0.48678 | 22.616
84 | 0.02002 | 0.0050196 | -0.020012 | -0.005015 | 7.6941e-06 | 4.6504e-06 | 0.030559 | 0.030559 | 0.030559 | 0.97487 | -0.48331 | 0.97446 | -0.49138 | 8.3953
85 | 0.049572 | 0.012463 | -0.049513 | -0.012425 | 5.9484e-05 | 3.7725e-05 | 0.075694 | 0.075694 | 0.075694 | 0.97469 | -0.48678 | 0.97342 | -0.51194 | 20.795
86 | 0.015774 | 0.0039527 | -0.01577 | -0.0039505 | 3.7707e-06 | 2.1974e-06 | 0.024086 | 0.024086 | 0.024086 | 0.97446 | -0.49138 | 0.97421 | -0.4964 | 6.6171
87 | -0.0042897 | -0.0010751 | 0.00429 | 0.001075 | 3.0755e-07 | -6.1311e-08 | 0.0064196 | 0.0064195 | 0.0064196 | 0.99431 | -0.10763 | 0.99439 | -0.10613 | 1.7636
88 | -0.005782 | -0.001449 | 0.0057822 | 0.001449 | 1.5421e-07 | 2.7432e-08 | 0.0086522 | 0.0086522 | 0.0086522 | 0.99439 | -0.10613 | 0.99442 | -0.10557 | 2.377
89 | -0.009495 | -0.0023805 | 0.0094958 | 0.0023808 | 7.8307e-07 | 3.7649e-07 | 0.014472 | 0.014472 | 0.014472 | 0.97627 | -0.45637 | 0.97636 | -0.45464 | 3.9759
90 | 0.009495 | 0.0023805 | -0.0094913 | -0.0023787 | 3.6442e-06 | 1.7524e-06 | 0.014472 | 0.014473 | 0.014473 | 0.97627 | -0.45637 | 0.97587 | -0.46443 | 3.976
91 | 0.015387 | 0.0038588 | -0.015383 | -0.003856 | 4.8071e-06 | 2.7852e-06 | 0.023452 | 0.023452 | 0.023452 | 0.97636 | -0.45464 | 0.97603 | -0.46119 | 6.4428
92 | -0.024883 | -0.0062396 | 0.024892 | 0.0062453 | 9.205e-06 | 5.6777e-06 | 0.037924 | 0.037924 | 0.037924 | 0.97636 | -0.45464 | 0.97676 | -0.44688 | 10.4187
93 | 0.0052612 | 0.0013185 | -0.0052608 | -0.0013185 | 3.4503e-07 | 4.2219e-08 | 0.0080223 | 0.0080224 | 0.0080224 | 0.97587 | -0.46443 | 0.9758 | -0.4658 | 2.204
94 | 0.013959 | 0.0034991 | -0.013958 | -0.0034986 | 9.3318e-07 | 5.2857e-07 | 0.021281 | 0.021281 | 0.021281 | 0.97603 | -0.46119 | 0.97596 | -0.4626 | 5.8464
95 | -0.029229 | -0.0073322 | 0.029239 | 0.0073387 | 1.0436e-05 | 6.5035e-06 | 0.044531 | 0.044531 | 0.044531 | 0.97676 | -0.44688 | 0.97714 | -0.43939 | 12.2337
96 | 0.012568 | 0.0031503 | -0.012567 | -0.0031498 | 8.216e-07 | 4.5127e-07 | 0.019162 | 0.019162 | 0.019162 | 0.97596 | -0.4626 | 0.97589 | -0.46397 | 5.2643
97 | 0.011201 | 0.0028075 | -0.011201 | -0.0028072 | 5.955e-07 | 3.1311e-07 | 0.017079 | 0.017079 | 0.017079 | 0.97589 | -0.46397 | 0.97583 | -0.46509 | 4.6921
98 | 0.0013135 | 0.00032862 | -0.0013134 | -0.00032917 | 6.6289e-08 | -5.5241e-07 | 0.0019643 | 0.0019645 | 0.0019645 | 0.9949 | -0.097982 | 0.99485 | -0.099042 | 0.5397
99 | 0.0061565 | 0.0015429 | -0.0061564 | -0.0015428 | 6.0163e-08 | 1.4111e-08 | 0.0092247 | 0.0092247 | 0.0092247 | 0.99308 | -0.13314 | 0.99307 | -0.13334 | 2.5343
100 | 0.0038979 | 0.00097681 | -0.0038977 | -0.00097687 | 1.5501e-07 | -5.7565e-08 | 0.0058406 | 0.0058406 | 0.0058406 | 0.99307 | -0.13334 | 0.99303 | -0.13418 | 1.6046
101 | 0.0097816 | 0.0024516 | -0.009781 | -0.0024513 | 6.4121e-07 | 3.1436e-07 | 0.014916 | 0.014916 | 0.014916 | 0.97583 | -0.46509 | 0.97576 | -0.46646 | 4.0977
102 | -0.0018911 | -0.00047395 | 0.0018913 | 0.00047307 | 2.6241e-07 | -8.7429e-07 | 0.0028901 | 0.0028897 | 0.0028901 | 0.97365 | -0.50741 | 0.9738 | -0.50449 | 0.79399
103 | 0.0018681 | 0.00046653 | -0.0018679 | -0.00046729 | 2.2125e-07 | -7.5935e-07 | 0.002854 | 0.0028543 | 0.0028543 | 0.9738 | -0.50449 | 0.97367 | -0.50698 | 0.78414
104 | -0.0037594 | -0.00093961 | 0.0037597 | 0.0009395 | 2.8808e-07 | -1.0536e-07 | 0.0057437 | 0.0057436 | 0.0057437 | 0.9738 | -0.50449 | 0.97388 | -0.50288 | 1.5779
105 | -0.064559 | -0.016241 | 0.064566 | 0.016245 | 6.3989e-06 | 4.0729e-06 | 0.098033 | 0.098033 | 0.098033 | 0.98015 | -0.38035 | 0.98026 | -0.37827 | 26.932
106 | 0.062841 | 0.01581 | -0.062834 | -0.015806 | 6.6726e-06 | 4.2458e-06 | 0.095424 | 0.095424 | 0.095424 | 0.98015 | -0.38035 | 0.98004 | -0.38257 | 26.2153
107 | -0.066215 | -0.016659 | 0.066287 | 0.016704 | 7.2063e-05 | 4.588e-05 | 0.10054 | 0.10054 | 0.10054 | 0.98026 | -0.37827 | 0.98142 | -0.35552 | 27.62
108 | 0.0061028 | 0.0015293 | -0.0061019 | -0.0015291 | 8.8252e-07 | 2.1948e-07 | 0.0092659 | 0.0092661 | 0.0092661 | 0.98004 | -0.38257 | 0.97988 | -0.3856 | 2.5456
109 | -0.067997 | -0.017133 | 0.068019 | 0.017147 | 2.2008e-05 | 1.4015e-05 | 0.10313 | 0.10313 | 0.10313 | 0.98142 | -0.35552 | 0.98177 | -0.34876 | 28.3321
110 | 0.0044676 | 0.0011195 | -0.0044675 | -0.0011195 | 9.261e-08 | -8.3168e-09 | 0.0067843 | 0.0067843 | 0.0067843 | 0.97988 | -0.3856 | 0.97986 | -0.38604 | 1.8638
111 | -0.069676 | -0.017562 | 0.069698 | 0.017576 | 2.2575e-05 | 1.438e-05 | 0.10564 | 0.10564 | 0.10564 | 0.98177 | -0.34876 | 0.98211 | -0.34199 | 29.0219
112 | 0.0028143 | 0.00070522 | -0.0028143 | -0.00070526 | 3.6994e-08 | -4.4354e-08 | 0.0042738 | 0.0042738 | 0.0042738 | 0.97986 | -0.38604 | 0.97984 | -0.38632 | 1.1741
113 | 0.0014276 | 0.00035772 | -0.0014276 | -0.00035779 | 9.6917e-09 | -6.3058e-08 | 0.002168 | 0.002168 | 0.002168 | 0.97984 | -0.38632 | 0.97984 | -0.38646 | 0.5956
114 | 0.01118 | 0.0028002 | -0.011177 | -0.0027985 | 3.2321e-06 | 1.7006e-06 | 0.017076 | 0.017076 | 0.017076 | 0.97421 | -0.4964 | 0.9739 | -0.50247 | 4.6912
115 | 0.011177 | 0.0027985 | -0.011177 | -0.0027983 | 2.1868e-07 | 1.1507e-07 | 0.017076 | 0.017076 | 0.017076 | 0.9739 | -0.50247 | 0.97388 | -0.50288 | 4.6912
116 | 0.030053 | 0.0075434 | -0.030045 | -0.0075387 | 7.5737e-06 | 4.7282e-06 | 0.045945 | 0.045945 | 0.045945 | 0.97342 | -0.51194 | 0.97315 | -0.51722 | 12.6222
117 | 0.01946 | 0.0048816 | -0.019453 | -0.0048777 | 6.4981e-06 | 3.9155e-06 | 0.029749 | 0.029749 | 0.029749 | 0.97342 | -0.51194 | 0.97306 | -0.51894 | 8.1728
118 | 0.010599 | 0.0026567 | -0.010596 | -0.0026552 | 2.9117e-06 | 1.4973e-06 | 0.016217 | 0.016218 | 0.016218 | 0.97252 | -0.52959 | 0.97223 | -0.53536 | 4.4554
119 | -0.010599 | -0.0026567 | 0.010602 | 0.0026582 | 2.9258e-06 | 1.5043e-06 | 0.016217 | 0.016217 | 0.016217 | 0.97252 | -0.52959 | 0.97282 | -0.5238 | 4.4554
120 | 0.0080056 | 0.0020061 | -0.0080052 | -0.002006 | 3.5247e-07 | 1.4795e-07 | 0.012253 | 0.012253 | 0.012253 | 0.97223 | -0.53536 | 0.97218 | -0.53628 | 3.3661
121 | 0.0025907 | 0.00064907 | -0.0025906 | -0.00064926 | 1.308e-07 | -1.9139e-07 | 0.0039651 | 0.0039652 | 0.0039652 | 0.97223 | -0.53536 | 0.97218 | -0.53642 | 1.0893
122 | -0.015205 | -0.0038118 | 0.015208 | 0.0038138 | 3.5194e-06 | 2.0369e-06 | 0.023258 | 0.023258 | 0.023258 | 0.97282 | -0.5238 | 0.97306 | -0.51894 | 6.3895
123 | 0.024899 | 0.006249 | -0.024888 | -0.0062417 | 1.1846e-05 | 7.3108e-06 | 0.038076 | 0.038076 | 0.038076 | 0.97315 | -0.51722 | 0.97264 | -0.5272 | 10.4605
124 | 0.0022608 | 0.00056632 | -0.0022607 | -0.00056659 | 1.2827e-07 | -2.7208e-07 | 0.0034603 | 0.0034604 | 0.0034604 | 0.97218 | -0.53628 | 0.97212 | -0.53748 | 0.95067
125 | 0.00088383 | 0.00022067 | -0.00088381 | -0.00022103 | 2.0317e-08 | -3.5646e-07 | 0.0013504 | 0.0013505 | 0.0013505 | 0.97367 | -0.50698 | 0.97365 | -0.50747 | 0.37103
126 | 0.018049 | 0.0045278 | -0.01804 | -0.0045222 | 9.3169e-06 | 5.5587e-06 | 0.027614 | 0.027614 | 0.027614 | 0.97264 | -0.5272 | 0.9721 | -0.53804 | 7.5864
127 | 0.0083629 | 0.0020959 | -0.0083626 | -0.0020957 | 3.3447e-07 | 1.4557e-07 | 0.012753 | 0.012753 | 0.012753 | 0.97576 | -0.46646 | 0.97572 | -0.4673 | 3.5036
128 | 0.0069699 | 0.0017467 | -0.0069697 | -0.0017466 | 2.3004e-07 | 7.9414e-08 | 0.010629 | 0.010629 | 0.010629 | 0.97572 | -0.4673 | 0.97568 | -0.46799 | 2.9202
129 | 0.0055754 | 0.0013972 | -0.0055753 | -0.0013971 | 1.4649e-07 | 2.6278e-08 | 0.008503 | 0.008503 | 0.008503 | 0.97568 | -0.46799 | 0.97566 | -0.46855 | 2.336
130 | 0.0041964 | 0.0010516 | -0.0041963 | -0.0010516 | 8.2845e-08 | -1.4333e-08 | 0.0064 | 0.0064 | 0.0064 | 0.97566 | -0.46855 | 0.97563 | -0.46896 | 1.7583
131 | 0.0028098 | 0.00070408 | -0.0028097 | -0.00070413 | 3.715e-08 | -4.3588e-08 | 0.0042854 | 0.0042854 | 0.0042854 | 0.97563 | -0.46896 | 0.97562 | -0.46924 | 1.1773
132 | 0.0014324 | 0.00035893 | -0.0014324 | -0.000359 | 9.8112e-09 | -6.217e-08 | 0.0021847 | 0.0021847 | 0.0021847 | 0.97562 | -0.46924 | 0.97561 | -0.46938 | 0.6002
133 | 0.051755 | 0.013032 | -0.051748 | -0.013028 | 6.7227e-06 | 4.2658e-06 | 0.078522 | 0.078522 | 0.078522 | 0.98104 | -0.36291 | 0.98091 | -0.36563 | 21.5719
134 | -0.054169 | -0.013637 | 0.054215 | 0.013667 | 4.5957e-05 | 2.9183e-05 | 0.082184 | 0.082184 | 0.082184 | 0.98104 | -0.36291 | 0.98195 | -0.34518 | 22.5781
135 | 0.046709 | 0.011765 | -0.046678 | -0.011746 | 3.021e-05 | 1.9132e-05 | 0.070877 | 0.070877 | 0.070877 | 0.98091 | -0.36563 | 0.98021 | -0.37916 | 19.4718
136 | -0.05569 | -0.014036 | 0.055716 | 0.014052 | 2.5699e-05 | 1.6325e-05 | 0.084419 | 0.084419 | 0.084419 | 0.98195 | -0.34518 | 0.98245 | -0.33554 | 23.1921
137 | 0.044442 | 0.011185 | -0.044406 | -0.011163 | 3.5763e-05 | 2.2625e-05 | 0.067482 | 0.067482 | 0.067482 | 0.98021 | -0.37916 | 0.97935 | -0.39601 | 18.5389
138 | -0.056873 | -0.014343 | 0.056888 | 0.014352 | 1.4509e-05 | 9.22e-06 | 0.086172 | 0.086172 | 0.086172 | 0.98245 | -0.33554 | 0.98272 | -0.33021 | 23.6737
139 | -0.058043 | -0.014641 | 0.058054 | 0.014649 | 1.1536e-05 | 7.3325e-06 | 0.087921 | 0.087921 | 0.087921 | 0.98272 | -0.33021 | 0.98293 | -0.32606 | 24.1541
140 | -0.059961 | -0.015126 | 0.059983 | 0.015141 | 2.2272e-05 | 1.4163e-05 | 0.090807 | 0.090807 | 0.090807 | 0.98293 | -0.32606 | 0.98333 | -0.31831 | 24.9471
141 | -0.061261 | -0.015461 | 0.061273 | 0.015468 | 1.2158e-05 | 7.7334e-06 | 0.092741 | 0.09274 | 0.092741 | 0.98333 | -0.31831 | 0.98355 | -0.31416 | 25.4782
142 | 0.00088381 | 0.00022103 | -0.00088378 | -0.0002215 | 2.6852e-08 | -4.7098e-07 | 0.0013505 | 0.0013507 | 0.0013507 | 0.97365 | -0.50747 | 0.97361 | -0.50811 | 0.37108

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48399 | 0.12366

## res_load
| p_mw | q_mvar
0 | 0.0052132 | 0.0013065
1 | 0.0021025 | 0.00052694
2 | 0.0027203 | 0.00068176
3 | 0.0049528 | 0.0012413
4 | 0.0016632 | 0.00041684
5 | 0.0018099 | 0.00045361
6 | 0.0014439 | 0.00036188
7 | 0.001525 | 0.0003822
8 | 0.0024928 | 0.00062474
9 | 0.0018137 | 0.00045456
10 | 0.0015043 | 0.00037702
11 | 0.00064248 | 0.00016102
12 | 0.00144 | 0.00036089
13 | 0.013856 | 0.0034727
14 | 0.0006482 | 0.00016245
15 | 0.0020607 | 0.00051646
16 | 0.0024571 | 0.00061582
17 | 0.038013 | 0.0095271
18 | 0.012375 | 0.0031015
19 | 0.021663 | 0.0054294
20 | 0.063551 | 0.015927
21 | 0.016427 | 0.004117
22 | 0.0086476 | 0.0021673
23 | 0.0043859 | 0.0010992
24 | 0.0055462 | 0.00139
25 | 0.0012873 | 0.00032262
26 | 0.0038393 | 0.00096222
27 | 0.013402 | 0.0033588
28 | 0.0049285 | 0.0012352
29 | 0.0023785 | 0.00059612
30 | 0.001007 | 0.00025237
31 | 0.0016704 | 0.00041865
32 | 0.001004 | 0.00025162
33 | 0.0010242 | 0.0002567
34 | 0.0021032 | 0.00052711
35 | 0.0016229 | 0.00040673
36 | 0.0038495 | 0.00096477
37 | 0.0022524 | 0.0005645
38 | 0.002195 | 0.00055013
39 | 0.0026031 | 0.0006524
40 | 0.0059062 | 0.0014802
41 | 0.0025805 | 0.00064674
42 | 0.00528 | 0.0013233
43 | 0.0048882 | 0.0012251
44 | 0.0014565 | 0.00036502
45 | 0.0011569 | 0.00028994
46 | 0.0017039 | 0.00042703
47 | 0.0038035 | 0.00095323
48 | 0.0043358 | 0.0010867
49 | 0.0012305 | 0.0003084
50 | 0.0030041 | 0.00075289
51 | 0.0011488 | 0.00028793
52 | 0.0078664 | 0.0019715
53 | 0.0011512 | 0.00028852
54 | 0.0046351 | 0.0011617
55 | 0.0011587 | 0.00029041
56 | 0.0016351 | 0.00040979
57 | 0.0016288 | 0.00040822
58 | 0.0016483 | 0.00041311
59 | 0.0011526 | 0.00028887
60 | 0.0015881 | 0.00039801
61 | 0.0040773 | 0.0010219
62 | 0.004342 | 0.0010882
63 | 0.0042387 | 0.0010623
64 | 0.0042897 | 0.0010751
65 | 0.001492 | 0.00037394
66 | 0.0014496 | 0.00036331
67 | 0.0042302 | 0.0010602
68 | 0.001424 | 0.00035689
69 | 0.0043367 | 0.0010869
70 | 0.0052608 | 0.0013185
71 | 0.0013897 | 0.0003483
72 | 0.0031524 | 0.00079007
73 | 0.0013659 | 0.00034233
74 | 0.0020983 | 0.00052589
75 | 0.0013134 | 0.00032917
76 | 0.0020698 | 0.00051873
77 | 0.0022585 | 0.00056604
78 | 0.0038977 | 0.00097687
79 | 0.001419 | 0.00035562
80 | 0.0018911 | 0.00047395
81 | 0.0017185 | 0.00043071
82 | 0.0016497 | 0.00041346
83 | 0.0017096 | 0.00042847
84 | 0.0016343 | 0.00040959
85 | 0.0016565 | 0.00041517
86 | 0.0016532 | 0.00041432
87 | 0.0016379 | 0.0004105
88 | 0.0013867 | 0.00034754
89 | 0.0014276 | 0.00035779
90 | 0.0045898 | 0.0011503
91 | 0.0074169 | 0.0018588
92 | 0.0046027 | 0.0011536
93 | 0.005146 | 0.0012897
94 | 0.004245 | 0.0010639
95 | 0.0057444 | 0.0014397
96 | 0.0025906 | 0.00064926
97 | 0.00098404 | 0.00024662
98 | 0.0068386 | 0.0017139
99 | 0.0037194 | 0.00093217
100 | 0.0022607 | 0.00056659
101 | 0.0014181 | 0.0003554
102 | 0.0013926 | 0.00034902
103 | 0.0013943 | 0.00034944
104 | 0.0013789 | 0.00034558
105 | 0.0013865 | 0.00034749
106 | 0.0013773 | 0.00034519
107 | 0.0024148 | 0.00060521
108 | 0.0050391 | 0.0012629
109 | 0.0014749 | 0.00036965
110 | 0.0022369 | 0.00056062
111 | 0.0011575 | 0.0002901
112 | 0.0045712 | 0.0011456
113 | 0.0011547 | 0.00028939
114 | 0.0019068 | 0.00047788
115 | 0.0012776 | 0.00032019
116 | 0.0015113 | 0.00037877
117 | 0.00088378 | 0.0002215
118 | 0.0014324 | 0.000359

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1