## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_200-7_1_4_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_200-7_1_4_node_5 | 0.4 | n |  | TRUE
2 | bus_LV_200-7_1_4_node_18 | 0.4 | n |  | TRUE
3 | bus_LV_200-7_1_4_node_26 | 0.4 | n |  | TRUE
4 | bus_LV_200-7_1_4_node_79 | 0.4 | n |  | TRUE
5 | bus_LV_200-7_1_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_200-7_1_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_200-7_1_4_node_57 | 0.4 | n |  | TRUE
8 | bus_LV_200-7_1_4_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_200-7_1_4_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_200-7_1_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_200-7_1_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_200-7_1_4_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_200-7_1_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_200-7_1_4_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_200-7_1_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_200-7_1_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_200-7_1_4_node_80 | 0.4 | n |  | TRUE
18 | bus_LV_200-7_1_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_200-7_1_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_200-7_1_4_node_74 | 0.4 | n |  | TRUE
21 | bus_LV_200-7_1_4_node_75 | 0.4 | n |  | TRUE
22 | bus_LV_200-7_1_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_200-7_1_4_node_78 | 0.4 | n |  | TRUE
24 | bus_LV_200-7_1_4_node_76 | 0.4 | n |  | TRUE
25 | bus_LV_200-7_1_4_node_77 | 0.4 | n |  | TRUE
26 | bus_LV_200-7_1_4_node_81 | 0.4 | n |  | TRUE
27 | bus_MV_504_0_node_116 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_200-7_1_4_load_26 | 3 | 0.011264 | 0.002823 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_200-7_1_4_load_79 | 4 | 0.025231 | 0.0063235 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_200-7_1_4_load_57 | 7 | 0.0088822 | 0.0022261 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_200-7_1_4_load_51 | 9 | 0.0021407 | 0.00053651 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_200-7_1_4_load_11 | 10 | 0.0020775 | 0.00052068 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_200-7_1_4_load_12 | 11 | 0.0045282 | 0.0011349 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_200-7_1_4_load_13 | 12 | 0.0045385 | 0.0011375 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_200-7_1_4_load_16 | 13 | 0.052203 | 0.013083 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_200-7_1_4_load_80 | 17 | 0.010738 | 0.0026912 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_200-7_1_4_load_75 | 21 | 0.018743 | 0.0046976 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_200-7_1_4_load_24 | 22 | 0.012626 | 0.0031644 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_200-7_1_4_load_78 | 23 | 0.034276 | 0.0085903 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_200-7_1_4_load_76 | 24 | 0.018767 | 0.0047034 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_200-7_1_4_load_81 | 26 | 0.018722 | 0.0046922 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_200-7_1_4_line_0 |  | 0 | 1 | 0.066707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_200-7_1_4_line_1 |  | 0 | 2 | 0.062416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_200-7_1_4_line_2 |  | 0 | 3 | 0.032955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_200-7_1_4_line_3 |  | 1 | 4 | 0.014184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_200-7_1_4_line_4 |  | 2 | 13 | 0.01585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_200-7_1_4_line_5 |  | 5 | 6 | 0.09405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_200-7_1_4_line_6 |  | 5 | 7 | 0.078499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_200-7_1_4_line_7 |  | 6 | 8 | 0.036391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_200-7_1_4_line_8 |  | 6 | 9 | 0.01308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_200-7_1_4_line_9 |  | 7 | 12 | 0.014787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_200-7_1_4_line_10 |  | 8 | 23 | 0.010327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_200-7_1_4_line_11 |  | 9 | 18 | 0.012141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_200-7_1_4_line_12 |  | 10 | 11 | 0.062003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_200-7_1_4_line_13 |  | 11 | 12 | 0.014797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_200-7_1_4_line_14 |  | 13 | 14 | 0.018529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_200-7_1_4_line_15 |  | 14 | 15 | 0.004358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_200-7_1_4_line_16 |  | 14 | 16 | 0.046467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_200-7_1_4_line_17 |  | 15 | 17 | 0.070162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_200-7_1_4_line_18 |  | 15 | 18 | 0.047088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_200-7_1_4_line_19 |  | 16 | 20 | 0.014408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_200-7_1_4_line_20 |  | 16 | 21 | 0.003096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_200-7_1_4_line_21 |  | 18 | 19 | 0.039494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_200-7_1_4_line_22 |  | 19 | 22 | 0.0059343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_200-7_1_4_line_23 |  | 20 | 24 | 0.00289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_200-7_1_4_line_24 |  | 20 | 25 | 0.014961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_200-7_1_4_line_25 |  | 25 | 26 | 0.002883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_200-7_1_4_trafo_19 | 0.63 MVA 20/0.4 kV | 27 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2689562.6081 | 1252546.5952 | 2689559.5914 | 1252567.8993 | 2689564.8408 | 1252568.6347 | 2689580.7125 | 1252589.1015 | 2689580.9199 | 1252589.3604 | 2689582.8151 | 1252575.8342
1 | 2689562.3657 | 1252491.7718 | 2689562.2006 | 1252492.7033 | 2689561.9457 | 1252493.589 | 2689561.2937 | 1252498.772 | 2689560.5329 | 1252506.6555 | 2689568.4805 | 1252507.643 | 2689566.4609 | 1252519.4104 | 2689562.6081 | 1252546.5952
2 | 2689562.6081 | 1252546.5952 | 2689554.1886 | 1252545.3781 | 2689554.4823 | 1252543.4255 | 2689532.2018 | 1252540.4866
3 | 2689596.9759 | 1252577.1938 | 2689582.8151 | 1252575.8342
4 | 2689562.3657 | 1252491.7718 | 2689564.6181 | 1252476.0827
5 | 2689647.94 | 1252508.0784 | 2689667.1462 | 1252526.6387 | 2689674.2396 | 1252534.6856 | 2689679.5158 | 1252550.5887 | 2689683.9106 | 1252582.8244 | 2689691.105 | 1252584.201
6 | 2689691.105 | 1252584.201 | 2689692.5399 | 1252579.6526 | 2689691.0725 | 1252575.3827 | 2689684.3782 | 1252560.4254 | 2689676.5738 | 1252530.0618 | 2689685.4727 | 1252521.5567 | 2689686.8143 | 1252512.4881
7 | 2689647.94 | 1252508.0784 | 2689646.0285 | 1252510.2066 | 2689645.4583 | 1252517.4591 | 2689624.3091 | 1252533.0178
8 | 2689647.94 | 1252508.0784 | 2689638.5378 | 1252498.9847
9 | 2689688.9785 | 1252497.8602 | 2689686.8143 | 1252512.4881
10 | 2689630.5946 | 1252541.0857 | 2689628.5281 | 1252539.4977 | 2689626.6165 | 1252536.6443 | 2689624.3091 | 1252533.0178
11 | 2689627.9016 | 1252493.1304 | 2689638.5378 | 1252498.9847
12 | 2689674.3367 | 1252435.7553 | 2689665.9542 | 1252443.3791 | 2689673.8842 | 1252454.9969 | 2689692.7458 | 1252472.3957 | 2689691.144 | 1252483.2226
13 | 2689691.144 | 1252483.2226 | 2689688.9785 | 1252497.8602
14 | 2689582.9475 | 1252478.7952 | 2689564.6181 | 1252476.0827
15 | 2689582.9475 | 1252478.7952 | 2689587.2783 | 1252479.3833
16 | 2689582.9475 | 1252478.7952 | 2689587.2382 | 1252448.1143 | 2689588.2017 | 1252442.3022 | 2689584.45 | 1252437.8532 | 2689584.982 | 1252434.114
17 | 2689587.2783 | 1252479.3833 | 2689594.6236 | 1252428.3998 | 2689611.1455 | 1252430.3623 | 2689611.4179 | 1252428.3204
18 | 2689587.2783 | 1252479.3833 | 2689606.8542 | 1252482.0147 | 2689617.4489 | 1252483.6317 | 2689624.2637 | 1252484.6578 | 2689628.2011 | 1252490.2995 | 2689627.9016 | 1252493.1304
19 | 2689584.982 | 1252434.114 | 2689586.8737 | 1252419.8316
20 | 2689584.982 | 1252434.114 | 2689581.9178 | 1252433.6117
21 | 2689620.5919 | 1252460.973 | 2689617.4489 | 1252483.6317 | 2689624.2637 | 1252484.6578 | 2689628.2011 | 1252490.2995 | 2689627.9016 | 1252493.1304
22 | 2689620.5919 | 1252460.973 | 2689621.0325 | 1252457.2991 | 2689621.3753 | 1252455.0915
23 | 2689586.8737 | 1252419.8316 | 2689584.0209 | 1252419.3214
24 | 2689586.8737 | 1252419.8316 | 2689589.0524 | 1252405.031
25 | 2689589.0524 | 1252405.031 | 2689586.1906 | 1252404.6207

## bus_geodata
| x | y | coords
0 | 2689562.6081 | 1252546.5952
1 | 2689582.8151 | 1252575.8342
2 | 2689562.3657 | 1252491.7718
3 | 2689532.2018 | 1252540.4866
4 | 2689596.9759 | 1252577.1938
5 | 2689691.105 | 1252584.201
6 | 2689647.94 | 1252508.0784
7 | 2689686.8143 | 1252512.4881
8 | 2689624.3091 | 1252533.0178
9 | 2689638.5378 | 1252498.9847
10 | 2689674.3367 | 1252435.7553
11 | 2689691.144 | 1252483.2226
12 | 2689688.9785 | 1252497.8602
13 | 2689564.6181 | 1252476.0827
14 | 2689582.9475 | 1252478.7952
15 | 2689587.2783 | 1252479.3833
16 | 2689584.982 | 1252434.114
17 | 2689611.4179 | 1252428.3204
18 | 2689627.9016 | 1252493.1304
19 | 2689620.5919 | 1252460.973
20 | 2689586.8737 | 1252419.8316
21 | 2689581.9178 | 1252433.6117
22 | 2689621.3753 | 1252455.0915
23 | 2689630.5946 | 1252541.0857
24 | 2689584.0209 | 1252419.3214
25 | 2689589.0524 | 1252405.031
26 | 2689586.1906 | 1252404.6207
27 | 2689582.9475 | 1252478.7952

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99561 | -0.084312 | 0 | 0
1 | 0.99408 | -0.11395 | 0 | 0
2 | 0.99769 | -0.044338 | 0 | 0
3 | 0.99527 | -0.090841 | 0.011264 | 0.002823
4 | 0.99375 | -0.12027 | 0.025231 | 0.0063235
5 | 0.99404 | -0.11455 | 0 | 0
6 | 0.99576 | -0.08137 | 0 | 0
7 | 0.9926 | -0.14232 | 0.0088822 | 0.0022261
8 | 0.99462 | -0.10332 | 0 | 0
9 | 0.99641 | -0.06889 | 0.0021407 | 0.00053651
10 | 0.99225 | -0.14925 | 0.0020775 | 0.00052068
11 | 0.99236 | -0.14697 | 0.0045282 | 0.0011349
12 | 0.99245 | -0.14524 | 0.0045385 | 0.0011375
13 | 0.99822 | -0.034213 | 0.052203 | 0.013083
14 | 0.99971 | -0.0055062 | 0 | 0
15 | 1 | 0 | -0.2272 | -0.056835
16 | 0.99734 | -0.051185 | 0 | 0
17 | 0.99932 | -0.013142 | 0.010738 | 0.0026912
18 | 0.99703 | -0.056865 | 0 | 0
19 | 0.99658 | -0.065613 | 0 | 0
20 | 0.99684 | -0.060655 | 0 | 0
21 | 0.99728 | -0.052202 | 0.018743 | 0.0046976
22 | 0.99651 | -0.066928 | 0.012626 | 0.0031644
23 | 0.9943 | -0.10956 | 0.034276 | 0.0085903
24 | 0.9968 | -0.061606 | 0.018767 | 0.0047034
25 | 0.99659 | -0.065569 | 0 | 0
26 | 0.99654 | -0.066517 | 0.018722 | 0.0046922
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.025274 | 0.0063501 | -0.025239 | -0.0063281 | 3.5705e-05 | 2.1985e-05 | 0.03778 | 0.03778 | 0.03778 | 0.99561 | -0.084312 | 0.99408 | -0.11395 | 10.3792
1 | -0.036541 | -0.0091749 | 0.036611 | 0.0092188 | 6.9828e-05 | 4.3876e-05 | 0.05462 | 0.05462 | 0.05462 | 0.99561 | -0.084312 | 0.99769 | -0.044338 | 15.0055
2 | 0.011267 | 0.0028248 | -0.011264 | -0.002823 | 3.5047e-06 | 1.8146e-06 | 0.01684 | 0.01684 | 0.01684 | 0.99561 | -0.084312 | 0.99527 | -0.090841 | 4.6264
3 | 0.025239 | 0.0063281 | -0.025231 | -0.0063235 | 7.592e-06 | 4.6751e-06 | 0.03778 | 0.03778 | 0.03778 | 0.99408 | -0.11395 | 0.99375 | -0.12027 | 10.3792
4 | -0.036611 | -0.0092188 | 0.036629 | 0.0092299 | 1.7732e-05 | 1.1141e-05 | 0.05462 | 0.05462 | 0.05462 | 0.99769 | -0.044338 | 0.99822 | -0.034213 | 15.0054
5 | -0.020055 | -0.0050354 | 0.020087 | 0.0050545 | 3.1794e-05 | 1.9127e-05 | 0.030025 | 0.030024 | 0.030025 | 0.99404 | -0.11455 | 0.99576 | -0.08137 | 8.2485
6 | 0.020055 | 0.0050354 | -0.020029 | -0.0050194 | 2.6537e-05 | 1.5968e-05 | 0.030025 | 0.030025 | 0.030025 | 0.99404 | -0.11455 | 0.9926 | -0.14232 | 8.2486
7 | 0.034322 | 0.0086192 | -0.034286 | -0.0085967 | 3.5907e-05 | 2.2508e-05 | 0.051295 | 0.051295 | 0.051295 | 0.99576 | -0.08137 | 0.99462 | -0.10332 | 14.0921
8 | -0.054409 | -0.013674 | 0.054441 | 0.013694 | 3.2437e-05 | 2.0589e-05 | 0.081319 | 0.081319 | 0.081319 | 0.99576 | -0.08137 | 0.99641 | -0.06889 | 22.3405
9 | 0.011147 | 0.0027933 | -0.011145 | -0.0027925 | 1.5483e-06 | 7.9981e-07 | 0.01671 | 0.01671 | 0.01671 | 0.9926 | -0.14232 | 0.99245 | -0.14524 | 4.5906
10 | 0.034286 | 0.0085967 | -0.034276 | -0.0085903 | 1.019e-05 | 6.3874e-06 | 0.051295 | 0.051295 | 0.051295 | 0.99462 | -0.10332 | 0.9943 | -0.10956 | 14.0921
11 | -0.056582 | -0.014231 | 0.056615 | 0.014251 | 3.2521e-05 | 2.0655e-05 | 0.084516 | 0.084516 | 0.084516 | 0.99641 | -0.06889 | 0.99703 | -0.056865 | 23.2187
12 | -0.0020775 | -0.00052068 | 0.0020778 | 0.00052002 | 2.2567e-07 | -6.5653e-07 | 0.0031155 | 0.0031153 | 0.0031155 | 0.99225 | -0.14925 | 0.99236 | -0.14697 | 0.85592
13 | -0.0066059 | -0.0016549 | 0.0066065 | 0.001655 | 5.4441e-07 | 1.5723e-07 | 0.0099051 | 0.0099051 | 0.0099051 | 0.99236 | -0.14697 | 0.99245 | -0.14524 | 2.7212
14 | -0.088832 | -0.022313 | 0.088954 | 0.022391 | 0.00012187 | 7.7756e-05 | 0.13244 | 0.13244 | 0.13244 | 0.99822 | -0.034213 | 0.99971 | -0.0055062 | 36.384
15 | -0.14533 | -0.036577 | 0.14537 | 0.036601 | 3.8256e-05 | 2.437e-05 | 0.21637 | 0.21637 | 0.21637 | 0.99971 | -0.0055062 | 1 | 0 | 29.7218
16 | 0.056379 | 0.014186 | -0.056257 | -0.014108 | 0.00012277 | 7.7965e-05 | 0.083937 | 0.083937 | 0.083937 | 0.99971 | -0.0055062 | 0.99734 | -0.051185 | 23.0597
17 | 0.010745 | 0.0026946 | -0.010738 | -0.0026912 | 6.7264e-06 | 3.385e-06 | 0.015989 | 0.015989 | 0.015989 | 1 | 0 | 0.99932 | -0.013142 | 4.3926
18 | 0.069435 | 0.017539 | -0.069247 | -0.017419 | 0.00018868 | 0.00012014 | 0.10337 | 0.10337 | 0.10337 | 1 | 0 | 0.99703 | -0.056865 | 28.3982
19 | 0.037512 | 0.0094099 | -0.037495 | -0.0093993 | 1.6926e-05 | 1.0645e-05 | 0.055971 | 0.055971 | 0.055971 | 0.99734 | -0.051185 | 0.99684 | -0.060655 | 15.3766
20 | 0.018744 | 0.0046981 | -0.018743 | -0.0046976 | 9.0805e-07 | 5.4075e-07 | 0.027967 | 0.027967 | 0.027967 | 0.99734 | -0.051185 | 0.99728 | -0.052202 | 7.6831
21 | 0.012632 | 0.0031676 | -0.012627 | -0.0031648 | 5.2642e-06 | 2.8543e-06 | 0.018853 | 0.018853 | 0.018853 | 0.99703 | -0.056865 | 0.99658 | -0.065613 | 5.1795
22 | 0.012627 | 0.0031648 | -0.012626 | -0.0031643 | 7.91e-07 | 4.2892e-07 | 0.018853 | 0.018853 | 0.018853 | 0.99658 | -0.065613 | 0.99651 | -0.066928 | 5.1795
23 | 0.018768 | 0.004704 | -0.018767 | -0.0047034 | 8.5059e-07 | 5.067e-07 | 0.028015 | 0.028015 | 0.028015 | 0.99684 | -0.060655 | 0.9968 | -0.061606 | 7.6965
24 | 0.018727 | 0.0046953 | -0.018723 | -0.0046927 | 4.3846e-06 | 2.6111e-06 | 0.027955 | 0.027956 | 0.027956 | 0.99684 | -0.060655 | 0.99659 | -0.065569 | 7.6801
25 | 0.018723 | 0.0046927 | -0.018722 | -0.0046922 | 8.4491e-07 | 5.0318e-07 | 0.027956 | 0.027956 | 0.027956 | 0.99659 | -0.065569 | 0.99654 | -0.066517 | 7.6801

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2272 | 0.056835

## res_load
| p_mw | q_mvar
0 | 0.011264 | 0.002823
1 | 0.025231 | 0.0063235
2 | 0.0088822 | 0.0022261
3 | 0.0021407 | 0.00053651
4 | 0.0020775 | 0.00052068
5 | 0.0045282 | 0.0011349
6 | 0.0045385 | 0.0011375
7 | 0.052203 | 0.013083
8 | 0.010738 | 0.0026912
9 | 0.018743 | 0.0046976
10 | 0.012626 | 0.0031644
11 | 0.034276 | 0.0085903
12 | 0.018767 | 0.0047034
13 | 0.018722 | 0.0046922

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1