## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-13_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-13_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-13_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2196-13_0_6_node_32 | 0.4 | n |  | TRUE
4 | bus_LV_2196-13_0_6_node_36 | 0.4 | n |  | TRUE
5 | bus_LV_2196-13_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2196-13_0_6_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_2196-13_0_6_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_2196-13_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2196-13_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2196-13_0_6_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_2196-13_0_6_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_2196-13_0_6_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_2196-13_0_6_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_2196-13_0_6_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2196-13_0_6_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_2196-13_0_6_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_2196-13_0_6_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_2196-13_0_6_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2196-13_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2196-13_0_6_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_2196-13_0_6_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2196-13_0_6_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_2196-13_0_6_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_2196-13_0_6_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2196-13_0_6_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_2196-13_0_6_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2196-13_0_6_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_2196-13_0_6_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2196-13_0_6_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_2196-13_0_6_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_2196-13_0_6_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_2196-13_0_6_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_2196-13_0_6_node_31 | 0.4 | n |  | TRUE
34 | bus_MV_507_0_node_118 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-13_0_6_load_0 | 0 | 0.016042 | 0.0040205 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-13_0_6_load_32 | 3 | 0.025132 | 0.0062986 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-13_0_6_load_36 | 4 | 0.024939 | 0.0062502 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-13_0_6_load_20 | 6 | 0.042572 | 0.010669 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-13_0_6_load_17 | 7 | 0.015946 | 0.0039964 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-13_0_6_load_24 | 10 | 0.026285 | 0.0065877 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-13_0_6_load_26 | 11 | 0.016263 | 0.0040758 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-13_0_6_load_30 | 12 | 0.019749 | 0.0049495 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-13_0_6_load_35 | 13 | 0.025917 | 0.0064955 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-13_0_6_load_18 | 15 | 0.01845 | 0.004624 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-13_0_6_load_34 | 16 | 0.0041766 | 0.0010468 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-13_0_6_load_33 | 17 | 0.017633 | 0.0044192 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-13_0_6_load_11 | 19 | 0.049668 | 0.012448 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-13_0_6_load_8 | 20 | 0.059351 | 0.014875 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-13_0_6_load_21 | 22 | 0.052565 | 0.013174 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-13_0_6_load_23 | 23 | 0.014813 | 0.0037125 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-13_0_6_load_10 | 25 | 0.027693 | 0.0069405 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-13_0_6_load_15 | 26 | 0.027821 | 0.0069727 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-13_0_6_load_27 | 27 | 0.015515 | 0.0038885 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-13_0_6_load_22 | 28 | 0.0024367 | 0.0006107 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-13_0_6_load_28 | 29 | 0.019774 | 0.0049559 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-13_0_6_load_19 | 30 | 0.0078318 | 0.0019628 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-13_0_6_load_25 | 31 | 0.015238 | 0.003819 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-13_0_6_load_29 | 32 | 0.02618 | 0.0065614 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2196-13_0_6_load_31 | 33 | 0.027042 | 0.0067774 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-13_0_6_line_0 |  | 0 | 1 | 0.021943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-13_0_6_line_1 |  | 1 | 2 | 0.01322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-13_0_6_line_2 |  | 2 | 3 | 0.0052826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-13_0_6_line_3 |  | 2 | 4 | 0.004959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-13_0_6_line_4 |  | 3 | 12 | 0.010486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-13_0_6_line_5 |  | 4 | 13 | 0.011022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2196-13_0_6_line_6 |  | 5 | 6 | 0.00015218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2196-13_0_6_line_7 |  | 5 | 7 | 0.010799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2196-13_0_6_line_8 |  | 6 | 14 | 0.035549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2196-13_0_6_line_9 |  | 7 | 15 | 0.0054959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2196-13_0_6_line_10 |  | 8 | 9 | 0.034921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-13_0_6_line_11 |  | 8 | 10 | 0.043666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-13_0_6_line_12 |  | 9 | 11 | 0.033351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-13_0_6_line_13 |  | 10 | 23 | 0.014113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-13_0_6_line_14 |  | 11 | 24 | 0.011827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-13_0_6_line_15 |  | 12 | 32 | 0.00094739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-13_0_6_line_16 |  | 13 | 31 | 0.011289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2196-13_0_6_line_17 |  | 14 | 21 | 0.011086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2196-13_0_6_line_18 |  | 15 | 30 | 0.0045318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2196-13_0_6_line_19 |  | 16 | 17 | 0.0082421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-13_0_6_line_20 |  | 17 | 33 | 0.013934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-13_0_6_line_21 |  | 18 | 19 | 0.032417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2196-13_0_6_line_22 |  | 18 | 20 | 0.015061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2196-13_0_6_line_23 |  | 19 | 22 | 0.0319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2196-13_0_6_line_24 |  | 20 | 25 | 0.0036731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2196-13_0_6_line_25 |  | 21 | 22 | 0.018642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2196-13_0_6_line_26 |  | 23 | 28 | 0.0098272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-13_0_6_line_27 |  | 24 | 27 | 0.015756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-13_0_6_line_28 |  | 24 | 25 | 0.029346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-13_0_6_line_29 |  | 25 | 26 | 0.040247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-13_0_6_line_30 |  | 27 | 29 | 0.0067893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-13_0_6_line_31 |  | 30 | 31 | 0.0057562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2196-13_0_6_line_32 |  | 32 | 33 | 0.010667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-13_0_6_trafo_9 | 0.63 MVA 20/0.4 kV | 34 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2578311.1113 | 1183888.4239 | 2578292.9005 | 1183900.6663
1 | 2578318.3573 | 1183899.4922 | 2578311.1113 | 1183888.4239
2 | 2578318.3573 | 1183899.4922 | 2578322.7881 | 1183896.6156
3 | 2578318.3573 | 1183899.4922 | 2578314.1596 | 1183902.1324
4 | 2578331.5834 | 1183890.9054 | 2578322.7881 | 1183896.6156
5 | 2578304.8296 | 1183908.0006 | 2578314.1596 | 1183902.1324
6 | 2578275.8297 | 1183932.2306 | 2578275.7204 | 1183932.3365
7 | 2578275.8297 | 1183932.2306 | 2578283.6125 | 1183924.7449
8 | 2578252.1337 | 1183958.7418 | 2578260.2215 | 1183947.3509 | 2578275.7204 | 1183932.3365
9 | 2578283.6125 | 1183924.7449 | 2578285.703 | 1183922.7342 | 2578287.7186 | 1183921.0992
10 | 2578419.4815 | 1184034.2737 | 2578420.8758 | 1184027.2316 | 2578421.723 | 1184022.9819 | 2578427.442 | 1184000.2827
11 | 2578419.4815 | 1184034.2737 | 2578420.2049 | 1184035.883 | 2578420.2765 | 1184043.0087 | 2578424.9492 | 1184064.4696 | 2578427.9478 | 1184076.9261
12 | 2578427.442 | 1184000.2827 | 2578409.8766 | 1183999.8238 | 2578402.1981 | 1183999.9517 | 2578394.1714 | 1183998.8622
13 | 2578427.9478 | 1184076.9261 | 2578431.2509 | 1184090.6475
14 | 2578382.4567 | 1183997.2439 | 2578383.0525 | 1183997.353 | 2578394.1714 | 1183998.8622
15 | 2578331.5834 | 1183890.9054 | 2578332.378 | 1183890.3895
16 | 2578304.8296 | 1183908.0006 | 2578300.544 | 1183910.6961 | 2578295.7086 | 1183914.6183
17 | 2578254.7879 | 1183968.6262 | 2578255.4443 | 1183966.5116 | 2578255.482 | 1183964.2992 | 2578254.9093 | 1183962.1557 | 2578253.765 | 1183960.2478 | 2578252.1337 | 1183958.7418
18 | 2578291.2381 | 1183918.2444 | 2578287.7186 | 1183921.0992
19 | 2578353.0114 | 1183876.9936 | 2578355.0173 | 1183875.6912 | 2578359.8799 | 1183872.4381
20 | 2578341.3247 | 1183884.581 | 2578353.0114 | 1183876.9936
21 | 2578335.1296 | 1183988.3109 | 2578303.2912 | 1183982.2116
22 | 2578335.1296 | 1183988.3109 | 2578349.9288 | 1183991.1082
23 | 2578303.2912 | 1183982.2116 | 2578297.2581 | 1183981.0559 | 2578272.3065 | 1183974.6661
24 | 2578353.538 | 1183991.7904 | 2578349.9288 | 1183991.1082
25 | 2578254.7879 | 1183968.6262 | 2578259.9427 | 1183971.3978 | 2578265.6275 | 1183972.9556 | 2578272.3065 | 1183974.6661
26 | 2578433.5509 | 1184100.2017 | 2578431.2509 | 1184090.6475
27 | 2578382.4567 | 1183997.2439 | 2578381.7489 | 1183987.2746 | 2578381.241 | 1183981.535
28 | 2578382.4567 | 1183997.2439 | 2578353.538 | 1183991.7904
29 | 2578353.538 | 1183991.7904 | 2578349.6401 | 1184013.527 | 2578353.5815 | 1184014.3019 | 2578367.4982 | 1184016.8417
30 | 2578380.6426 | 1183974.7721 | 2578381.241 | 1183981.535
31 | 2578291.2381 | 1183918.2444 | 2578295.7086 | 1183914.6183
32 | 2578332.378 | 1183890.3895 | 2578341.3247 | 1183884.581

## bus_geodata
| x | y | coords
0 | 2578292.9005 | 1183900.6663
1 | 2578311.1113 | 1183888.4239
2 | 2578318.3573 | 1183899.4922
3 | 2578322.7881 | 1183896.6156
4 | 2578314.1596 | 1183902.1324
5 | 2578275.8297 | 1183932.2306
6 | 2578275.7204 | 1183932.3365
7 | 2578283.6125 | 1183924.7449
8 | 2578419.4815 | 1184034.2737
9 | 2578427.442 | 1184000.2827
10 | 2578427.9478 | 1184076.9261
11 | 2578394.1714 | 1183998.8622
12 | 2578331.5834 | 1183890.9054
13 | 2578304.8296 | 1183908.0006
14 | 2578252.1337 | 1183958.7418
15 | 2578287.7186 | 1183921.0992
16 | 2578359.8799 | 1183872.4381
17 | 2578353.0114 | 1183876.9936
18 | 2578335.1296 | 1183988.3109
19 | 2578303.2912 | 1183982.2116
20 | 2578349.9288 | 1183991.1082
21 | 2578254.7879 | 1183968.6262
22 | 2578272.3065 | 1183974.6661
23 | 2578431.2509 | 1184090.6475
24 | 2578382.4567 | 1183997.2439
25 | 2578353.538 | 1183991.7904
26 | 2578367.4982 | 1184016.8417
27 | 2578381.241 | 1183981.535
28 | 2578433.5509 | 1184100.2017
29 | 2578380.6426 | 1183974.7721
30 | 2578291.2381 | 1183918.2444
31 | 2578295.7086 | 1183914.6183
32 | 2578332.378 | 1183890.3895
33 | 2578341.3247 | 1183884.581
34 | 2578353.538 | 1183991.7904

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98258 | -0.33522 | 0.016042 | 0.0040205
1 | 0.98291 | -0.32887 | 0 | 0
2 | 0.9831 | -0.32504 | 0 | 0
3 | 0.98252 | -0.33647 | 0.025132 | 0.0062986
4 | 0.98372 | -0.31289 | 0.024939 | 0.0062502
5 | 0.98704 | -0.24841 | 0 | 0
6 | 0.98705 | -0.24819 | 0.042572 | 0.010669
7 | 0.98623 | -0.26416 | 0.015946 | 0.0039964
8 | 0.99288 | -0.13694 | 0 | 0
9 | 0.99427 | -0.1101 | 0 | 0
10 | 0.99114 | -0.17061 | 0.026285 | 0.0065877
11 | 0.99559 | -0.084531 | 0.016263 | 0.0040758
12 | 0.9816 | -0.35443 | 0.019749 | 0.0049495
13 | 0.98454 | -0.29693 | 0.025917 | 0.0064955
14 | 0.99018 | -0.18757 | 0 | 0
15 | 0.98584 | -0.27165 | 0.01845 | 0.004624
16 | 0.98074 | -0.37128 | 0.0041766 | 0.0010468
17 | 0.98077 | -0.37066 | 0.017633 | 0.0044192
18 | 1 | 0 | -0.60627 | -0.15369
19 | 0.99613 | -0.073567 | 0.049668 | 0.012448
20 | 0.99904 | -0.01839 | 0.059351 | 0.014875
21 | 0.99116 | -0.16875 | 0 | 0
22 | 0.99281 | -0.13718 | 0.052565 | 0.013174
23 | 0.99091 | -0.17493 | 0.014813 | 0.0037125
24 | 0.99624 | -0.072103 | 0 | 0
25 | 0.99879 | -0.023221 | 0.027693 | 0.0069405
26 | 0.99777 | -0.042805 | 0.027821 | 0.0069727
27 | 0.99573 | -0.081873 | 0.015515 | 0.0038885
28 | 0.99089 | -0.17536 | 0.0024367 | 0.0006107
29 | 0.99561 | -0.084233 | 0.019774 | 0.0049559
30 | 0.98555 | -0.27734 | 0.0078318 | 0.0019628
31 | 0.98519 | -0.2843 | 0.015238 | 0.003819
32 | 0.98153 | -0.35572 | 0.02618 | 0.0065614
33 | 0.98105 | -0.36515 | 0.027042 | 0.0067774
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016042 | -0.0040205 | 0.016047 | 0.0040234 | 4.8566e-06 | 2.8302e-06 | 0.024294 | 0.024294 | 0.024294 | 0.98258 | -0.33522 | 0.98291 | -0.32887 | 6.6742
1 | -0.016047 | -0.0040234 | 0.01605 | 0.0040251 | 2.9259e-06 | 1.705e-06 | 0.024294 | 0.024294 | 0.024294 | 0.98291 | -0.32887 | 0.9831 | -0.32504 | 6.6742
2 | 0.12009 | 0.030167 | -0.12003 | -0.030125 | 6.547e-05 | 4.1834e-05 | 0.18179 | 0.18179 | 0.18179 | 0.9831 | -0.32504 | 0.98252 | -0.33647 | 49.9436
3 | -0.13614 | -0.034192 | 0.13622 | 0.034242 | 7.8983e-05 | 5.0486e-05 | 0.20609 | 0.20609 | 0.20609 | 0.9831 | -0.32504 | 0.98372 | -0.31289 | 56.6177
4 | 0.094894 | 0.023826 | -0.094813 | -0.023775 | 8.124e-05 | 5.1861e-05 | 0.14373 | 0.14373 | 0.14373 | 0.98252 | -0.33647 | 0.9816 | -0.35443 | 39.487
5 | -0.16116 | -0.040493 | 0.16128 | 0.040571 | 0.00012285 | 7.8343e-05 | 0.24381 | 0.24381 | 0.24381 | 0.98372 | -0.31289 | 0.98454 | -0.29693 | 33.4906
6 | -0.24517 | -0.06179 | 0.24517 | 0.061792 | 2.6004e-06 | 1.6584e-06 | 0.36973 | 0.36973 | 0.36973 | 0.98704 | -0.24841 | 0.98705 | -0.24819 | 33.858
7 | 0.24517 | 0.06179 | -0.24498 | -0.061672 | 0.00018452 | 0.00011768 | 0.36973 | 0.36973 | 0.36973 | 0.98704 | -0.24841 | 0.98623 | -0.26416 | 33.858
8 | -0.28774 | -0.072461 | 0.28858 | 0.072995 | 0.00083663 | 0.00053407 | 0.43391 | 0.43391 | 0.43391 | 0.98705 | -0.24819 | 0.99018 | -0.18757 | 39.7351
9 | 0.22904 | 0.057676 | -0.22896 | -0.057624 | 8.2086e-05 | 5.2325e-05 | 0.34567 | 0.34567 | 0.34567 | 0.98623 | -0.26416 | 0.98584 | -0.27165 | 31.6548
10 | -0.043609 | -0.010957 | 0.043665 | 0.010993 | 5.5952e-05 | 3.5357e-05 | 0.065366 | 0.065366 | 0.065366 | 0.99288 | -0.13694 | 0.99427 | -0.1101 | 17.9577
11 | 0.043609 | 0.010957 | -0.043539 | -0.010913 | 6.9966e-05 | 4.4214e-05 | 0.065366 | 0.065366 | 0.065366 | 0.99288 | -0.13694 | 0.99114 | -0.17061 | 17.9578
12 | -0.043665 | -0.010993 | 0.043718 | 0.011026 | 5.3437e-05 | 3.3767e-05 | 0.065366 | 0.065366 | 0.065366 | 0.99427 | -0.1101 | 0.99559 | -0.084531 | 17.9577
13 | 0.017253 | 0.0043252 | -0.01725 | -0.0043231 | 3.5512e-06 | 2.0909e-06 | 0.025903 | 0.025904 | 0.025904 | 0.99114 | -0.17061 | 0.99091 | -0.17493 | 7.1164
14 | -0.059981 | -0.015102 | 0.060017 | 0.015125 | 3.5662e-05 | 2.267e-05 | 0.089672 | 0.089672 | 0.089672 | 0.99559 | -0.084531 | 0.99624 | -0.072103 | 24.6352
15 | 0.075064 | 0.018825 | -0.07506 | -0.018822 | 4.6006e-06 | 2.9324e-06 | 0.1138 | 0.1138 | 0.1138 | 0.9816 | -0.35443 | 0.98153 | -0.35572 | 31.2625
16 | -0.1872 | -0.047067 | 0.18731 | 0.047138 | 0.000113 | 7.189e-05 | 0.28298 | 0.28298 | 0.28298 | 0.98454 | -0.29693 | 0.98519 | -0.2843 | 25.9142
17 | -0.28858 | -0.072995 | 0.28884 | 0.073162 | 0.0002609 | 0.00016655 | 0.43391 | 0.43391 | 0.43391 | 0.99018 | -0.18757 | 0.99116 | -0.16875 | 39.7351
18 | 0.21051 | 0.053 | -0.21045 | -0.052963 | 5.722e-05 | 3.6447e-05 | 0.31782 | 0.31782 | 0.31782 | 0.98584 | -0.27165 | 0.98555 | -0.27734 | 29.1046
19 | -0.0041766 | -0.0010468 | 0.0041768 | 0.0010467 | 1.2412e-07 | -2.4574e-08 | 0.006337 | 0.0063369 | 0.006337 | 0.98074 | -0.37128 | 0.98077 | -0.37066 | 1.7409
20 | -0.02181 | -0.005466 | 0.021815 | 0.0054695 | 5.7211e-06 | 3.4856e-06 | 0.03309 | 0.033089 | 0.03309 | 0.98077 | -0.37066 | 0.98105 | -0.36515 | 9.0905
21 | 0.39396 | 0.10063 | -0.39256 | -0.099733 | 0.0013957 | 0.00089198 | 0.58688 | 0.58688 | 0.58688 | 1 | 0 | 0.99613 | -0.073567 | 53.7439
22 | 0.21066 | 0.053068 | -0.21047 | -0.05295 | 0.0001851 | 0.00011787 | 0.31356 | 0.31356 | 0.31356 | 1 | 0 | 0.99904 | -0.01839 | 28.7143
23 | 0.34289 | 0.087285 | -0.34185 | -0.086616 | 0.0010481 | 0.00066955 | 0.51269 | 0.51269 | 0.51269 | 0.99613 | -0.073567 | 0.99281 | -0.13718 | 46.9497
24 | 0.15112 | 0.038075 | -0.15109 | -0.038053 | 3.4916e-05 | 2.225e-05 | 0.22516 | 0.22516 | 0.22516 | 0.99904 | -0.01839 | 0.99879 | -0.023221 | 30.9286
25 | -0.28884 | -0.073162 | 0.28928 | 0.073442 | 0.00043872 | 0.00028006 | 0.43391 | 0.43391 | 0.43391 | 0.99116 | -0.16875 | 0.99281 | -0.13718 | 39.7351
26 | 0.0024368 | 0.00061061 | -0.0024367 | -0.0006107 | 4.9344e-08 | -9.501e-08 | 0.0036592 | 0.0036592 | 0.0036592 | 0.99091 | -0.17493 | 0.99089 | -0.17536 | 1.0053
27 | 0.035308 | 0.0088561 | -0.035292 | -0.0088458 | 1.6435e-05 | 1.0313e-05 | 0.05274 | 0.05274 | 0.05274 | 0.99624 | -0.072103 | 0.99573 | -0.081873 | 14.4891
28 | -0.095325 | -0.023981 | 0.095548 | 0.024123 | 0.00022319 | 0.00014246 | 0.14241 | 0.14241 | 0.14241 | 0.99624 | -0.072103 | 0.99879 | -0.023221 | 39.1242
29 | 0.027847 | 0.0069888 | -0.027821 | -0.0069727 | 2.5982e-05 | 1.6102e-05 | 0.041491 | 0.041491 | 0.041491 | 0.99879 | -0.023221 | 0.99777 | -0.042805 | 11.3987
30 | 0.019777 | 0.0049572 | -0.019774 | -0.0049559 | 2.2238e-06 | 1.3349e-06 | 0.029554 | 0.029554 | 0.029554 | 0.99573 | -0.081873 | 0.99561 | -0.084233 | 8.1193
31 | 0.20262 | 0.051 | -0.20255 | -0.050957 | 6.7373e-05 | 4.2899e-05 | 0.306 | 0.306 | 0.306 | 0.98555 | -0.27734 | 0.98519 | -0.2843 | 28.0218
32 | 0.048879 | 0.012261 | -0.048857 | -0.012247 | 2.1967e-05 | 1.3924e-05 | 0.074106 | 0.074106 | 0.074106 | 0.98153 | -0.35572 | 0.98105 | -0.36515 | 20.3587

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60627 | 0.15369

## res_load
| p_mw | q_mvar
0 | 0.016042 | 0.0040205
1 | 0.025132 | 0.0062986
2 | 0.024939 | 0.0062502
3 | 0.042572 | 0.010669
4 | 0.015946 | 0.0039964
5 | 0.026285 | 0.0065877
6 | 0.016263 | 0.0040758
7 | 0.019749 | 0.0049495
8 | 0.025917 | 0.0064955
9 | 0.01845 | 0.004624
10 | 0.0041766 | 0.0010468
11 | 0.017633 | 0.0044192
12 | 0.049668 | 0.012448
13 | 0.059351 | 0.014875
14 | 0.052565 | 0.013174
15 | 0.014813 | 0.0037125
16 | 0.027693 | 0.0069405
17 | 0.027821 | 0.0069727
18 | 0.015515 | 0.0038885
19 | 0.0024367 | 0.0006107
20 | 0.019774 | 0.0049559
21 | 0.0078318 | 0.0019628
22 | 0.015238 | 0.003819
23 | 0.02618 | 0.0065614
24 | 0.027042 | 0.0067774

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1