## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-28_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-28_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-28_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-28_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-28_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2196-28_0_3_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_2196-28_0_3_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_2196-28_0_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_2196-28_0_3_node_50 | 0.4 | n |  | TRUE
9 | bus_LV_2196-28_0_3_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_2196-28_0_3_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_2196-28_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_2196-28_0_3_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_2196-28_0_3_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_2196-28_0_3_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_2196-28_0_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_2196-28_0_3_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_2196-28_0_3_node_51 | 0.4 | n |  | TRUE
18 | bus_LV_2196-28_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_2196-28_0_3_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_2196-28_0_3_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_2196-28_0_3_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_2196-28_0_3_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_2196-28_0_3_node_60 | 0.4 | n |  | TRUE
24 | bus_LV_2196-28_0_3_node_59 | 0.4 | n |  | TRUE
25 | bus_MV_507_0_node_128 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-28_0_3_load_0 | 0 | 0.04989 | 0.012504 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-28_0_3_load_1 | 1 | 0.009492 | 0.0023789 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-28_0_3_load_3 | 3 | 0.0027361 | 0.00068574 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-28_0_3_load_4 | 4 | 0.0026197 | 0.00065655 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-28_0_3_load_36 | 5 | 0.0021007 | 0.00052647 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-28_0_3_load_18 | 6 | 0.0040832 | 0.0010234 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-28_0_3_load_57 | 9 | 0.025742 | 0.0064517 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-28_0_3_load_15 | 10 | 0.012105 | 0.0030338 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-28_0_3_load_21 | 12 | 0.032372 | 0.0081132 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-28_0_3_load_24 | 15 | 0.015968 | 0.004002 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-28_0_3_load_45 | 20 | 0.096915 | 0.024289 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-28_0_3_load_46 | 22 | 0.0080291 | 0.0020123 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-28_0_3_load_60 | 23 | 0.023704 | 0.0059408 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-28_0_3_load_59 | 24 | 0.01845 | 0.004624 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-28_0_3_line_0 |  | 0 | 1 | 0.0084777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-28_0_3_line_1 |  | 0 | 2 | 0.036966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-28_0_3_line_2 |  | 2 | 3 | 0.020067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-28_0_3_line_3 |  | 2 | 4 | 0.0055556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-28_0_3_line_4 |  | 3 | 5 | 0.029066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-28_0_3_line_5 |  | 4 | 6 | 0.031116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-28_0_3_line_6 |  | 5 | 16 | 0.04129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-28_0_3_line_7 |  | 6 | 11 | 0.012651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-28_0_3_line_8 |  | 7 | 8 | 0.030491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-28_0_3_line_9 |  | 7 | 9 | 0.020197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-28_0_3_line_10 |  | 8 | 24 | 0.011867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-28_0_3_line_11 |  | 8 | 17 | 0.072595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-28_0_3_line_12 |  | 10 | 11 | 0.04289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-28_0_3_line_13 |  | 12 | 13 | 0.042318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-28_0_3_line_14 |  | 12 | 14 | 0.052034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-28_0_3_line_15 |  | 13 | 15 | 0.039985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-28_0_3_line_16 |  | 14 | 16 | 0.019809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-28_0_3_line_17 |  | 15 | 17 | 0.022477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-28_0_3_line_18 |  | 17 | 21 | 0.057086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2196-28_0_3_line_19 |  | 18 | 19 | 0.1269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-28_0_3_line_20 |  | 18 | 20 | 0.047399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-28_0_3_line_21 |  | 19 | 23 | 0.023181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-28_0_3_line_22 |  | 20 | 22 | 5.5233e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-28_0_3_line_23 |  | 21 | 22 | 0.018702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-28_0_3_trafo_51 | 0.63 MVA 20/0.4 kV | 25 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2577876.0919 | 1184710.2158 | 2577876.0298 | 1184701.7383
1 | 2577872.3285 | 1184746.2155 | 2577876.2993 | 1184738.5301 | 2577876.0919 | 1184710.2158
2 | 2577872.3285 | 1184746.2155 | 2577889.9036 | 1184755.8997
3 | 2577872.3285 | 1184746.2155 | 2577867.6123 | 1184743.2792
4 | 2577914.9991 | 1184770.5235 | 2577907.8601 | 1184765.794 | 2577889.9036 | 1184755.8997
5 | 2577867.6123 | 1184743.2792 | 2577861.8559 | 1184739.6953 | 2577841.0893 | 1184727.0096
6 | 2577950.6624 | 1184786.7911 | 2577945.3958 | 1184788.7561 | 2577940.5676 | 1184787.4621 | 2577914.9991 | 1184770.5235
7 | 2577830.2939 | 1184720.4136 | 2577837.5992 | 1184724.8776 | 2577841.0893 | 1184727.0096
8 | 2577833.8414 | 1184641.9817 | 2577858.1519 | 1184646.5382 | 2577863.9914 | 1184646.7389
9 | 2577833.8414 | 1184641.9817 | 2577825.8088 | 1184636.9422 | 2577829.6075 | 1184626.924
10 | 2577863.9914 | 1184646.7389 | 2577859.6458 | 1184635.6937
11 | 2577929.9127 | 1184665.6379 | 2577912.068 | 1184649.0286 | 2577906.9105 | 1184649.548 | 2577885.4866 | 1184647.4596 | 2577863.9914 | 1184646.7389
12 | 2577830.2939 | 1184720.4136 | 2577831.9965 | 1184714.4152 | 2577832.1323 | 1184677.7605
13 | 2577989.1715 | 1184680.638 | 2577986.2346 | 1184689.3423 | 2577974.6569 | 1184720.3853
14 | 2577958.2694 | 1184769.6763 | 2577958.3863 | 1184768.2752 | 2577958.5032 | 1184766.8629 | 2577969.2079 | 1184734.9956 | 2577974.6569 | 1184720.3853
15 | 2577989.1715 | 1184680.638 | 2577949.6721 | 1184674.4236
16 | 2577958.2694 | 1184769.6763 | 2577957.1887 | 1184778.7628 | 2577954.917 | 1184783.6182 | 2577950.6624 | 1184786.7911
17 | 2577929.9127 | 1184665.6379 | 2577938.0133 | 1184672.5894 | 2577949.6721 | 1184674.4236
18 | 2577929.9127 | 1184665.6379 | 2577954.8036 | 1184629.0602 | 2577947.4451 | 1184618.4818
19 | 2577896.748 | 1184576.403 | 2577893.1808 | 1184571.5136 | 2577891.2283 | 1184565.7178 | 2577875.0245 | 1184547.1238 | 2577873.1089 | 1184551.2775 | 2577872.4583 | 1184554.904 | 2577871.5271 | 1184556.953 | 2577870.0947 | 1184557.6142 | 2577868.1099 | 1184557.5104 | 2577866.4576 | 1184558.5615 | 2577865.5296 | 1184561.4887 | 2577865.3181 | 1184564.1242 | 2577864.2178 | 1184565.8403 | 2577862.6182 | 1184566.7244 | 2577860.5974 | 1184571.301 | 2577849.6159 | 1184559.3911 | 2577823.1789 | 1184547.4942 | 2577820.4933 | 1184553.9408 | 2577819.041 | 1184557.4481 | 2577817.702 | 1184560.6658
20 | 2577896.748 | 1184576.403 | 2577934.395 | 1184605.2015
21 | 2577817.702 | 1184560.6658 | 2577817.7743 | 1184567.8026 | 2577832.4151 | 1184574.4517
22 | 2577934.4388 | 1184605.235 | 2577934.395 | 1184605.2015
23 | 2577947.4451 | 1184618.4818 | 2577940.7433 | 1184610.0578 | 2577934.4388 | 1184605.235

## bus_geodata
| x | y | coords
0 | 2577876.0919 | 1184710.2158
1 | 2577876.0298 | 1184701.7383
2 | 2577872.3285 | 1184746.2155
3 | 2577889.9036 | 1184755.8997
4 | 2577867.6123 | 1184743.2792
5 | 2577914.9991 | 1184770.5235
6 | 2577841.0893 | 1184727.0096
7 | 2577833.8414 | 1184641.9817
8 | 2577863.9914 | 1184646.7389
9 | 2577829.6075 | 1184626.924
10 | 2577832.1323 | 1184677.7605
11 | 2577830.2939 | 1184720.4136
12 | 2577974.6569 | 1184720.3853
13 | 2577989.1715 | 1184680.638
14 | 2577958.2694 | 1184769.6763
15 | 2577949.6721 | 1184674.4236
16 | 2577950.6624 | 1184786.7911
17 | 2577929.9127 | 1184665.6379
18 | 2577896.748 | 1184576.403
19 | 2577817.702 | 1184560.6658
20 | 2577934.395 | 1184605.2015
21 | 2577947.4451 | 1184618.4818
22 | 2577934.4388 | 1184605.235
23 | 2577832.4151 | 1184574.4517
24 | 2577859.6458 | 1184635.6937
25 | 2577912.068 | 1184649.0286

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97401 | -0.50035 | 0.04989 | 0.012504
1 | 0.97393 | -0.50183 | 0.009492 | 0.0023789
2 | 0.97605 | -0.46011 | 0 | 0
3 | 0.97751 | -0.43145 | 0.0027361 | 0.00068574
4 | 0.97596 | -0.46202 | 0.0026197 | 0.00065655
5 | 0.9797 | -0.38863 | 0.0021007 | 0.00052647
6 | 0.97549 | -0.47124 | 0.0040832 | 0.0010234
7 | 0.99637 | -0.069855 | 0 | 0
8 | 0.99708 | -0.056084 | 0 | 0
9 | 0.99589 | -0.078987 | 0.025742 | 0.0064517
10 | 0.97486 | -0.48357 | 0.012105 | 0.0030338
11 | 0.97535 | -0.47405 | 0 | 0
12 | 0.98845 | -0.21956 | 0.032372 | 0.0081132
13 | 0.99298 | -0.13283 | 0 | 0
14 | 0.98443 | -0.29695 | 0 | 0
15 | 0.99726 | -0.05161 | 0.015968 | 0.004002
16 | 0.98289 | -0.32658 | 0 | 0
17 | 1 | 0 | -0.30954 | -0.078586
18 | 0.99003 | -0.19156 | 0 | 0
19 | 0.98727 | -0.24521 | 0 | 0
20 | 0.99106 | -0.1716 | 0.096915 | 0.024289
21 | 0.99327 | -0.12888 | 0 | 0
22 | 0.99107 | -0.17148 | 0.0080291 | 0.0020123
23 | 0.98676 | -0.25504 | 0.023704 | 0.0059408
24 | 0.99688 | -0.059923 | 0.01845 | 0.004624
25 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0094927 | 0.0023793 | -0.009492 | -0.0023789 | 6.6863e-07 | 3.2241e-07 | 0.014502 | 0.014502 | 0.014502 | 0.97401 | -0.50035 | 0.97393 | -0.50183 | 3.9842
1 | -0.059383 | -0.014883 | 0.059497 | 0.014955 | 0.00011409 | 7.2555e-05 | 0.09072 | 0.09072 | 0.09072 | 0.97401 | -0.50035 | 0.97605 | -0.46011 | 24.9231
2 | -0.078321 | -0.019678 | 0.078428 | 0.019747 | 0.00010731 | 6.8429e-05 | 0.11942 | 0.11942 | 0.11942 | 0.97605 | -0.46011 | 0.97751 | -0.43145 | 32.8075
3 | 0.018824 | 0.0047228 | -0.018822 | -0.0047218 | 1.7159e-06 | 1.0288e-06 | 0.028699 | 0.028699 | 0.028699 | 0.97605 | -0.46011 | 0.97596 | -0.46202 | 7.8844
4 | -0.081164 | -0.020432 | 0.081331 | 0.020539 | 0.00016647 | 0.00010618 | 0.12358 | 0.12358 | 0.12358 | 0.97751 | -0.43145 | 0.9797 | -0.38863 | 33.9517
5 | 0.016203 | 0.0040652 | -0.016195 | -0.004061 | 7.1218e-06 | 4.1693e-06 | 0.024705 | 0.024705 | 0.024705 | 0.97596 | -0.46202 | 0.97549 | -0.47124 | 6.7872
6 | -0.083431 | -0.021065 | 0.08368 | 0.021224 | 0.00024885 | 0.00015874 | 0.12677 | 0.12677 | 0.12677 | 0.9797 | -0.38863 | 0.98289 | -0.32658 | 34.8282
7 | 0.012112 | 0.0030377 | -0.012111 | -0.0030368 | 1.6196e-06 | 8.7864e-07 | 0.018477 | 0.018477 | 0.018477 | 0.97549 | -0.47124 | 0.97535 | -0.47405 | 5.0761
8 | -0.025754 | -0.0064586 | 0.025771 | 0.006469 | 1.6916e-05 | 1.0429e-05 | 0.038463 | 0.038463 | 0.038463 | 0.99637 | -0.069855 | 0.99708 | -0.056084 | 10.5668
9 | 0.025754 | 0.0064586 | -0.025742 | -0.0064517 | 1.1205e-05 | 6.9081e-06 | 0.038463 | 0.038463 | 0.038463 | 0.99637 | -0.069855 | 0.99589 | -0.078987 | 10.5668
10 | 0.018453 | 0.004626 | -0.01845 | -0.004624 | 3.3751e-06 | 2.0053e-06 | 0.02754 | 0.02754 | 0.02754 | 0.99708 | -0.056084 | 0.99688 | -0.059923 | 7.5659
11 | -0.044224 | -0.011095 | 0.044342 | 0.01117 | 0.00011859 | 7.4949e-05 | 0.066003 | 0.066002 | 0.066003 | 0.99708 | -0.056084 | 1 | 0 | 18.1326
12 | -0.012105 | -0.0030338 | 0.012111 | 0.0030368 | 5.491e-06 | 2.9792e-06 | 0.018477 | 0.018477 | 0.018477 | 0.97486 | -0.48357 | 0.97535 | -0.47405 | 5.0761
13 | -0.11649 | -0.029613 | 0.11697 | 0.029925 | 0.00048882 | 0.0003123 | 0.17551 | 0.17551 | 0.17551 | 0.98845 | -0.21956 | 0.99298 | -0.13283 | 48.2162
14 | 0.084113 | 0.0215 | -0.083799 | -0.0213 | 0.0003136 | 0.00020004 | 0.12677 | 0.12677 | 0.12677 | 0.98845 | -0.21956 | 0.98443 | -0.29695 | 34.8281
15 | -0.11697 | -0.029925 | 0.11744 | 0.030221 | 0.00046187 | 0.00029508 | 0.17551 | 0.17551 | 0.17551 | 0.99298 | -0.13283 | 0.99726 | -0.05161 | 48.2162
16 | 0.083799 | 0.0213 | -0.08368 | -0.021224 | 0.00011939 | 7.6156e-05 | 0.12677 | 0.12677 | 0.12677 | 0.98443 | -0.29695 | 0.98289 | -0.32658 | 34.8282
17 | -0.1334 | -0.034223 | 0.13374 | 0.034437 | 0.0003349 | 0.00021404 | 0.19933 | 0.19933 | 0.19933 | 0.99726 | -0.05161 | 1 | 0 | 54.7616
18 | 0.12981 | 0.032979 | -0.12901 | -0.032468 | 0.00079997 | 0.00051124 | 0.19331 | 0.19331 | 0.19331 | 1 | 0 | 0.99327 | -0.12888 | 53.1074
19 | 0.023776 | 0.0059849 | -0.023715 | -0.0059476 | 6.0804e-05 | 3.7287e-05 | 0.035744 | 0.035745 | 0.035745 | 0.99003 | -0.19156 | 0.98727 | -0.24521 | 9.82
20 | -0.023776 | -0.0059849 | 0.023799 | 0.0059988 | 2.271e-05 | 1.3924e-05 | 0.035744 | 0.035744 | 0.035744 | 0.99003 | -0.19156 | 0.99106 | -0.1716 | 9.8199
21 | 0.023715 | 0.0059476 | -0.023704 | -0.0059408 | 1.1107e-05 | 6.8122e-06 | 0.035745 | 0.035745 | 0.035745 | 0.98727 | -0.24521 | 0.98676 | -0.25504 | 9.8201
22 | -0.12071 | -0.030288 | 0.12071 | 0.030288 | 6.8048e-07 | 4.348e-07 | 0.18126 | 0.18126 | 0.18126 | 0.99106 | -0.1716 | 0.99107 | -0.17148 | 49.7956
23 | 0.12901 | 0.032468 | -0.12874 | -0.032301 | 0.00026208 | 0.00016749 | 0.19331 | 0.19331 | 0.19331 | 0.99327 | -0.12888 | 0.99107 | -0.17148 | 53.1074

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30954 | 0.078586

## res_load
| p_mw | q_mvar
0 | 0.04989 | 0.012504
1 | 0.009492 | 0.0023789
2 | 0.0027361 | 0.00068574
3 | 0.0026197 | 0.00065655
4 | 0.0021007 | 0.00052647
5 | 0.0040832 | 0.0010234
6 | 0.025742 | 0.0064517
7 | 0.012105 | 0.0030338
8 | 0.032372 | 0.0081132
9 | 0.015968 | 0.004002
10 | 0.096915 | 0.024289
11 | 0.0080291 | 0.0020123
12 | 0.023704 | 0.0059408
13 | 0.01845 | 0.004624

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1