## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-33_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-33_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-33_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2196-33_0_3_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_2196-33_0_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_2196-33_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2196-33_0_3_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_2196-33_0_3_node_45 | 0.4 | n |  | TRUE
8 | bus_LV_2196-33_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2196-33_0_3_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_2196-33_0_3_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_2196-33_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2196-33_0_3_node_27 | 0.4 | n |  | TRUE
13 | bus_LV_2196-33_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2196-33_0_3_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_2196-33_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2196-33_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_2196-33_0_3_node_48 | 0.4 | n |  | TRUE
18 | bus_LV_2196-33_0_3_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_2196-33_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_2196-33_0_3_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_2196-33_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2196-33_0_3_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_2196-33_0_3_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_2196-33_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2196-33_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2196-33_0_3_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_2196-33_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2196-33_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2196-33_0_3_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_2196-33_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2196-33_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2196-33_0_3_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_2196-33_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2196-33_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_2196-33_0_3_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_2196-33_0_3_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_2196-33_0_3_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_2196-33_0_3_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_2196-33_0_3_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2196-33_0_3_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_2196-33_0_3_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2196-33_0_3_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2196-33_0_3_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_2196-33_0_3_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_2196-33_0_3_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_2196-33_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_MV_507_0_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-33_0_3_load_0 | 0 | 0.009335 | 0.0023396 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-33_0_3_load_1 | 1 | 0.0056419 | 0.001414 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-33_0_3_load_19 | 3 | 0.013873 | 0.0034769 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-33_0_3_load_45 | 7 | 0.022714 | 0.0056927 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-33_0_3_load_22 | 9 | 0.011509 | 0.0028844 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-33_0_3_load_20 | 10 | 0.0043583 | 0.0010923 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-33_0_3_load_27 | 12 | 0.0080838 | 0.002026 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-33_0_3_load_26 | 14 | 0.014717 | 0.0036883 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-33_0_3_load_48 | 17 | 0.00085081 | 0.00021323 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-33_0_3_load_47 | 18 | 0.010846 | 0.0027184 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-33_0_3_load_24 | 19 | 0.0056172 | 0.0014078 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-33_0_3_load_38 | 20 | 0.0090338 | 0.0022641 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-33_0_3_load_43 | 22 | 0.024872 | 0.0062334 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-33_0_3_load_42 | 23 | 0.016987 | 0.0042574 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-33_0_3_load_39 | 26 | 0.0083865 | 0.0021019 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-33_0_3_load_49 | 29 | 0.031324 | 0.0078506 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-33_0_3_load_23 | 30 | 0.040534 | 0.010159 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-33_0_3_load_21 | 31 | 0.01206 | 0.0030226 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-33_0_3_load_44 | 32 | 0.016648 | 0.0041724 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-33_0_3_load_25 | 33 | 0.010521 | 0.0026368 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-33_0_3_load_28 | 34 | 0.025667 | 0.0064329 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-33_0_3_load_46 | 35 | 0.0060077 | 0.0015057 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-33_0_3_load_37 | 36 | 0.0047413 | 0.0011883 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-33_0_3_load_41 | 37 | 0.0099757 | 0.0025001 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2196-33_0_3_load_40 | 38 | 0.0066275 | 0.001661 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2196-33_0_3_load_29 | 39 | 0.0086555 | 0.0021693 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2196-33_0_3_load_30 | 40 | 0.012662 | 0.0031733 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2196-33_0_3_load_31 | 41 | 0.0092893 | 0.0023281 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2196-33_0_3_load_32 | 42 | 0.014509 | 0.0036362 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2196-33_0_3_load_33 | 43 | 0.012928 | 0.00324 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2196-33_0_3_load_34 | 44 | 0.0036994 | 0.00092717 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2196-33_0_3_load_35 | 45 | 0.0050222 | 0.0012587 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2196-33_0_3_load_36 | 46 | 0.011204 | 0.0028081 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-33_0_3_line_0 |  | 0 | 1 | 0.0034836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-33_0_3_line_1 |  | 1 | 2 | 0.031306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-33_0_3_line_2 |  | 2 | 3 | 0.033077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-33_0_3_line_3 |  | 2 | 4 | 0.011039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-33_0_3_line_4 |  | 4 | 17 | 0.004115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-33_0_3_line_5 |  | 4 | 13 | 0.036379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-33_0_3_line_6 |  | 4 | 18 | 0.010253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-33_0_3_line_7 |  | 5 | 6 | 0.004945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-33_0_3_line_8 |  | 5 | 7 | 0.010942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-33_0_3_line_9 |  | 6 | 20 | 0.010074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-33_0_3_line_10 |  | 7 | 15 | 0.010035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-33_0_3_line_11 |  | 8 | 9 | 0.0096519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2196-33_0_3_line_12 |  | 8 | 10 | 0.018058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2196-33_0_3_line_13 |  | 9 | 33 | 0.010169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2196-33_0_3_line_14 |  | 10 | 31 | 0.0093593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2196-33_0_3_line_15 |  | 11 | 12 | 0.0088941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2196-33_0_3_line_16 |  | 11 | 13 | 0.055232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-33_0_3_line_17 |  | 11 | 14 | 0.0014164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2196-33_0_3_line_18 |  | 12 | 34 | 0.0062306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2196-33_0_3_line_19 |  | 13 | 19 | 0.013817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-33_0_3_line_20 |  | 14 | 33 | 0.011356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2196-33_0_3_line_21 |  | 15 | 16 | 0.033836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-33_0_3_line_22 |  | 16 | 32 | 0.0039282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-33_0_3_line_23 |  | 18 | 35 | 0.0012989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-33_0_3_line_24 |  | 19 | 30 | 0.0083497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-33_0_3_line_25 |  | 20 | 36 | 0.0054387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-33_0_3_line_26 |  | 21 | 22 | 0.0084737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-33_0_3_line_27 |  | 21 | 23 | 0.016939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-33_0_3_line_28 |  | 22 | 32 | 0.016359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-33_0_3_line_29 |  | 23 | 37 | 0.0068152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-33_0_3_line_30 |  | 24 | 25 | 0.007848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2196-33_0_3_line_31 |  | 24 | 26 | 0.02016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2196-33_0_3_line_32 |  | 25 | 31 | 0.008556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2196-33_0_3_line_33 |  | 26 | 38 | 0.0042825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2196-33_0_3_line_34 |  | 27 | 28 | 0.0096218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2196-33_0_3_line_35 |  | 27 | 29 | 0.0067434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2196-33_0_3_line_36 |  | 28 | 30 | 0.036395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2196-33_0_3_line_37 |  | 36 | 45 | 0.0040147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2196-33_0_3_line_38 |  | 37 | 43 | 0.0049456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2196-33_0_3_line_39 |  | 38 | 42 | 0.0043302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2196-33_0_3_line_40 |  | 39 | 40 | 0.0026127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2196-33_0_3_line_41 |  | 39 | 41 | 0.003117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2196-33_0_3_line_42 |  | 40 | 42 | 0.0079004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2196-33_0_3_line_43 |  | 41 | 43 | 0.0082866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2196-33_0_3_line_44 |  | 44 | 45 | 0.0045726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2196-33_0_3_line_45 |  | 44 | 46 | 0.0019986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-33_0_3_trafo_28 | 0.63 MVA 20/0.4 kV | 47 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2578851.5934 | 1184021.9646 | 2578848.7359 | 1184019.972
1 | 2578822.3507 | 1184003.1252 | 2578847.3902 | 1184019.0336 | 2578848.7359 | 1184019.972
2 | 2578822.3507 | 1184003.1252 | 2578811.3755 | 1184012.0466 | 2578798.2828 | 1184025.7238
3 | 2578815.9697 | 1183996.7557 | 2578819.3826 | 1183999.1448 | 2578818.0818 | 1184000.4056 | 2578822.3507 | 1184003.1252
4 | 2578813.1944 | 1183999.8004 | 2578815.9697 | 1183996.7557
5 | 2578815.9697 | 1183996.7557 | 2578824.8743 | 1183987.2413 | 2578839.78 | 1183978.1393 | 2578843.3127 | 1183973.4354
6 | 2578815.9697 | 1183996.7557 | 2578814.5617 | 1183995.7713 | 2578807.3967 | 1183991.134
7 | 2578818.2279 | 1183893.2604 | 2578816.3278 | 1183891.2773 | 2578816.0911 | 1183889.0881
8 | 2578816.0911 | 1183889.0881 | 2578819.6284 | 1183885.6737 | 2578823.9645 | 1183881.4895
9 | 2578818.2279 | 1183893.2604 | 2578825.7413 | 1183899.9706
10 | 2578817.6698 | 1183873.6744 | 2578823.9645 | 1183881.4895
11 | 2578894.2669 | 1183957.0242 | 2578890.143 | 1183956.4718 | 2578885.9511 | 1183952.9248
12 | 2578894.2669 | 1183957.0242 | 2578906.2699 | 1183943.5328
13 | 2578885.9511 | 1183952.9248 | 2578878.1881 | 1183946.356
14 | 2578906.2699 | 1183943.5328 | 2578912.491 | 1183936.5403
15 | 2578868.438 | 1183938.1058 | 2578861.8051 | 1183932.1803
16 | 2578843.3127 | 1183973.4354 | 2578851.1682 | 1183962.9466 | 2578845.2891 | 1183958.2094 | 2578846.6644 | 1183956.4258 | 2578849.9165 | 1183952.2232 | 2578850.7938 | 1183947.7733 | 2578850.1447 | 1183945.5522 | 2578862.8126 | 1183942.4835 | 2578868.438 | 1183938.1058
17 | 2578868.438 | 1183938.1058 | 2578869.5192 | 1183939.0207
18 | 2578857.1586 | 1183928.0294 | 2578861.8051 | 1183932.1803
19 | 2578843.3127 | 1183973.4354 | 2578832.1699 | 1183965.2652
20 | 2578878.1881 | 1183946.356 | 2578869.5192 | 1183939.0207
21 | 2578817.6698 | 1183873.6744 | 2578821.1555 | 1183868.5928 | 2578828.9628 | 1183861.7282 | 2578845.7259 | 1183857.5443
22 | 2578845.7259 | 1183857.5443 | 2578849.649 | 1183857.7435
23 | 2578806.3063 | 1183990.4283 | 2578807.3967 | 1183991.134
24 | 2578832.1699 | 1183965.2652 | 2578825.4363 | 1183960.328
25 | 2578829.7978 | 1183903.5934 | 2578825.7413 | 1183899.9706
26 | 2578873.2974 | 1183864.0278 | 2578865.4935 | 1183860.7259
27 | 2578873.2974 | 1183864.0278 | 2578878.8132 | 1183873.9356 | 2578881.3124 | 1183878.9459
28 | 2578865.4935 | 1183860.7259 | 2578859.6439 | 1183858.2509 | 2578849.649 | 1183857.7435
29 | 2578884.3559 | 1183885.0438 | 2578883.3413 | 1183883.0132 | 2578881.3124 | 1183878.9459
30 | 2578922.5748 | 1183923.6401 | 2578918.1782 | 1183930.1479
31 | 2578922.5748 | 1183923.6401 | 2578912.7809 | 1183917.0157 | 2578905.9153 | 1183912.2875
32 | 2578918.1782 | 1183930.1479 | 2578912.491 | 1183936.5403
33 | 2578905.9153 | 1183912.2875 | 2578902.3883 | 1183909.8585
34 | 2578796.0855 | 1183938.8072 | 2578796.3699 | 1183937.1943 | 2578798.6906 | 1183937.2638 | 2578800.9884 | 1183937.3335 | 2578804.2958 | 1183937.9443
35 | 2578804.2958 | 1183937.9443 | 2578809.7696 | 1183941.8826
36 | 2578796.0855 | 1183938.8072 | 2578825.4363 | 1183960.328
37 | 2578832.7921 | 1183906.2677 | 2578829.7978 | 1183903.5934
38 | 2578886.5664 | 1183889.4678 | 2578884.3559 | 1183885.0438
39 | 2578902.3883 | 1183909.8585 | 2578901.8923 | 1183909.517 | 2578899.1626 | 1183906.9779
40 | 2578893.3779 | 1183901.597 | 2578891.9746 | 1183900.2917 | 2578891.6635 | 1183899.6689
41 | 2578890.2703 | 1183896.8806 | 2578891.6635 | 1183899.6689
42 | 2578899.1626 | 1183906.9779 | 2578893.3779 | 1183901.597
43 | 2578890.2703 | 1183896.8806 | 2578886.5664 | 1183889.4678
44 | 2578836.2026 | 1183909.3136 | 2578832.7921 | 1183906.2677
45 | 2578837.6933 | 1183910.6449 | 2578836.2026 | 1183909.3136

## bus_geodata
| x | y | coords
0 | 2578851.5934 | 1184021.9646
1 | 2578848.7359 | 1184019.972
2 | 2578822.3507 | 1184003.1252
3 | 2578798.2828 | 1184025.7238
4 | 2578815.9697 | 1183996.7557
5 | 2578816.0911 | 1183889.0881
6 | 2578818.2279 | 1183893.2604
7 | 2578823.9645 | 1183881.4895
8 | 2578894.2669 | 1183957.0242
9 | 2578885.9511 | 1183952.9248
10 | 2578906.2699 | 1183943.5328
11 | 2578868.438 | 1183938.1058
12 | 2578861.8051 | 1183932.1803
13 | 2578843.3127 | 1183973.4354
14 | 2578869.5192 | 1183939.0207
15 | 2578817.6698 | 1183873.6744
16 | 2578845.7259 | 1183857.5443
17 | 2578813.1944 | 1183999.8004
18 | 2578807.3967 | 1183991.134
19 | 2578832.1699 | 1183965.2652
20 | 2578825.7413 | 1183899.9706
21 | 2578873.2974 | 1183864.0278
22 | 2578865.4935 | 1183860.7259
23 | 2578881.3124 | 1183878.9459
24 | 2578922.5748 | 1183923.6401
25 | 2578918.1782 | 1183930.1479
26 | 2578905.9153 | 1183912.2875
27 | 2578804.2958 | 1183937.9443
28 | 2578796.0855 | 1183938.8072
29 | 2578809.7696 | 1183941.8826
30 | 2578825.4363 | 1183960.328
31 | 2578912.491 | 1183936.5403
32 | 2578849.649 | 1183857.7435
33 | 2578878.1881 | 1183946.356
34 | 2578857.1586 | 1183928.0294
35 | 2578806.3063 | 1183990.4283
36 | 2578829.7978 | 1183903.5934
37 | 2578884.3559 | 1183885.0438
38 | 2578902.3883 | 1183909.8585
39 | 2578891.6635 | 1183899.6689
40 | 2578893.3779 | 1183901.597
41 | 2578890.2703 | 1183896.8806
42 | 2578899.1626 | 1183906.9779
43 | 2578886.5664 | 1183889.4678
44 | 2578836.2026 | 1183909.3136
45 | 2578832.7921 | 1183906.2677
46 | 2578837.6933 | 1183910.6449
47 | 2578868.438 | 1183938.1058

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98967 | -0.19853 | 0.009335 | 0.0023396
1 | 0.9897 | -0.19795 | 0.0056419 | 0.001414
2 | 0.99013 | -0.18961 | 0 | 0
3 | 0.98971 | -0.19777 | 0.013873 | 0.0034769
4 | 0.99042 | -0.18395 | 0 | 0
5 | 0.98217 | -0.34376 | 0 | 0
6 | 0.98202 | -0.34677 | 0 | 0
7 | 0.98251 | -0.3371 | 0.022714 | 0.0056927
8 | 0.99598 | -0.076601 | 0 | 0
9 | 0.99662 | -0.064489 | 0.011509 | 0.0028844
10 | 0.9948 | -0.099302 | 0.0043583 | 0.0010923
11 | 0.99825 | -0.033318 | 0 | 0
12 | 0.99927 | -0.013884 | 0.0080838 | 0.002026
13 | 0.99197 | -0.1539 | 0 | 0
14 | 0.99814 | -0.035393 | 0.014717 | 0.0036883
15 | 0.98303 | -0.32688 | 0 | 0
16 | 0.9848 | -0.29251 | 0 | 0
17 | 0.99042 | -0.18401 | 0.00085081 | 0.00021323
18 | 0.99026 | -0.18702 | 0.010846 | 0.0027184
19 | 0.99099 | -0.17288 | 0.0056172 | 0.0014078
20 | 0.9817 | -0.35291 | 0.0090338 | 0.0022641
21 | 0.98687 | -0.25222 | 0 | 0
22 | 0.9861 | -0.26708 | 0.024872 | 0.0062334
23 | 0.9884 | -0.22258 | 0.016987 | 0.0042574
24 | 0.9932 | -0.12996 | 0 | 0
25 | 0.99368 | -0.12081 | 0 | 0
26 | 0.99198 | -0.15349 | 0.0083865 | 0.0021019
27 | 0.98912 | -0.20918 | 0 | 0
28 | 0.9894 | -0.20382 | 0 | 0
29 | 0.98893 | -0.21295 | 0.031324 | 0.0078506
30 | 0.99044 | -0.18354 | 0.040534 | 0.010159
31 | 0.99419 | -0.11085 | 0.01206 | 0.0030226
32 | 0.985 | -0.28853 | 0.016648 | 0.0041724
33 | 0.99732 | -0.051062 | 0.010521 | 0.0026368
34 | 1 | 0 | -0.38861 | -0.098424
35 | 0.99026 | -0.18716 | 0.0060077 | 0.0015057
36 | 0.98158 | -0.35534 | 0.0047413 | 0.0011883
37 | 0.98912 | -0.20861 | 0.0099757 | 0.0025001
38 | 0.99173 | -0.15828 | 0.0066275 | 0.001661
39 | 0.99095 | -0.17324 | 0.0086555 | 0.0021693
40 | 0.99108 | -0.17083 | 0.012662 | 0.0031733
41 | 0.99074 | -0.17731 | 0.0092893 | 0.0023281
42 | 0.99149 | -0.16297 | 0.014509 | 0.0036362
43 | 0.98969 | -0.19761 | 0.012928 | 0.00324
44 | 0.98144 | -0.35802 | 0.0036994 | 0.00092717
45 | 0.9815 | -0.35678 | 0.0050222 | 0.0012587
46 | 0.98142 | -0.35842 | 0.011204 | 0.0028081
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.009335 | -0.0023396 | 0.0093352 | 0.0023397 | 2.5735e-07 | 1.1994e-07 | 0.014036 | 0.014036 | 0.014036 | 0.98967 | -0.19853 | 0.9897 | -0.19795 | 3.8559
1 | -0.014977 | -0.0037537 | 0.014983 | 0.0037571 | 5.9529e-06 | 3.4074e-06 | 0.022518 | 0.022518 | 0.022518 | 0.9897 | -0.19795 | 0.99013 | -0.18961 | 6.1863
2 | 0.013878 | 0.0034799 | -0.013873 | -0.0034769 | 5.3964e-06 | 3.0284e-06 | 0.020858 | 0.020858 | 0.020858 | 0.99013 | -0.18961 | 0.98971 | -0.19777 | 5.7302
3 | -0.028862 | -0.007237 | 0.028869 | 0.0072419 | 7.7887e-06 | 4.8427e-06 | 0.043376 | 0.043376 | 0.043376 | 0.99013 | -0.18961 | 0.99042 | -0.18395 | 11.9164
4 | 0.00085081 | 0.00021318 | -0.00085081 | -0.00021323 | 2.5214e-09 | -5.1343e-08 | 0.0012782 | 0.0012783 | 0.0012783 | 0.99042 | -0.18395 | 0.99042 | -0.18401 | 0.35117
5 | -0.046577 | -0.011681 | 0.046644 | 0.011723 | 6.6808e-05 | 4.2288e-05 | 0.06998 | 0.06998 | 0.06998 | 0.99042 | -0.18395 | 0.99197 | -0.1539 | 19.2252
6 | 0.016857 | 0.0042255 | -0.016854 | -0.0042241 | 2.466e-06 | 1.4463e-06 | 0.025326 | 0.025326 | 0.025326 | 0.99042 | -0.18395 | 0.99026 | -0.18702 | 6.9577
7 | 0.033721 | 0.0084588 | -0.033716 | -0.0084557 | 4.8405e-06 | 3.0354e-06 | 0.051091 | 0.051091 | 0.051091 | 0.98217 | -0.34376 | 0.98202 | -0.34677 | 14.0361
8 | -0.033721 | -0.0084588 | 0.033732 | 0.0084655 | 1.0711e-05 | 6.7164e-06 | 0.051091 | 0.051091 | 0.051091 | 0.98217 | -0.34376 | 0.98251 | -0.3371 | 14.0361
9 | 0.033716 | 0.0084557 | -0.033707 | -0.0084495 | 9.8608e-06 | 6.1835e-06 | 0.051091 | 0.051091 | 0.051091 | 0.98202 | -0.34677 | 0.9817 | -0.35291 | 14.0361
10 | -0.056446 | -0.014158 | 0.056474 | 0.014176 | 2.7504e-05 | 1.7475e-05 | 0.085492 | 0.085492 | 0.085492 | 0.98251 | -0.3371 | 0.98303 | -0.32688 | 23.4869
11 | -0.21605 | -0.054797 | 0.21618 | 0.054877 | 0.00012589 | 8.019e-05 | 0.32302 | 0.32302 | 0.32302 | 0.99598 | -0.076601 | 0.99662 | -0.064489 | 29.5804
12 | 0.21605 | 0.054797 | -0.21582 | -0.054647 | 0.00023552 | 0.00015003 | 0.32302 | 0.32302 | 0.32302 | 0.99598 | -0.076601 | 0.9948 | -0.099302 | 29.5804
13 | -0.22769 | -0.057761 | 0.22784 | 0.057855 | 0.00014712 | 9.3759e-05 | 0.3402 | 0.3402 | 0.3402 | 0.99662 | -0.064489 | 0.99732 | -0.051062 | 31.154
14 | 0.21146 | 0.053555 | -0.21134 | -0.05348 | 0.00011719 | 7.4639e-05 | 0.3165 | 0.3165 | 0.3165 | 0.9948 | -0.099302 | 0.99419 | -0.11085 | 28.9834
15 | -0.37827 | -0.096007 | 0.37862 | 0.096233 | 0.000354 | 0.00022621 | 0.56428 | 0.56428 | 0.56428 | 0.99825 | -0.033318 | 0.99927 | -0.013884 | 51.6742
16 | 0.12499 | 0.031696 | -0.12427 | -0.031236 | 0.00071999 | 0.00046007 | 0.18644 | 0.18644 | 0.18644 | 0.99825 | -0.033318 | 0.99197 | -0.1539 | 51.221
17 | 0.25328 | 0.064311 | -0.25325 | -0.064295 | 2.5275e-05 | 1.6121e-05 | 0.37784 | 0.37784 | 0.37784 | 0.99825 | -0.033318 | 0.99814 | -0.035393 | 34.6005
18 | -0.38671 | -0.098259 | 0.38696 | 0.098424 | 0.00025868 | 0.00016531 | 0.57632 | 0.57632 | 0.57632 | 0.99927 | -0.013884 | 1 | 0 | 52.7765
19 | 0.077627 | 0.019513 | -0.077556 | -0.019468 | 7.0281e-05 | 4.4802e-05 | 0.11646 | 0.11646 | 0.11646 | 0.99197 | -0.1539 | 0.99099 | -0.17288 | 31.9958
20 | 0.23854 | 0.060607 | -0.23836 | -0.060492 | 0.0001798 | 0.00011463 | 0.3559 | 0.3559 | 0.3559 | 0.99814 | -0.035393 | 0.99732 | -0.051062 | 32.5915
21 | -0.056474 | -0.014176 | 0.056567 | 0.014235 | 9.2738e-05 | 5.8922e-05 | 0.085492 | 0.085492 | 0.085492 | 0.98303 | -0.32688 | 0.9848 | -0.29251 | 23.4868
22 | -0.056567 | -0.014235 | 0.056577 | 0.014241 | 1.0766e-05 | 6.8405e-06 | 0.085492 | 0.085492 | 0.085492 | 0.9848 | -0.29251 | 0.985 | -0.28853 | 23.4868
23 | 0.0060078 | 0.0015057 | -0.0060077 | -0.0015057 | 3.9695e-08 | 8.6947e-09 | 0.0090275 | 0.0090275 | 0.0090275 | 0.99026 | -0.18702 | 0.99026 | -0.18716 | 2.4801
24 | 0.071939 | 0.01806 | -0.071902 | -0.018037 | 3.6542e-05 | 2.328e-05 | 0.10803 | 0.10803 | 0.10803 | 0.99099 | -0.17288 | 0.99044 | -0.18354 | 29.6787
25 | 0.024673 | 0.0061854 | -0.02467 | -0.0061837 | 2.8526e-06 | 1.7569e-06 | 0.037398 | 0.037398 | 0.037398 | 0.9817 | -0.35291 | 0.98158 | -0.35534 | 10.2743
26 | 0.098242 | 0.02474 | -0.098172 | -0.024695 | 6.9766e-05 | 4.4542e-05 | 0.14817 | 0.14817 | 0.14817 | 0.98687 | -0.25222 | 0.9861 | -0.26708 | 40.7068
27 | -0.098242 | -0.02474 | 0.098381 | 0.024829 | 0.00013946 | 8.9038e-05 | 0.14817 | 0.14817 | 0.14817 | 0.98687 | -0.25222 | 0.9884 | -0.22258 | 40.7068
28 | 0.073301 | 0.018462 | -0.073225 | -0.018414 | 7.51e-05 | 4.7855e-05 | 0.11064 | 0.11064 | 0.11064 | 0.9861 | -0.26708 | 0.985 | -0.28853 | 30.3962
29 | -0.11537 | -0.029086 | 0.11545 | 0.029135 | 7.7151e-05 | 4.9289e-05 | 0.17375 | 0.17375 | 0.17375 | 0.9884 | -0.22258 | 0.98912 | -0.20861 | 47.7327
30 | -0.1991 | -0.050341 | 0.19919 | 0.050397 | 8.7379e-05 | 5.5618e-05 | 0.29845 | 0.29845 | 0.29845 | 0.9932 | -0.12996 | 0.99368 | -0.12081 | 27.3305
31 | 0.1991 | 0.050341 | -0.19887 | -0.050198 | 0.00022446 | 0.00014287 | 0.29845 | 0.29845 | 0.29845 | 0.9932 | -0.12996 | 0.99198 | -0.15349 | 27.3305
32 | -0.19919 | -0.050397 | 0.19928 | 0.050457 | 9.5262e-05 | 6.0635e-05 | 0.29845 | 0.29845 | 0.29845 | 0.99368 | -0.12081 | 0.99419 | -0.11085 | 27.3304
33 | 0.19049 | 0.048096 | -0.19044 | -0.048068 | 4.3746e-05 | 2.7832e-05 | 0.28587 | 0.28587 | 0.28587 | 0.99198 | -0.15349 | 0.99173 | -0.15828 | 26.1785
34 | -0.03133 | -0.0078541 | 0.031338 | 0.0078591 | 8.0155e-06 | 5.0064e-06 | 0.047133 | 0.047133 | 0.047133 | 0.98912 | -0.20918 | 0.9894 | -0.20382 | 12.9486
35 | 0.03133 | 0.0078541 | -0.031324 | -0.0078506 | 5.6177e-06 | 3.5088e-06 | 0.047133 | 0.047133 | 0.047133 | 0.98912 | -0.20918 | 0.98893 | -0.21295 | 12.9486
36 | -0.031338 | -0.0078591 | 0.031368 | 0.007878 | 3.0319e-05 | 1.8936e-05 | 0.047133 | 0.047133 | 0.047133 | 0.9894 | -0.20382 | 0.99044 | -0.18354 | 12.9486
37 | 0.019929 | 0.0049954 | -0.019927 | -0.0049946 | 1.3741e-06 | 8.2866e-07 | 0.030211 | 0.030211 | 0.030211 | 0.98158 | -0.35534 | 0.9815 | -0.35678 | 8.2997
38 | -0.12542 | -0.031636 | 0.12549 | 0.031678 | 6.6075e-05 | 4.2225e-05 | 0.18875 | 0.18875 | 0.18875 | 0.98912 | -0.20861 | 0.98969 | -0.19761 | 51.8555
39 | 0.18382 | 0.046407 | -0.18378 | -0.046381 | 4.121e-05 | 2.6207e-05 | 0.27592 | 0.27592 | 0.27592 | 0.99173 | -0.15828 | 0.99149 | -0.16297 | 25.2678
40 | -0.15652 | -0.03952 | 0.15654 | 0.039531 | 1.8057e-05 | 1.1456e-05 | 0.23514 | 0.23514 | 0.23514 | 0.99095 | -0.17324 | 0.99108 | -0.17083 | 21.533
41 | 0.14787 | 0.03735 | -0.14784 | -0.037332 | 2.884e-05 | 1.8377e-05 | 0.22214 | 0.22214 | 0.22214 | 0.99095 | -0.17324 | 0.99074 | -0.17731 | 30.5141
42 | -0.1692 | -0.042704 | 0.16927 | 0.042745 | 6.3788e-05 | 4.0519e-05 | 0.25415 | 0.25415 | 0.25415 | 0.99108 | -0.17083 | 0.99149 | -0.16297 | 23.2738
43 | 0.13855 | 0.035004 | -0.13842 | -0.034918 | 0.00013469 | 8.6095e-05 | 0.20819 | 0.20819 | 0.20819 | 0.99074 | -0.17731 | 0.98969 | -0.19761 | 57.1954
44 | -0.014904 | -0.0037354 | 0.014905 | 0.0037359 | 8.7558e-07 | 5.0258e-07 | 0.022597 | 0.022597 | 0.022597 | 0.98144 | -0.35802 | 0.9815 | -0.35678 | 6.2079
45 | 0.011205 | 0.0028082 | -0.011204 | -0.0028081 | 2.1629e-07 | 1.1317e-07 | 0.016988 | 0.016988 | 0.016988 | 0.98144 | -0.35802 | 0.98142 | -0.35842 | 4.667

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41428 | 0.10486

## res_load
| p_mw | q_mvar
0 | 0.009335 | 0.0023396
1 | 0.0056419 | 0.001414
2 | 0.013873 | 0.0034769
3 | 0.022714 | 0.0056927
4 | 0.011509 | 0.0028844
5 | 0.0043583 | 0.0010923
6 | 0.0080838 | 0.002026
7 | 0.014717 | 0.0036883
8 | 0.00085081 | 0.00021323
9 | 0.010846 | 0.0027184
10 | 0.0056172 | 0.0014078
11 | 0.0090338 | 0.0022641
12 | 0.024872 | 0.0062334
13 | 0.016987 | 0.0042574
14 | 0.0083865 | 0.0021019
15 | 0.031324 | 0.0078506
16 | 0.040534 | 0.010159
17 | 0.01206 | 0.0030226
18 | 0.016648 | 0.0041724
19 | 0.010521 | 0.0026368
20 | 0.025667 | 0.0064329
21 | 0.0060077 | 0.0015057
22 | 0.0047413 | 0.0011883
23 | 0.0099757 | 0.0025001
24 | 0.0066275 | 0.001661
25 | 0.0086555 | 0.0021693
26 | 0.012662 | 0.0031733
27 | 0.0092893 | 0.0023281
28 | 0.014509 | 0.0036362
29 | 0.012928 | 0.00324
30 | 0.0036994 | 0.00092717
31 | 0.0050222 | 0.0012587
32 | 0.011204 | 0.0028081

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1