## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-35_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-35_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-35_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-35_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-35_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2196-35_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2196-35_0_3_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_2196-35_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_2196-35_0_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_2196-35_0_3_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_2196-35_0_3_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_2196-35_0_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_2196-35_0_3_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_2196-35_0_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2196-35_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2196-35_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2196-35_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2196-35_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2196-35_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2196-35_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2196-35_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2196-35_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2196-35_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2196-35_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_2196-35_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_2196-35_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_2196-35_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2196-35_0_3_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_2196-35_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_2196-35_0_3_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2196-35_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_2196-35_0_3_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_2196-35_0_3_node_32 | 0.4 | n |  | TRUE
33 | bus_MV_507_0_node_44 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-35_0_3_load_0 | 0 | 0.031669 | 0.0079371 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-35_0_3_load_15 | 6 | 0.014715 | 0.003688 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-35_0_3_load_17 | 7 | 0.023656 | 0.0059287 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-35_0_3_load_19 | 9 | 0.08894 | 0.022291 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-35_0_3_load_33 | 11 | 0.018532 | 0.0046446 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-35_0_3_load_18 | 13 | 0.0428 | 0.010727 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-35_0_3_load_6 | 14 | 0.013294 | 0.0033318 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-35_0_3_load_7 | 15 | 0.0056055 | 0.0014049 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-35_0_3_load_10 | 18 | 0.0039005 | 0.00097755 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-35_0_3_load_12 | 20 | 0.017598 | 0.0044104 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-35_0_3_load_13 | 21 | 0.001235 | 0.00030952 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-35_0_3_load_20 | 22 | 0.049706 | 0.012457 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-35_0_3_load_28 | 25 | 0.015195 | 0.0038083 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-35_0_3_load_31 | 28 | 0.01928 | 0.004832 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-35_0_3_load_29 | 30 | 0.01609 | 0.0040325 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-35_0_3_load_34 | 31 | 0.047573 | 0.011923 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-35_0_3_load_32 | 32 | 0.01112 | 0.002787 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-35_0_3_line_0 |  | 0 | 1 | 0.030699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-35_0_3_line_1 |  | 0 | 2 | 0.024566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-35_0_3_line_2 |  | 1 | 3 | 0.026621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-35_0_3_line_3 |  | 2 | 4 | 0.035899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-35_0_3_line_4 |  | 3 | 5 | 0.052311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-35_0_3_line_5 |  | 3 | 6 | 0.028653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-35_0_3_line_6 |  | 4 | 7 | 0.035648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-35_0_3_line_7 |  | 5 | 8 | 0.042545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2196-35_0_3_line_8 |  | 5 | 9 | 0.071491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2196-35_0_3_line_9 |  | 8 | 10 | 0.047565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-35_0_3_line_10 |  | 8 | 11 | 0.018089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-35_0_3_line_11 |  | 8 | 12 | 0.17907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2196-35_0_3_line_12 |  | 9 | 13 | 0.0082683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-35_0_3_line_13 |  | 10 | 31 | 0.024236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-35_0_3_line_14 |  | 12 | 22 | 0.017311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2196-35_0_3_line_15 |  | 13 | 19 | 0.16118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-35_0_3_line_16 |  | 14 | 15 | 0.00092901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-35_0_3_line_17 |  | 14 | 16 | 0.025534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-35_0_3_line_18 |  | 15 | 17 | 0.016667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2196-35_0_3_line_19 |  | 16 | 18 | 0.0057518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-35_0_3_line_20 |  | 16 | 19 | 0.11032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-35_0_3_line_21 |  | 17 | 20 | 0.0029891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-35_0_3_line_22 |  | 20 | 21 | 0.017199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-35_0_3_line_23 |  | 22 | 23 | 0.075267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-35_0_3_line_24 |  | 23 | 24 | 0.016071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-35_0_3_line_25 |  | 23 | 25 | 0.008572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-35_0_3_line_26 |  | 24 | 32 | 0.041347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-35_0_3_line_27 |  | 24 | 28 | 0.039331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-35_0_3_line_28 |  | 26 | 27 | 0.033631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-35_0_3_line_29 |  | 26 | 28 | 0.012934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-35_0_3_line_30 |  | 27 | 29 | 0.008143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-35_0_3_line_31 |  | 29 | 30 | 0.011258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-35_0_3_trafo_19 | 0.63 MVA 20/0.4 kV | 33 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2578198.4354 | 1184712.8199 | 2578198.4963 | 1184682.121
1 | 2578200.2048 | 1184658.196 | 2578198.5401 | 1184660.0364 | 2578198.4963 | 1184682.121
2 | 2578185.3394 | 1184736.0132 | 2578198.4354 | 1184712.8199
3 | 2578200.2048 | 1184658.196 | 2578202.1129 | 1184656.0991 | 2578215.5229 | 1184656.1501 | 2578218.7888 | 1184662.2192 | 2578230.2396 | 1184656.5855
4 | 2578144.1216 | 1184703.6583 | 2578185.3394 | 1184736.0132
5 | 2578185.3394 | 1184736.0132 | 2578204.5747 | 1184757.2502
6 | 2578230.2396 | 1184656.5855 | 2578240.9143 | 1184660.004 | 2578251.0828 | 1184669.0049 | 2578255.0726 | 1184679.1051
7 | 2578144.1216 | 1184703.6583 | 2578110.406 | 1184677.5905
8 | 2578144.1216 | 1184703.6583 | 2578135.2189 | 1184727.6701 | 2578128.3826 | 1184757.3773 | 2578130.4382 | 1184772.638
9 | 2578077.4944 | 1184685.5154 | 2578093.6592 | 1184664.6451 | 2578110.406 | 1184677.5905
10 | 2578110.406 | 1184677.5905 | 2578113.1222 | 1184673.1671 | 2578116.6813 | 1184660.7695
11 | 2578000.7837 | 1184689.9 | 2578000.2729 | 1184679.6854 | 2577995.1357 | 1184665.019 | 2578003.6455 | 1184640.1413 | 2578007.1992 | 1184629.0001 | 2578017.4898 | 1184631.6858 | 2578033.7343 | 1184636.6175 | 2578051.3254 | 1184642.478 | 2578075.099 | 1184652.5848 | 2578087.942 | 1184660.3194 | 2578093.6592 | 1184664.6451 | 2578110.406 | 1184677.5905
12 | 2578130.4382 | 1184772.638 | 2578131.2698 | 1184778.8112 | 2578131.6941 | 1184780.8058
13 | 2578077.4944 | 1184685.5154 | 2578081.3407 | 1184689.5589 | 2578081.0658 | 1184708.2141
14 | 2578000.7837 | 1184689.9 | 2578002.5496 | 1184707.1211
15 | 2578074.5758 | 1184856.9934 | 2578124.3503 | 1184869.0615 | 2578139.6151 | 1184871.3734 | 2578144.1779 | 1184868.9777 | 2578142.8332 | 1184833.1639 | 2578131.6941 | 1184780.8058
16 | 2578042.9401 | 1184984.0931 | 2578042.6695 | 1184984.9818
17 | 2578049.9676 | 1184959.971 | 2578050.5 | 1184963.6265 | 2578045.266 | 1184976.4525 | 2578042.9401 | 1184984.0931
18 | 2578037.8158 | 1185000.926 | 2578042.6695 | 1184984.9818
19 | 2578049.9676 | 1184959.971 | 2578048.2479 | 1184959.2881 | 2578044.3477 | 1184959.1913
20 | 2578074.5758 | 1184856.9934 | 2578080.1966 | 1184870.4242 | 2578080.8978 | 1184876.4137 | 2578080.0217 | 1184883.0648 | 2578075.6047 | 1184900.2011 | 2578057.6114 | 1184948.6815 | 2578049.9676 | 1184959.971
21 | 2578037.8158 | 1185000.926 | 2578040.7666 | 1185001.403
22 | 2578040.7666 | 1185001.403 | 2578057.7452 | 1185004.1476
23 | 2578033.7286 | 1184763.5727 | 2578024.5895 | 1184762.6392 | 2578014.128 | 1184759.0758 | 2578007.141 | 1184751.8978 | 2578002.5496 | 1184707.1211
24 | 2578033.7286 | 1184763.5727 | 2578029.6111 | 1184779.107
25 | 2578033.7286 | 1184763.5727 | 2578042.2799 | 1184764.4528
26 | 2578029.6111 | 1184779.107 | 2578022.3169 | 1184806.6038 | 2578018.99 | 1184806.7828 | 2578019.0252 | 1184816.3502
27 | 2578029.6111 | 1184779.107 | 2577990.2815 | 1184779.478
28 | 2577977.3482 | 1184779.6 | 2577977.0342 | 1184789.6397 | 2577964.5924 | 1184789.2521 | 2577954.4517 | 1184794.0031
29 | 2577977.3482 | 1184779.6 | 2577990.2815 | 1184779.478
30 | 2577954.4517 | 1184794.0031 | 2577950.6624 | 1184786.7911
31 | 2577950.6624 | 1184786.7911 | 2577945.3958 | 1184788.7561 | 2577940.5676 | 1184787.4621 | 2577940.0351 | 1184787.1094

## bus_geodata
| x | y | coords
0 | 2578198.4963 | 1184682.121
1 | 2578198.4354 | 1184712.8199
2 | 2578200.2048 | 1184658.196
3 | 2578185.3394 | 1184736.0132
4 | 2578230.2396 | 1184656.5855
5 | 2578144.1216 | 1184703.6583
6 | 2578204.5747 | 1184757.2502
7 | 2578255.0726 | 1184679.1051
8 | 2578110.406 | 1184677.5905
9 | 2578130.4382 | 1184772.638
10 | 2578077.4944 | 1184685.5154
11 | 2578116.6813 | 1184660.7695
12 | 2578000.7837 | 1184689.9
13 | 2578131.6941 | 1184780.8058
14 | 2578042.9401 | 1184984.0931
15 | 2578042.6695 | 1184984.9818
16 | 2578049.9676 | 1184959.971
17 | 2578037.8158 | 1185000.926
18 | 2578044.3477 | 1184959.1913
19 | 2578074.5758 | 1184856.9934
20 | 2578040.7666 | 1185001.403
21 | 2578057.7452 | 1185004.1476
22 | 2578002.5496 | 1184707.1211
23 | 2578033.7286 | 1184763.5727
24 | 2578029.6111 | 1184779.107
25 | 2578042.2799 | 1184764.4528
26 | 2577977.3482 | 1184779.6
27 | 2577954.4517 | 1184794.0031
28 | 2577990.2815 | 1184779.478
29 | 2577950.6624 | 1184786.7911
30 | 2577940.0351 | 1184787.1094
31 | 2578081.0658 | 1184708.2141
32 | 2578019.0252 | 1184816.3502
33 | 2578144.1216 | 1184703.6583

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98551 | -0.27741 | 0.031669 | 0.0079371
1 | 0.98708 | -0.24698 | 0 | 0
2 | 0.98498 | -0.28785 | 0 | 0
3 | 0.98843 | -0.22066 | 0 | 0
4 | 0.9842 | -0.30312 | 0 | 0
5 | 0.99181 | -0.15552 | 0 | 0
6 | 0.98805 | -0.22819 | 0.014715 | 0.003688
7 | 0.98342 | -0.3183 | 0.023656 | 0.0059287
8 | 0.98831 | -0.22267 | 0 | 0
9 | 1 | 0 | -0.33855 | -0.086338
10 | 0.98622 | -0.26313 | 0 | 0
11 | 0.988 | -0.22865 | 0.018532 | 0.0046446
12 | 0.97902 | -0.40235 | 0 | 0
13 | 0.99936 | -0.012177 | 0.0428 | 0.010727
14 | 0.9881 | -0.22873 | 0.013294 | 0.0033318
15 | 0.98808 | -0.22913 | 0.0056055 | 0.0014049
16 | 0.98898 | -0.21154 | 0 | 0
17 | 0.98779 | -0.23474 | 0 | 0
18 | 0.98896 | -0.21194 | 0.0039005 | 0.00097755
19 | 0.9932 | -0.13003 | 0 | 0
20 | 0.98774 | -0.23574 | 0.017598 | 0.0044104
21 | 0.98772 | -0.23612 | 0.001235 | 0.00030952
22 | 0.97813 | -0.4199 | 0.049706 | 0.012457
23 | 0.97379 | -0.50486 | 0 | 0
24 | 0.9731 | -0.51861 | 0 | 0
25 | 0.97367 | -0.50726 | 0.015195 | 0.0038083
26 | 0.9716 | -0.54809 | 0 | 0
27 | 0.9711 | -0.55809 | 0 | 0
28 | 0.9718 | -0.54425 | 0.01928 | 0.004832
29 | 0.97098 | -0.56051 | 0 | 0
30 | 0.97081 | -0.56386 | 0.01609 | 0.0040325
31 | 0.98516 | -0.28381 | 0.047573 | 0.011923
32 | 0.97267 | -0.52707 | 0.01112 | 0.002787
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.055371 | -0.013894 | 0.055452 | 0.013945 | 8.0478e-05 | 5.1114e-05 | 0.083611 | 0.08361 | 0.083611 | 0.98551 | -0.27741 | 0.98708 | -0.24698 | 22.9699
1 | 0.023702 | 0.0059571 | -0.02369 | -0.0059498 | 1.1803e-05 | 7.2408e-06 | 0.035793 | 0.035794 | 0.035794 | 0.98551 | -0.27741 | 0.98498 | -0.28785 | 9.8334
2 | -0.055452 | -0.013945 | 0.055522 | 0.01399 | 6.9787e-05 | 4.4323e-05 | 0.08361 | 0.08361 | 0.08361 | 0.98708 | -0.24698 | 0.98843 | -0.22066 | 22.9699
3 | 0.02369 | 0.0059498 | -0.023673 | -0.0059392 | 1.7247e-05 | 1.0582e-05 | 0.035794 | 0.035794 | 0.035794 | 0.98498 | -0.28785 | 0.9842 | -0.30312 | 9.8334
4 | -0.070242 | -0.017681 | 0.070462 | 0.01782 | 0.00021946 | 0.00013978 | 0.10577 | 0.10577 | 0.10577 | 0.98843 | -0.22066 | 0.99181 | -0.15552 | 29.0581
5 | 0.014721 | 0.003691 | -0.014715 | -0.003688 | 5.2771e-06 | 3.0102e-06 | 0.022161 | 0.022161 | 0.022161 | 0.98843 | -0.22066 | 0.98805 | -0.22819 | 6.0883
6 | 0.023673 | 0.0059392 | -0.023656 | -0.0059287 | 1.7127e-05 | 1.0509e-05 | 0.035794 | 0.035794 | 0.035794 | 0.9842 | -0.30312 | 0.98342 | -0.3183 | 9.8335
7 | 0.17963 | 0.045842 | -0.17905 | -0.045471 | 0.00058066 | 0.00037053 | 0.2698 | 0.2698 | 0.2698 | 0.99181 | -0.15552 | 0.98831 | -0.22267 | 37.06
8 | -0.25009 | -0.063662 | 0.25198 | 0.06487 | 0.0018907 | 0.0012082 | 0.37557 | 0.37557 | 0.37557 | 0.99181 | -0.15552 | 1 | 0 | 51.589
9 | 0.047712 | 0.012011 | -0.047619 | -0.011953 | 9.2094e-05 | 5.8332e-05 | 0.071854 | 0.071855 | 0.071855 | 0.98831 | -0.22267 | 0.98622 | -0.26313 | 19.7403
10 | 0.018538 | 0.0046478 | -0.018532 | -0.0046446 | 5.2846e-06 | 3.1504e-06 | 0.027911 | 0.027911 | 0.027911 | 0.98831 | -0.22267 | 0.988 | -0.22865 | 7.668
11 | 0.1128 | 0.028812 | -0.11183 | -0.028196 | 0.0009707 | 0.0006167 | 0.17003 | 0.17003 | 0.17003 | 0.98831 | -0.22267 | 0.97902 | -0.40235 | 23.3562
12 | 0.08492 | 0.021468 | -0.084871 | -0.021437 | 4.956e-05 | 3.161e-05 | 0.12643 | 0.12643 | 0.12643 | 1 | 0 | 0.99936 | -0.012177 | 34.733
13 | 0.047619 | 0.011953 | -0.047573 | -0.011923 | 4.6925e-05 | 2.9723e-05 | 0.071855 | 0.071855 | 0.071855 | 0.98622 | -0.26313 | 0.98516 | -0.28381 | 19.7403
14 | 0.11183 | 0.028196 | -0.11174 | -0.028136 | 9.3843e-05 | 5.9624e-05 | 0.17003 | 0.17003 | 0.17003 | 0.97902 | -0.40235 | 0.97813 | -0.4199 | 23.3562
15 | 0.042071 | 0.01071 | -0.041833 | -0.01056 | 0.00023762 | 0.00014998 | 0.0627 | 0.062701 | 0.062701 | 0.99936 | -0.012177 | 0.9932 | -0.13003 | 17.2256
16 | 0.024445 | 0.0061285 | -0.024444 | -0.0061282 | 4.7212e-07 | 2.9026e-07 | 0.036813 | 0.036813 | 0.036813 | 0.9881 | -0.22873 | 0.98808 | -0.22913 | 10.1135
17 | -0.037739 | -0.0094603 | 0.03777 | 0.0094797 | 3.0928e-05 | 1.9466e-05 | 0.056833 | 0.056833 | 0.056833 | 0.9881 | -0.22873 | 0.98898 | -0.21154 | 15.6135
18 | 0.018839 | 0.0047233 | -0.018834 | -0.0047203 | 5.0308e-06 | 3.0063e-06 | 0.028371 | 0.028371 | 0.028371 | 0.98808 | -0.22913 | 0.98779 | -0.23474 | 7.7943
19 | 0.0039005 | 0.00097752 | -0.0039005 | -0.00097755 | 7.4288e-08 | -2.626e-08 | 0.0058687 | 0.0058687 | 0.0058687 | 0.98898 | -0.21154 | 0.98896 | -0.21194 | 1.6123
20 | -0.04167 | -0.010457 | 0.041833 | 0.01056 | 0.00016265 | 0.00010267 | 0.062702 | 0.062701 | 0.062702 | 0.98898 | -0.21154 | 0.9932 | -0.13003 | 17.2257
21 | 0.018834 | 0.0047203 | -0.018833 | -0.0047198 | 9.0226e-07 | 5.3919e-07 | 0.028371 | 0.028371 | 0.028371 | 0.98779 | -0.23474 | 0.98774 | -0.23574 | 7.7943
22 | 0.001235 | 0.00030932 | -0.001235 | -0.00030952 | 2.2326e-08 | -2.0585e-07 | 0.0018605 | 0.0018606 | 0.0018606 | 0.98774 | -0.23574 | 0.98772 | -0.23612 | 0.51114
23 | 0.062032 | 0.015679 | -0.06178 | -0.015519 | 0.00025161 | 0.00016009 | 0.094417 | 0.094417 | 0.094417 | 0.97813 | -0.4199 | 0.97379 | -0.50486 | 25.9387
24 | 0.046583 | 0.011709 | -0.046553 | -0.01169 | 3.0547e-05 | 1.935e-05 | 0.071195 | 0.071195 | 0.071195 | 0.97379 | -0.50486 | 0.9731 | -0.51861 | 19.559
25 | 0.015197 | 0.0038093 | -0.015195 | -0.0038083 | 1.7335e-06 | 1.0028e-06 | 0.023222 | 0.023222 | 0.023222 | 0.97379 | -0.50486 | 0.97367 | -0.50726 | 6.3798
26 | 0.011125 | 0.0027894 | -0.01112 | -0.002787 | 4.4874e-06 | 2.3585e-06 | 0.017012 | 0.017012 | 0.017012 | 0.9731 | -0.51861 | 0.97267 | -0.52707 | 4.6737
27 | 0.035428 | 0.0089005 | -0.035385 | -0.0088733 | 4.33e-05 | 2.7224e-05 | 0.054183 | 0.054183 | 0.054183 | 0.9731 | -0.51861 | 0.9718 | -0.54425 | 14.8854
28 | 0.016102 | 0.0040396 | -0.016094 | -0.0040351 | 7.6703e-06 | 4.4927e-06 | 0.024662 | 0.024662 | 0.024662 | 0.9716 | -0.54809 | 0.9711 | -0.55809 | 6.7752
29 | -0.016102 | -0.0040396 | 0.016105 | 0.0040413 | 2.9498e-06 | 1.7277e-06 | 0.024662 | 0.024661 | 0.024662 | 0.9716 | -0.54809 | 0.9718 | -0.54425 | 6.7751
30 | 0.016094 | 0.0040351 | -0.016092 | -0.004034 | 1.8572e-06 | 1.0879e-06 | 0.024662 | 0.024662 | 0.024662 | 0.9711 | -0.55809 | 0.97098 | -0.56051 | 6.7752
31 | 0.016092 | 0.004034 | -0.01609 | -0.0040325 | 2.5678e-06 | 1.5042e-06 | 0.024662 | 0.024662 | 0.024662 | 0.97098 | -0.56051 | 0.97081 | -0.56386 | 6.7752

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42749 | 0.10863

## res_load
| p_mw | q_mvar
0 | 0.031669 | 0.0079371
1 | 0.014715 | 0.003688
2 | 0.023656 | 0.0059287
3 | 0.08894 | 0.022291
4 | 0.018532 | 0.0046446
5 | 0.0428 | 0.010727
6 | 0.013294 | 0.0033318
7 | 0.0056055 | 0.0014049
8 | 0.0039005 | 0.00097755
9 | 0.017598 | 0.0044104
10 | 0.001235 | 0.00030952
11 | 0.049706 | 0.012457
12 | 0.015195 | 0.0038083
13 | 0.01928 | 0.004832
14 | 0.01609 | 0.0040325
15 | 0.047573 | 0.011923
16 | 0.01112 | 0.002787

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1