## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-39_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-39_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-39_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-39_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-39_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2196-39_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2196-39_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_2196-39_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2196-39_0_4_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_2196-39_0_4_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_2196-39_0_4_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_2196-39_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2196-39_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2196-39_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2196-39_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2196-39_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2196-39_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2196-39_0_4_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_2196-39_0_4_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_2196-39_0_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_2196-39_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2196-39_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2196-39_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2196-39_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_2196-39_0_4_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_2196-39_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_2196-39_0_4_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2196-39_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2196-39_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2196-39_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2196-39_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2196-39_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_2196-39_0_4_node_34 | 0.4 | n |  | TRUE
33 | bus_MV_508_0_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-39_0_4_load_0 | 0 | 0.0072004 | 0.0018046 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-39_0_4_load_1 | 1 | 0.003015 | 0.00075562 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-39_0_4_load_4 | 4 | 0.00045304 | 0.00011354 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-39_0_4_load_9 | 5 | 0.0013872 | 0.00034767 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-39_0_4_load_10 | 6 | 0.00059954 | 0.00015026 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-39_0_4_load_8 | 7 | 0.00039761 | 9.9651e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-39_0_4_load_14 | 10 | 0.00054728 | 0.00013716 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-39_0_4_load_6 | 12 | 0.0062171 | 0.0015581 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-39_0_4_load_11 | 14 | 0.0053676 | 0.0013452 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-39_0_4_load_15 | 15 | 0.0093125 | 0.0023339 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-39_0_4_load_12 | 16 | 0.0032948 | 0.00082577 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-39_0_4_load_33 | 17 | 0.042368 | 0.010618 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-39_0_4_load_32 | 18 | 0.011089 | 0.0027792 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-39_0_4_load_18 | 20 | 0.021026 | 0.0052695 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-39_0_4_load_13 | 21 | 0.0031964 | 0.00080109 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-39_0_4_load_20 | 22 | 0.078727 | 0.019731 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-39_0_4_load_22 | 23 | 0.07839 | 0.019646 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-39_0_4_load_30 | 24 | 0.074586 | 0.018693 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-39_0_4_load_19 | 27 | 0.0082013 | 0.0020554 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-39_0_4_load_21 | 28 | 0.012266 | 0.0030741 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-39_0_4_load_26 | 30 | 0.012448 | 0.0031198 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-39_0_4_load_34 | 32 | 0.02802 | 0.0070226 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-39_0_4_line_0 |  | 0 | 1 | 0.025372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-39_0_4_line_1 |  | 0 | 2 | 0.0092439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-39_0_4_line_2 |  | 2 | 3 | 0.083069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-39_0_4_line_3 |  | 2 | 4 | 0.029518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-39_0_4_line_4 |  | 3 | 5 | 0.04394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-39_0_4_line_5 |  | 4 | 6 | 0.012559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-39_0_4_line_6 |  | 5 | 9 | 0.0075557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-39_0_4_line_7 |  | 6 | 10 | 0.016647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-39_0_4_line_8 |  | 7 | 8 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-39_0_4_line_9 |  | 8 | 9 | 0.026661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-39_0_4_line_10 |  | 10 | 20 | 0.16362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-39_0_4_line_11 |  | 10 | 21 | 0.049612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-39_0_4_line_12 |  | 11 | 12 | 0.098558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-39_0_4_line_13 |  | 11 | 13 | 0.060667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-39_0_4_line_14 |  | 12 | 14 | 0.029804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-39_0_4_line_15 |  | 13 | 15 | 0.089188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-39_0_4_line_16 |  | 14 | 16 | 0.0010601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-39_0_4_line_17 |  | 16 | 21 | 0.039106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-39_0_4_line_18 |  | 17 | 18 | 0.01696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2196-39_0_4_line_19 |  | 17 | 19 | 0.020104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-39_0_4_line_20 |  | 18 | 26 | 0.016072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-39_0_4_line_21 |  | 19 | 31 | 0.043421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-39_0_4_line_22 |  | 19 | 29 | 0.03199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-39_0_4_line_23 |  | 20 | 22 | 0.017681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-39_0_4_line_24 |  | 22 | 23 | 0.0096707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2196-39_0_4_line_25 |  | 23 | 24 | 0.042359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2196-39_0_4_line_26 |  | 24 | 25 | 0.010773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-39_0_4_line_27 |  | 25 | 26 | 0.021968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-39_0_4_line_28 |  | 27 | 28 | 0.017961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-39_0_4_line_29 |  | 28 | 29 | 0.026526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-39_0_4_line_30 |  | 29 | 30 | 0.02432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-39_0_4_line_31 |  | 31 | 32 | 0.012206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-39_0_4_trafo_22 | 0.63 MVA 20/0.4 kV | 33 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2578498.8899 | 1183403.0345 | 2578497.713 | 1183416.0139 | 2578498.9478 | 1183428.2909
1 | 2578499.7247 | 1183393.8284 | 2578498.8899 | 1183403.0345
2 | 2578499.7247 | 1183393.8284 | 2578500.2813 | 1183383.0541 | 2578505.793 | 1183321.6245 | 2578506.7551 | 1183311.0823
3 | 2578499.7247 | 1183393.8284 | 2578485.3887 | 1183381.2402 | 2578476.9252 | 1183375.1281
4 | 2578506.7551 | 1183311.0823 | 2578510.0407 | 1183267.2649
5 | 2578476.9252 | 1183375.1281 | 2578472.8287 | 1183372.1696 | 2578465.5019 | 1183370.5397 | 2578465.5019 | 1183370.5397
6 | 2578510.6085 | 1183259.7306 | 2578510.4772 | 1183261.443 | 2578510.0407 | 1183267.2649
7 | 2578450.4045 | 1183377.5534 | 2578465.5019 | 1183370.5397
8 | 2578484.8287 | 1183264.0924 | 2578482.9179 | 1183271.9145 | 2578483.0548 | 1183279.4257
9 | 2578510.6085 | 1183259.7306 | 2578503.395 | 1183262.0466 | 2578498.1132 | 1183264.4336 | 2578484.8287 | 1183264.0924
10 | 2578450.4045 | 1183377.5534 | 2578305.4584 | 1183301.639
11 | 2578450.4045 | 1183377.5534 | 2578434.1535 | 1183388.5511 | 2578428.5197 | 1183394.8748 | 2578428.054 | 1183403.3253 | 2578432.0544 | 1183407.6242 | 2578438.0005 | 1183411.656
12 | 2578539.924 | 1183537.9142 | 2578535.2027 | 1183536.8974 | 2578530.2372 | 1183527.4103 | 2578501.4661 | 1183483.0241 | 2578494.3094 | 1183460.7939 | 2578491.6477 | 1183454.5672
13 | 2578510.9072 | 1183567.2673 | 2578514.1742 | 1183562.9755 | 2578519.6829 | 1183568.5697 | 2578524.1826 | 1183565.274 | 2578545.6267 | 1183555.0026 | 2578543.6504 | 1183550.9632 | 2578539.924 | 1183537.9142
14 | 2578471.4378 | 1183433.9106 | 2578475.0144 | 1183436.284 | 2578485.8119 | 1183443.56 | 2578489.5362 | 1183449.6275 | 2578491.6477 | 1183454.5672
15 | 2578510.9072 | 1183567.2673 | 2578496.7199 | 1183549.2423 | 2578478.029 | 1183520.706 | 2578463.3006 | 1183492.1426
16 | 2578471.4378 | 1183433.9106 | 2578470.5545 | 1183433.3244
17 | 2578438.0005 | 1183411.656 | 2578442.5079 | 1183414.7123 | 2578470.5545 | 1183433.3244
18 | 2578216.7922 | 1183241.7641 | 2578214.9054 | 1183247.6963 | 2578211.7175 | 1183257.9473
19 | 2578216.7922 | 1183241.7641 | 2578222.8677 | 1183222.5987
20 | 2578206.945 | 1183273.2943 | 2578211.7175 | 1183257.9473
21 | 2578226.0345 | 1183186.6795 | 2578225.6796 | 1183187.748 | 2578220.8164 | 1183202.3067 | 2578218.4771 | 1183209.7858 | 2578226.2035 | 1183212.0588 | 2578222.8677 | 1183222.5987
22 | 2578246.2875 | 1183217.9664 | 2578226.2035 | 1183212.0588 | 2578222.8677 | 1183222.5987
23 | 2578288.4702 | 1183296.7383 | 2578305.4584 | 1183301.639 | 2578305.4584 | 1183301.639
24 | 2578288.4702 | 1183296.7383 | 2578279.1784 | 1183294.0578
25 | 2578238.4791 | 1183282.3171 | 2578279.1784 | 1183294.0578
26 | 2578228.1285 | 1183279.3312 | 2578238.4791 | 1183282.3171
27 | 2578228.1285 | 1183279.3312 | 2578206.945 | 1183273.2943
28 | 2578271.7892 | 1183225.2665 | 2578289.0563 | 1183230.2093
29 | 2578246.2875 | 1183217.9664 | 2578271.7892 | 1183225.2665
30 | 2578246.2875 | 1183217.9664 | 2578239.3865 | 1183241.287
31 | 2578226.0345 | 1183186.6795 | 2578214.3638 | 1183183.1062

## bus_geodata
| x | y | coords
0 | 2578498.8899 | 1183403.0345
1 | 2578498.9478 | 1183428.2909
2 | 2578499.7247 | 1183393.8284
3 | 2578506.7551 | 1183311.0823
4 | 2578476.9252 | 1183375.1281
5 | 2578510.0407 | 1183267.2649
6 | 2578465.5019 | 1183370.5397
7 | 2578483.0548 | 1183279.4257
8 | 2578484.8287 | 1183264.0924
9 | 2578510.6085 | 1183259.7306
10 | 2578450.4045 | 1183377.5534
11 | 2578539.924 | 1183537.9142
12 | 2578491.6477 | 1183454.5672
13 | 2578510.9072 | 1183567.2673
14 | 2578471.4378 | 1183433.9106
15 | 2578463.3006 | 1183492.1426
16 | 2578470.5545 | 1183433.3244
17 | 2578216.7922 | 1183241.7641
18 | 2578211.7175 | 1183257.9473
19 | 2578222.8677 | 1183222.5987
20 | 2578305.4584 | 1183301.639
21 | 2578438.0005 | 1183411.656
22 | 2578288.4702 | 1183296.7383
23 | 2578279.1784 | 1183294.0578
24 | 2578238.4791 | 1183282.3171
25 | 2578228.1285 | 1183279.3312
26 | 2578206.945 | 1183273.2943
27 | 2578289.0563 | 1183230.2093
28 | 2578271.7892 | 1183225.2665
29 | 2578246.2875 | 1183217.9664
30 | 2578239.3865 | 1183241.287
31 | 2578226.0345 | 1183186.6795
32 | 2578214.3638 | 1183183.1062
33 | 2578228.1285 | 1183279.3312

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99148 | -0.16368 | 0.0072004 | 0.0018046
1 | 0.99141 | -0.16503 | 0.003015 | 0.00075562
2 | 0.99157 | -0.162 | 0 | 0
3 | 0.99143 | -0.16464 | 0 | 0
4 | 0.99189 | -0.15572 | 0.00045304 | 0.00011354
5 | 0.99136 | -0.16603 | 0.0013872 | 0.00034767
6 | 0.99204 | -0.15295 | 0.00059954 | 0.00015026
7 | 0.99134 | -0.16638 | 0.00039761 | 9.9651e-05
8 | 0.99135 | -0.16627 | 0 | 0
9 | 0.99136 | -0.16609 | 0 | 0
10 | 0.99223 | -0.1491 | 0.00054728 | 0.00013716
11 | 0.98883 | -0.215 | 0 | 0
12 | 0.98968 | -0.19864 | 0.0062171 | 0.0015581
13 | 0.98832 | -0.22508 | 0 | 0
14 | 0.9901 | -0.1904 | 0.0053676 | 0.0013452
15 | 0.98755 | -0.23991 | 0.0093125 | 0.0023339
16 | 0.99012 | -0.19001 | 0.0032948 | 0.00082577
17 | 0.98961 | -0.19971 | 0.042368 | 0.010618
18 | 0.99121 | -0.16857 | 0.011089 | 0.0027792
19 | 0.98848 | -0.22153 | 0 | 0
20 | 0.99838 | -0.031033 | 0.021026 | 0.0052695
21 | 0.99099 | -0.1732 | 0.0031964 | 0.00080109
22 | 0.99938 | -0.011871 | 0.078727 | 0.019731
23 | 1 | 0 | -0.3333 | -0.083859
24 | 0.99634 | -0.07002 | 0.074586 | 0.018693
25 | 0.99521 | -0.091683 | 0 | 0
26 | 0.9929 | -0.13601 | 0 | 0
27 | 0.98688 | -0.25268 | 0.0082013 | 0.0020554
28 | 0.98701 | -0.25005 | 0.012266 | 0.0030741
29 | 0.98751 | -0.24034 | 0 | 0
30 | 0.98723 | -0.24575 | 0.012448 | 0.0031198
31 | 0.98736 | -0.24326 | 0 | 0
32 | 0.98705 | -0.24938 | 0.02802 | 0.0070226
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0030151 | 0.00075542 | -0.003015 | -0.00075562 | 1.9482e-07 | -2.025e-07 | 0.004525 | 0.0045252 | 0.0045252 | 0.99148 | -0.16368 | 0.99141 | -0.16503 | 1.2432
1 | -0.010216 | -0.00256 | 0.010216 | 0.0025604 | 8.148e-07 | 4.0225e-07 | 0.015331 | 0.015331 | 0.015331 | 0.99148 | -0.16368 | 0.99157 | -0.162 | 4.2119
2 | 0.0017852 | 0.00044527 | -0.001785 | -0.0004462 | 2.2347e-07 | -9.2834e-07 | 0.0026782 | 0.0026786 | 0.0026786 | 0.99157 | -0.162 | 0.99143 | -0.16464 | 0.73588
3 | -0.012002 | -0.0030057 | 0.012005 | 0.0030076 | 3.5903e-06 | 1.9169e-06 | 0.01801 | 0.018009 | 0.01801 | 0.99157 | -0.162 | 0.99189 | -0.15572 | 4.9477
4 | 0.001785 | 0.0004462 | -0.0017849 | -0.00044669 | 1.1823e-07 | -4.9092e-07 | 0.0026786 | 0.0026788 | 0.0026788 | 0.99143 | -0.16464 | 0.99136 | -0.16603 | 0.73594
5 | -0.012458 | -0.0031211 | 0.01246 | 0.003122 | 1.645e-06 | 8.9067e-07 | 0.018689 | 0.018689 | 0.018689 | 0.99189 | -0.15572 | 0.99204 | -0.15295 | 5.1344
6 | 0.00039762 | 9.9013e-05 | -0.00039762 | -9.911e-05 | 1.0085e-09 | -9.6774e-08 | 0.00059659 | 0.00059663 | 0.00059663 | 0.99136 | -0.16603 | 0.99136 | -0.16609 | 0.16391
7 | -0.013059 | -0.0032723 | 0.013062 | 0.0032736 | 2.3953e-06 | 1.318e-06 | 0.019588 | 0.019588 | 0.019588 | 0.99204 | -0.15295 | 0.99223 | -0.1491 | 5.3814
8 | -0.00039761 | -9.9651e-05 | 0.00039761 | 9.9451e-05 | 2.0788e-09 | -1.9935e-07 | 0.00059682 | 0.00059675 | 0.00059682 | 0.99134 | -0.16638 | 0.99135 | -0.16627 | 0.16396
9 | -0.00039761 | -9.9451e-05 | 0.00039762 | 9.911e-05 | 3.5596e-09 | -3.4147e-07 | 0.00059675 | 0.00059663 | 0.00059675 | 0.99135 | -0.16627 | 0.99136 | -0.16609 | 0.16394
10 | -0.041073 | -0.010319 | 0.041306 | 0.010466 | 0.00023286 | 0.00014691 | 0.061605 | 0.061604 | 0.061605 | 0.99223 | -0.1491 | 0.99838 | -0.031033 | 16.9244
11 | 0.027464 | 0.006908 | -0.027433 | -0.0068884 | 3.1573e-05 | 1.9567e-05 | 0.041196 | 0.041196 | 0.041196 | 0.99223 | -0.1491 | 0.99099 | -0.1732 | 11.3176
12 | -0.0093235 | -0.0023391 | 0.0093308 | 0.0023425 | 7.276e-06 | 3.3913e-06 | 0.014031 | 0.014031 | 0.014031 | 0.98883 | -0.215 | 0.98968 | -0.19864 | 3.8547
13 | 0.0093235 | 0.0023391 | -0.0093191 | -0.002337 | 4.479e-06 | 2.0887e-06 | 0.014031 | 0.014031 | 0.014031 | 0.98883 | -0.215 | 0.98832 | -0.22508 | 3.8548
14 | -0.015548 | -0.0039006 | 0.015554 | 0.0039042 | 6.1084e-06 | 3.5262e-06 | 0.023378 | 0.023378 | 0.023378 | 0.98968 | -0.19864 | 0.9901 | -0.1904 | 6.4226
15 | 0.0093191 | 0.002337 | -0.0093125 | -0.0023339 | 6.5849e-06 | 3.0723e-06 | 0.014031 | 0.014032 | 0.014032 | 0.98832 | -0.22508 | 0.98755 | -0.23991 | 3.8549
16 | -0.020922 | -0.0052494 | 0.020922 | 0.0052496 | 3.9308e-07 | 2.3793e-07 | 0.031445 | 0.031445 | 0.031445 | 0.9901 | -0.1904 | 0.99012 | -0.19001 | 8.6387
17 | -0.024217 | -0.0060754 | 0.024236 | 0.0060873 | 1.9427e-05 | 1.193e-05 | 0.036397 | 0.036397 | 0.036397 | 0.99012 | -0.19001 | 0.99099 | -0.1732 | 9.9991
18 | -0.10345 | -0.02598 | 0.1036 | 0.026079 | 0.00015392 | 9.8292e-05 | 0.15557 | 0.15557 | 0.15557 | 0.98961 | -0.19971 | 0.99121 | -0.16857 | 42.7383
19 | 0.06108 | 0.015362 | -0.061016 | -0.015321 | 6.3618e-05 | 4.0458e-05 | 0.091861 | 0.091862 | 0.091862 | 0.98961 | -0.19971 | 0.98848 | -0.22153 | 25.2367
20 | -0.11469 | -0.028858 | 0.11487 | 0.028972 | 0.00017875 | 0.00011419 | 0.17221 | 0.17221 | 0.17221 | 0.99121 | -0.16857 | 0.9929 | -0.13601 | 47.3116
21 | 0.028058 | 0.0070457 | -0.028028 | -0.0070276 | 2.9054e-05 | 1.8039e-05 | 0.042242 | 0.042242 | 0.042242 | 0.98848 | -0.22153 | 0.98736 | -0.24326 | 11.6049
22 | 0.032959 | 0.0082758 | -0.032929 | -0.0082573 | 2.9537e-05 | 1.8494e-05 | 0.04962 | 0.04962 | 0.04962 | 0.98848 | -0.22153 | 0.98751 | -0.24034 | 13.6319
23 | -0.062332 | -0.015735 | 0.062389 | 0.015772 | 5.7274e-05 | 3.6424e-05 | 0.092941 | 0.092941 | 0.092941 | 0.99838 | -0.031033 | 0.99938 | -0.011871 | 25.5333
24 | -0.14112 | -0.035502 | 0.1412 | 0.035553 | 8.0087e-05 | 5.1002e-05 | 0.21016 | 0.21016 | 0.21016 | 0.99938 | -0.011871 | 1 | 0 | 28.8683
25 | 0.19046 | 0.048305 | -0.18982 | -0.047897 | 0.00063882 | 0.00040774 | 0.28361 | 0.28361 | 0.28361 | 1 | 0 | 0.99634 | -0.07002 | 38.9569
26 | 0.11523 | 0.029204 | -0.11511 | -0.029128 | 0.00011981 | 7.6538e-05 | 0.17221 | 0.17221 | 0.17221 | 0.99634 | -0.07002 | 0.99521 | -0.091683 | 47.3115
27 | 0.11511 | 0.029128 | -0.11487 | -0.028972 | 0.00024432 | 0.00015608 | 0.17221 | 0.17221 | 0.17221 | 0.99521 | -0.091683 | 0.9929 | -0.13601 | 47.3116
28 | -0.0082013 | -0.0020554 | 0.0082024 | 0.0020559 | 1.0299e-06 | 4.2963e-07 | 0.012366 | 0.012366 | 0.012366 | 0.98688 | -0.25268 | 0.98701 | -0.25005 | 3.3972
29 | -0.020468 | -0.00513 | 0.020478 | 0.0051357 | 9.4717e-06 | 5.7227e-06 | 0.030858 | 0.030858 | 0.030858 | 0.98701 | -0.25005 | 0.98751 | -0.24034 | 8.4774
30 | 0.012451 | 0.0031216 | -0.012448 | -0.0031198 | 3.2106e-06 | 1.7437e-06 | 0.018763 | 0.018763 | 0.018763 | 0.98751 | -0.24034 | 0.98723 | -0.24575 | 5.1546
31 | 0.028028 | 0.0070276 | -0.02802 | -0.0070226 | 8.1672e-06 | 5.0709e-06 | 0.042242 | 0.042242 | 0.042242 | 0.98736 | -0.24326 | 0.98705 | -0.24938 | 11.6049

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41169 | 0.10351

## res_load
| p_mw | q_mvar
0 | 0.0072004 | 0.0018046
1 | 0.003015 | 0.00075562
2 | 0.00045304 | 0.00011354
3 | 0.0013872 | 0.00034767
4 | 0.00059954 | 0.00015026
5 | 0.00039761 | 9.9651e-05
6 | 0.00054728 | 0.00013716
7 | 0.0062171 | 0.0015581
8 | 0.0053676 | 0.0013452
9 | 0.0093125 | 0.0023339
10 | 0.0032948 | 0.00082577
11 | 0.042368 | 0.010618
12 | 0.011089 | 0.0027792
13 | 0.021026 | 0.0052695
14 | 0.0031964 | 0.00080109
15 | 0.078727 | 0.019731
16 | 0.07839 | 0.019646
17 | 0.074586 | 0.018693
18 | 0.0082013 | 0.0020554
19 | 0.012266 | 0.0030741
20 | 0.012448 | 0.0031198
21 | 0.02802 | 0.0070226

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1