## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-40_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-40_0_5_node_30 | 0.4 | n |  | TRUE
2 | bus_LV_2196-40_0_5_node_29 | 0.4 | n |  | TRUE
3 | bus_LV_2196-40_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-40_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2196-40_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2196-40_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2196-40_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2196-40_0_5_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_2196-40_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2196-40_0_5_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_2196-40_0_5_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_2196-40_0_5_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_2196-40_0_5_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2196-40_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2196-40_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2196-40_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2196-40_0_5_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2196-40_0_5_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_2196-40_0_5_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2196-40_0_5_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2196-40_0_5_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2196-40_0_5_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_2196-40_0_5_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2196-40_0_5_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_2196-40_0_5_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_2196-40_0_5_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_2196-40_0_5_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_2196-40_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2196-40_0_5_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2196-40_0_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2196-40_0_5_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2196-40_0_5_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_2196-40_0_5_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_2196-40_0_5_node_31 | 0.4 | n |  | TRUE
35 | bus_MV_507_0_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-40_0_5_load_0 | 0 | 0.03954 | 0.0099098 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-40_0_5_load_30 | 1 | 0.0095726 | 0.0023991 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-40_0_5_load_29 | 2 | 0.012967 | 0.0032497 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-40_0_5_load_3 | 3 | 0.011905 | 0.0029837 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-40_0_5_load_4 | 4 | 0.043578 | 0.010922 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-40_0_5_load_7 | 7 | 0.0084736 | 0.0021237 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-40_0_5_load_11 | 8 | 0.045978 | 0.011523 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-40_0_5_load_8 | 9 | 0.011388 | 0.0028541 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-40_0_5_load_20 | 11 | 0.0092214 | 0.0023111 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-40_0_5_load_14 | 12 | 0.0069837 | 0.0017503 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-40_0_5_load_15 | 13 | 0.056039 | 0.014045 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-40_0_5_load_9 | 14 | 0.077715 | 0.019477 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-40_0_5_load_10 | 15 | 0.01674 | 0.0041955 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-40_0_5_load_17 | 18 | 0.0038325 | 0.00096052 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-40_0_5_load_19 | 20 | 0.027977 | 0.0070118 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-40_0_5_load_18 | 21 | 0.0077071 | 0.0019316 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-40_0_5_load_25 | 22 | 0.0094213 | 0.0023612 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-40_0_5_load_28 | 23 | 0.0060377 | 0.0015132 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-40_0_5_load_35 | 24 | 0.0025275 | 0.00063344 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-40_0_5_load_23 | 25 | 0.0049366 | 0.0012372 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-40_0_5_load_34 | 26 | 0.0046363 | 0.001162 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-40_0_5_load_37 | 27 | 0.010174 | 0.00255 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-40_0_5_load_22 | 28 | 0.021411 | 0.005366 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-40_0_5_load_26 | 30 | 0.028425 | 0.007124 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2196-40_0_5_load_27 | 31 | 0.020074 | 0.005031 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2196-40_0_5_load_36 | 33 | 0.0021321 | 0.00053435 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-40_0_5_line_0 |  | 0 | 1 | 0.043342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-40_0_5_line_1 |  | 1 | 2 | 0.035836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-40_0_5_line_2 |  | 2 | 34 | 0.021204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-40_0_5_line_3 |  | 3 | 4 | 0.013527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-40_0_5_line_4 |  | 3 | 5 | 0.015894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-40_0_5_line_5 |  | 5 | 6 | 0.032521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-40_0_5_line_6 |  | 5 | 7 | 0.020461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-40_0_5_line_7 |  | 6 | 8 | 0.096541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-40_0_5_line_8 |  | 6 | 9 | 0.01788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-40_0_5_line_9 |  | 7 | 10 | 0.022011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2196-40_0_5_line_10 |  | 8 | 11 | 0.0015784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-40_0_5_line_11 |  | 10 | 12 | 0.011127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2196-40_0_5_line_12 |  | 10 | 13 | 0.031675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-40_0_5_line_13 |  | 11 | 19 | 0.089586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-40_0_5_line_14 |  | 12 | 21 | 0.013265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2196-40_0_5_line_15 |  | 13 | 23 | 0.0074441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-40_0_5_line_16 |  | 14 | 15 | 0.013392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-40_0_5_line_17 |  | 15 | 16 | 0.01632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-40_0_5_line_18 |  | 16 | 17 | 0.005141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2196-40_0_5_line_19 |  | 16 | 18 | 0.042005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2196-40_0_5_line_20 |  | 17 | 20 | 0.025985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-40_0_5_line_21 |  | 17 | 21 | 0.015735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2196-40_0_5_line_22 |  | 18 | 22 | 0.020685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2196-40_0_5_line_23 |  | 19 | 27 | 0.11189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-40_0_5_line_24 |  | 20 | 24 | 0.022366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-40_0_5_line_25 |  | 22 | 25 | 0.009796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-40_0_5_line_26 |  | 24 | 26 | 0.01451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-40_0_5_line_27 |  | 25 | 28 | 0.025615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-40_0_5_line_28 |  | 28 | 29 | 0.006433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-40_0_5_line_29 |  | 29 | 30 | 0.017186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-40_0_5_line_30 |  | 29 | 31 | 0.017906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-40_0_5_line_31 |  | 31 | 32 | 0.022541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2196-40_0_5_line_32 |  | 32 | 33 | 0.0754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2196-40_0_5_line_33 |  | 32 | 34 | 0.04403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-40_0_5_trafo_12 | 0.63 MVA 20/0.4 kV | 35 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2578263.6126 | 1184272.0561 | 2578225.1841 | 1184252.0111
1 | 2578257.8709 | 1184307.4293 | 2578263.6126 | 1184272.0561
2 | 2578254.4736 | 1184328.3593 | 2578257.8709 | 1184307.4293
3 | 2578405.3405 | 1184311.2803 | 2578406.1988 | 1184305.8966 | 2578407.5586 | 1184297.9363
4 | 2578410.2349 | 1184282.2697 | 2578407.5586 | 1184297.9363
5 | 2578442.6711 | 1184285.6764 | 2578410.2349 | 1184282.2697
6 | 2578410.2349 | 1184282.2697 | 2578390.0786 | 1184278.7491
7 | 2578442.6711 | 1184285.6764 | 2578445.4179 | 1184293.8485 | 2578444.0629 | 1184356.097 | 2578449.231 | 1184368.9739 | 2578451.6402 | 1184374.557 | 2578453.8968 | 1184379.7918
8 | 2578442.6711 | 1184285.6764 | 2578439.0436 | 1184303.1849
9 | 2578368.3962 | 1184274.9619 | 2578390.0786 | 1184278.7491
10 | 2578453.8968 | 1184379.7918 | 2578454.5216 | 1184381.2412
11 | 2578368.3962 | 1184274.9619 | 2578366.3236 | 1184285.8942
12 | 2578368.3962 | 1184274.9619 | 2578337.0277 | 1184270.5665
13 | 2578491.0227 | 1184462.9499 | 2578490.2796 | 1184462.1744 | 2578485.8997 | 1184454.0304 | 2578454.5216 | 1184381.2412
14 | 2578366.3236 | 1184285.8942 | 2578363.8528 | 1184298.9272
15 | 2578337.0277 | 1184270.5665 | 2578329.6556 | 1184269.5335
16 | 2578389.0526 | 1184324.9235 | 2578375.893 | 1184322.4411
17 | 2578359.8562 | 1184319.416 | 2578375.893 | 1184322.4411
18 | 2578359.8562 | 1184319.416 | 2578360.9218 | 1184314.3873
19 | 2578359.8562 | 1184319.416 | 2578359.1966 | 1184322.7423 | 2578354.8263 | 1184344.6696 | 2578351.6479 | 1184360.6117
20 | 2578360.9218 | 1184314.3873 | 2578353.6764 | 1184313.8577 | 2578335.2604 | 1184317.2174
21 | 2578360.9218 | 1184314.3873 | 2578363.8528 | 1184298.9272
22 | 2578331.2941 | 1184358.7153 | 2578338.632 | 1184357.8797 | 2578351.6479 | 1184360.6117 | 2578351.6479 | 1184360.6117
23 | 2578491.0227 | 1184462.9499 | 2578380.209 | 1184478.4363
24 | 2578313.2486 | 1184321.1723 | 2578314.2567 | 1184321.049 | 2578335.2604 | 1184317.2174
25 | 2578331.2941 | 1184358.7153 | 2578321.561 | 1184359.8235
26 | 2578298.8458 | 1184322.9335 | 2578313.2486 | 1184321.1723
27 | 2578296.111 | 1184362.7215 | 2578321.561 | 1184359.8235
28 | 2578289.7193 | 1184363.4493 | 2578296.111 | 1184362.7215
29 | 2578289.7193 | 1184363.4493 | 2578289.9168 | 1184346.2645
30 | 2578289.7193 | 1184363.4493 | 2578272.22 | 1184367.2435
31 | 2578250.1906 | 1184372.0199 | 2578272.22 | 1184367.2435
32 | 2578250.1906 | 1184372.0199 | 2578248.2531 | 1184428.8566 | 2578248.3207 | 1184447.3866
33 | 2578254.4736 | 1184328.3593 | 2578251.1279 | 1184344.391 | 2578250.1906 | 1184372.0199

## bus_geodata
| x | y | coords
0 | 2578225.1841 | 1184252.0111
1 | 2578263.6126 | 1184272.0561
2 | 2578257.8709 | 1184307.4293
3 | 2578407.5586 | 1184297.9363
4 | 2578405.3405 | 1184311.2803
5 | 2578410.2349 | 1184282.2697
6 | 2578442.6711 | 1184285.6764
7 | 2578390.0786 | 1184278.7491
8 | 2578453.8968 | 1184379.7918
9 | 2578439.0436 | 1184303.1849
10 | 2578368.3962 | 1184274.9619
11 | 2578454.5216 | 1184381.2412
12 | 2578366.3236 | 1184285.8942
13 | 2578337.0277 | 1184270.5665
14 | 2578389.0526 | 1184324.9235
15 | 2578375.893 | 1184322.4411
16 | 2578359.8562 | 1184319.416
17 | 2578360.9218 | 1184314.3873
18 | 2578351.6479 | 1184360.6117
19 | 2578491.0227 | 1184462.9499
20 | 2578335.2604 | 1184317.2173
21 | 2578363.8528 | 1184298.9272
22 | 2578331.2941 | 1184358.7153
23 | 2578329.6556 | 1184269.5335
24 | 2578313.2486 | 1184321.1723
25 | 2578321.561 | 1184359.8235
26 | 2578298.8458 | 1184322.9335
27 | 2578380.209 | 1184478.4363
28 | 2578296.111 | 1184362.7215
29 | 2578289.7193 | 1184363.4493
30 | 2578289.9168 | 1184346.2645
31 | 2578272.22 | 1184367.2435
32 | 2578250.1906 | 1184372.0199
33 | 2578248.3207 | 1184447.3866
34 | 2578254.4736 | 1184328.3593
35 | 2578360.9218 | 1184314.3873

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98089 | -0.3685 | 0.03954 | 0.0099098
1 | 0.98247 | -0.33751 | 0.0095726 | 0.0023991
2 | 0.9841 | -0.30578 | 0.012967 | 0.0032497
3 | 0.99081 | -0.17622 | 0.011905 | 0.0029837
4 | 0.99027 | -0.18669 | 0.043578 | 0.010922
5 | 0.99161 | -0.16057 | 0 | 0
6 | 0.98931 | -0.20493 | 0 | 0
7 | 0.9941 | -0.11272 | 0.0084736 | 0.0021237
8 | 0.98349 | -0.318 | 0.045978 | 0.011523
9 | 0.98913 | -0.20856 | 0.011388 | 0.0028541
10 | 0.99553 | -0.085447 | 0 | 0
11 | 0.98346 | -0.31855 | 0.0092214 | 0.0023111
12 | 0.99656 | -0.065624 | 0.0069837 | 0.0017503
13 | 0.99373 | -0.12009 | 0.056039 | 0.014045
14 | 0.99765 | -0.045113 | 0.077715 | 0.019477
15 | 0.9986 | -0.026905 | 0.01674 | 0.0041955
16 | 1 | 0 | -0.50514 | -0.12777
17 | 0.99941 | -0.011326 | 0 | 0
18 | 0.99706 | -0.055925 | 0.0038325 | 0.00096052
19 | 0.98262 | -0.335 | 0 | 0
20 | 0.99858 | -0.027274 | 0.027977 | 0.0070118
21 | 0.99784 | -0.041235 | 0.0077071 | 0.0019316
22 | 0.99565 | -0.082889 | 0.0094213 | 0.0023612
23 | 0.99369 | -0.12088 | 0.0060377 | 0.0015132
24 | 0.99843 | -0.030075 | 0.0025275 | 0.00063344
25 | 0.99439 | -0.10687 | 0.0049366 | 0.0012372
26 | 0.99837 | -0.031252 | 0.0046363 | 0.001162
27 | 0.98157 | -0.35558 | 0.010174 | 0.00255
28 | 0.99123 | -0.16762 | 0.021411 | 0.005366
29 | 0.99057 | -0.1805 | 0 | 0
30 | 0.99012 | -0.18918 | 0.028425 | 0.007124
31 | 0.98917 | -0.20734 | 0.020074 | 0.005031
32 | 0.98784 | -0.23316 | 0 | 0
33 | 0.98769 | -0.23604 | 0.0021321 | 0.00053435
34 | 0.98531 | -0.28211 | 0 | 0
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.03954 | -0.0099098 | 0.039599 | 0.0099466 | 5.8479e-05 | 3.6879e-05 | 0.059983 | 0.059983 | 0.059983 | 0.98089 | -0.3685 | 0.98247 | -0.33751 | 16.4789
1 | -0.049171 | -0.012346 | 0.049246 | 0.012393 | 7.455e-05 | 4.7257e-05 | 0.074481 | 0.074481 | 0.074481 | 0.98247 | -0.33751 | 0.9841 | -0.30578 | 20.4619
2 | -0.062213 | -0.015643 | 0.062283 | 0.015688 | 7.039e-05 | 4.478e-05 | 0.094087 | 0.094087 | 0.094087 | 0.9841 | -0.30578 | 0.98531 | -0.28211 | 25.8482
3 | 0.043599 | 0.010935 | -0.043578 | -0.010922 | 2.1751e-05 | 1.3747e-05 | 0.065482 | 0.065482 | 0.065482 | 0.99081 | -0.17622 | 0.99027 | -0.18669 | 17.9895
4 | -0.055504 | -0.013919 | 0.055546 | 0.013945 | 4.1417e-05 | 2.6302e-05 | 0.083361 | 0.083361 | 0.083361 | 0.99081 | -0.17622 | 0.99161 | -0.16057 | 22.9013
5 | 0.077301 | 0.019579 | -0.077137 | -0.019474 | 0.0001643 | 0.00010473 | 0.11607 | 0.11607 | 0.11607 | 0.99161 | -0.16057 | 0.98931 | -0.20493 | 31.8877
6 | -0.13285 | -0.033524 | 0.13315 | 0.033719 | 0.00030518 | 0.00019505 | 0.19943 | 0.19943 | 0.19943 | 0.99161 | -0.16057 | 0.9941 | -0.11272 | 54.7889
7 | 0.065747 | 0.016619 | -0.065392 | -0.016394 | 0.00035439 | 0.00022558 | 0.098939 | 0.09894 | 0.09894 | 0.98931 | -0.20493 | 0.98349 | -0.318 | 27.1813
8 | 0.01139 | 0.0028551 | -0.011388 | -0.0028541 | 1.9679e-06 | 1.0299e-06 | 0.017132 | 0.017132 | 0.017132 | 0.98931 | -0.20493 | 0.98913 | -0.20856 | 4.7065
9 | -0.14163 | -0.035843 | 0.14181 | 0.035961 | 0.00018569 | 0.00011827 | 0.21212 | 0.21211 | 0.21212 | 0.9941 | -0.11272 | 0.99553 | -0.085447 | 29.1367
10 | 0.019414 | 0.0048703 | -0.019414 | -0.00487 | 5.1074e-07 | 3.0685e-07 | 0.029375 | 0.029375 | 0.029375 | 0.98349 | -0.318 | 0.98346 | -0.31855 | 8.0702
11 | -0.20399 | -0.051584 | 0.20418 | 0.051708 | 0.00019417 | 0.00012398 | 0.30507 | 0.30507 | 0.30507 | 0.99553 | -0.085447 | 0.99656 | -0.065624 | 41.905
12 | 0.062179 | 0.015623 | -0.062077 | -0.015558 | 0.00010263 | 6.5273e-05 | 0.092954 | 0.092954 | 0.092954 | 0.99553 | -0.085447 | 0.99373 | -0.12009 | 25.5368
13 | 0.010192 | 0.0025589 | -0.010184 | -0.0025549 | 7.9914e-06 | 3.9787e-06 | 0.015423 | 0.015424 | 0.015424 | 0.98346 | -0.31855 | 0.98262 | -0.335 | 4.2372
14 | -0.21117 | -0.053459 | 0.21142 | 0.053617 | 0.00024757 | 0.0001581 | 0.3155 | 0.3155 | 0.3155 | 0.99656 | -0.065624 | 0.99784 | -0.041235 | 43.3374
15 | 0.0060379 | 0.0015132 | -0.0060377 | -0.0015132 | 2.2819e-07 | 4.9606e-08 | 0.0090412 | 0.0090412 | 0.0090412 | 0.99373 | -0.12009 | 0.99369 | -0.12088 | 2.4839
16 | -0.077715 | -0.019477 | 0.077783 | 0.01952 | 6.7474e-05 | 4.3008e-05 | 0.11591 | 0.11591 | 0.11591 | 0.99765 | -0.045113 | 0.9986 | -0.026905 | 31.8444
17 | -0.094523 | -0.023716 | 0.094644 | 0.023793 | 0.00012142 | 7.7498e-05 | 0.14086 | 0.14086 | 0.14086 | 0.9986 | -0.026905 | 1 | 0 | 38.6973
18 | 0.25475 | 0.064663 | -0.25461 | -0.064574 | 0.00013872 | 8.8647e-05 | 0.37936 | 0.37936 | 0.37936 | 1 | 0 | 0.99941 | -0.011326 | 52.1093
19 | 0.1541 | 0.03931 | -0.15368 | -0.039045 | 0.00041499 | 0.00026449 | 0.22954 | 0.22954 | 0.22954 | 1 | 0 | 0.99706 | -0.055925 | 31.5306
20 | 0.035169 | 0.0088243 | -0.035142 | -0.0088075 | 2.6722e-05 | 1.6762e-05 | 0.052367 | 0.052367 | 0.052367 | 0.99941 | -0.011326 | 0.99858 | -0.027274 | 14.3865
21 | 0.21944 | 0.05575 | -0.21912 | -0.055548 | 0.00031546 | 0.00020148 | 0.32699 | 0.32699 | 0.32699 | 0.99941 | -0.011326 | 0.99784 | -0.041235 | 44.9161
22 | 0.14985 | 0.038085 | -0.14965 | -0.037961 | 0.0001943 | 0.00012381 | 0.22382 | 0.22382 | 0.22382 | 0.99706 | -0.055925 | 0.99565 | -0.082889 | 30.7449
23 | 0.010184 | 0.0025549 | -0.010174 | -0.00255 | 9.9817e-06 | 4.9725e-06 | 0.015424 | 0.015424 | 0.015424 | 0.98262 | -0.335 | 0.98157 | -0.35558 | 4.2374
24 | 0.007165 | 0.0017957 | -0.0071641 | -0.0017954 | 9.5611e-07 | 3.1936e-07 | 0.010677 | 0.010677 | 0.010677 | 0.99858 | -0.027274 | 0.99843 | -0.030075 | 2.9332
25 | 0.14023 | 0.0356 | -0.14007 | -0.035496 | 0.0001616 | 0.0001033 | 0.20974 | 0.20974 | 0.20974 | 0.99565 | -0.082889 | 0.99439 | -0.10687 | 57.6217
26 | 0.0046366 | 0.001162 | -0.0046363 | -0.001162 | 2.5982e-07 | -2.3466e-08 | 0.0069101 | 0.0069102 | 0.0069102 | 0.99843 | -0.030075 | 0.99837 | -0.031252 | 1.8984
27 | 0.13514 | 0.034259 | -0.13474 | -0.034008 | 0.00039332 | 0.0002514 | 0.20236 | 0.20236 | 0.20236 | 0.99439 | -0.10687 | 0.99123 | -0.16762 | 55.5923
28 | 0.11333 | 0.028642 | -0.11326 | -0.028597 | 6.9894e-05 | 4.4649e-05 | 0.17021 | 0.17021 | 0.17021 | 0.99123 | -0.16762 | 0.99057 | -0.1805 | 46.7623
29 | 0.028437 | 0.0071313 | -0.028425 | -0.007124 | 1.1761e-05 | 7.3059e-06 | 0.042719 | 0.042719 | 0.042719 | 0.99057 | -0.1805 | 0.99012 | -0.18918 | 11.736
30 | 0.084825 | 0.021466 | -0.084716 | -0.021396 | 0.00010915 | 6.9625e-05 | 0.1275 | 0.1275 | 0.1275 | 0.99057 | -0.1805 | 0.98917 | -0.20734 | 35.0264
31 | 0.064642 | 0.016365 | -0.064561 | -0.016314 | 8.0025e-05 | 5.0927e-05 | 0.097299 | 0.097299 | 0.097299 | 0.98917 | -0.20734 | 0.98784 | -0.23316 | 26.7305
32 | 0.0021324 | 0.00053358 | -0.0021321 | -0.00053435 | 2.9171e-07 | -7.7844e-07 | 0.0032118 | 0.0032121 | 0.0032121 | 0.98784 | -0.23316 | 0.98769 | -0.23604 | 0.88246
33 | 0.062429 | 0.01578 | -0.062283 | -0.015688 | 0.00014616 | 9.2983e-05 | 0.094087 | 0.094087 | 0.094087 | 0.98784 | -0.23316 | 0.98531 | -0.28211 | 25.8482

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50514 | 0.12777

## res_load
| p_mw | q_mvar
0 | 0.03954 | 0.0099098
1 | 0.0095726 | 0.0023991
2 | 0.012967 | 0.0032497
3 | 0.011905 | 0.0029837
4 | 0.043578 | 0.010922
5 | 0.0084736 | 0.0021237
6 | 0.045978 | 0.011523
7 | 0.011388 | 0.0028541
8 | 0.0092214 | 0.0023111
9 | 0.0069837 | 0.0017503
10 | 0.056039 | 0.014045
11 | 0.077715 | 0.019477
12 | 0.01674 | 0.0041955
13 | 0.0038325 | 0.00096052
14 | 0.027977 | 0.0070118
15 | 0.0077071 | 0.0019316
16 | 0.0094213 | 0.0023612
17 | 0.0060377 | 0.0015132
18 | 0.0025275 | 0.00063344
19 | 0.0049366 | 0.0012372
20 | 0.0046363 | 0.001162
21 | 0.010174 | 0.00255
22 | 0.021411 | 0.005366
23 | 0.028425 | 0.007124
24 | 0.020074 | 0.005031
25 | 0.0021321 | 0.00053435

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1