## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-42_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-42_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-42_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-42_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-42_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2196-42_0_4_node_23 | 0.4 | n |  | TRUE
6 | bus_LV_2196-42_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2196-42_0_4_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_2196-42_0_4_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_2196-42_0_4_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_2196-42_0_4_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_2196-42_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2196-42_0_4_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_2196-42_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2196-42_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2196-42_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2196-42_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2196-42_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2196-42_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_2196-42_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2196-42_0_4_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_2196-42_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2196-42_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2196-42_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_2196-42_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2196-42_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2196-42_0_4_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_2196-42_0_4_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_2196-42_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2196-42_0_4_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_2196-42_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_2196-42_0_4_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_2196-42_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_MV_508_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-42_0_4_load_0 | 0 | 0.030445 | 0.0076302 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-42_0_4_load_1 | 1 | 0.03377 | 0.0084636 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-42_0_4_load_3 | 3 | 0.033405 | 0.0083721 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-42_0_4_load_5 | 4 | 0.059253 | 0.01485 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-42_0_4_load_4 | 6 | 0.052883 | 0.013254 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-42_0_4_load_22 | 8 | 0.066074 | 0.01656 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-42_0_4_load_21 | 10 | 0.0081454 | 0.0020414 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-42_0_4_load_6 | 13 | 0.013801 | 0.0034588 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-42_0_4_load_7 | 14 | 0.017317 | 0.00434 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-42_0_4_load_9 | 15 | 0.0036705 | 0.00091992 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-42_0_4_load_11 | 16 | 0.0087883 | 0.0022026 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-42_0_4_load_12 | 17 | 0.022701 | 0.0056895 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-42_0_4_load_13 | 19 | 0.025963 | 0.0065069 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-42_0_4_load_28 | 20 | 0.00948 | 0.0023759 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-42_0_4_load_16 | 23 | 0.025125 | 0.0062969 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-42_0_4_load_17 | 24 | 0.025446 | 0.0063773 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-42_0_4_load_26 | 25 | 0.0087762 | 0.0021995 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-42_0_4_load_30 | 26 | 0.035448 | 0.0088841 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-42_0_4_load_31 | 27 | 0.013609 | 0.0034108 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-42_0_4_load_25 | 28 | 0.040245 | 0.010086 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-42_0_4_load_27 | 29 | 0.0086533 | 0.0021687 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-42_0_4_load_29 | 30 | 0.0080575 | 0.0020194 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-42_0_4_load_34 | 31 | 0.038326 | 0.0096055 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-42_0_4_load_32 | 32 | 0.0071564 | 0.0017936 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-42_0_4_line_0 |  | 0 | 1 | 0.0040793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-42_0_4_line_1 |  | 0 | 2 | 0.012323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2196-42_0_4_line_2 |  | 1 | 3 | 0.019757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-42_0_4_line_3 |  | 2 | 4 | 0.023843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2196-42_0_4_line_4 |  | 3 | 5 | 0.0026138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-42_0_4_line_5 |  | 4 | 8 | 0.023155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2196-42_0_4_line_6 |  | 5 | 9 | 0.052347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-42_0_4_line_7 |  | 6 | 7 | 0.0158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2196-42_0_4_line_8 |  | 7 | 10 | 0.0089239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-42_0_4_line_9 |  | 7 | 11 | 0.012095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2196-42_0_4_line_10 |  | 8 | 12 | 0.036521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2196-42_0_4_line_11 |  | 9 | 26 | 0.067568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-42_0_4_line_12 |  | 10 | 20 | 0.0088435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-42_0_4_line_13 |  | 11 | 16 | 0.0043991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-42_0_4_line_14 |  | 11 | 13 | 0.013253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2196-42_0_4_line_15 |  | 12 | 22 | 0.037701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2196-42_0_4_line_16 |  | 13 | 14 | 0.022164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2196-42_0_4_line_17 |  | 14 | 15 | 0.016755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2196-42_0_4_line_18 |  | 15 | 17 | 1.3442e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2196-42_0_4_line_19 |  | 16 | 18 | 0.026565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-42_0_4_line_20 |  | 17 | 19 | 0.025086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2196-42_0_4_line_21 |  | 18 | 21 | 0.089081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-42_0_4_line_22 |  | 19 | 22 | 0.028774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2196-42_0_4_line_23 |  | 20 | 25 | 1.3989e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-42_0_4_line_24 |  | 21 | 24 | 0.076687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-42_0_4_line_25 |  | 22 | 23 | 0.014714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-42_0_4_line_26 |  | 25 | 28 | 0.0048595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-42_0_4_line_27 |  | 26 | 27 | 0.018566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-42_0_4_line_28 |  | 27 | 32 | 0.02564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-42_0_4_line_29 |  | 28 | 29 | 0.0042646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-42_0_4_line_30 |  | 29 | 30 | 0.0087479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-42_0_4_line_31 |  | 30 | 31 | 0.0076657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-42_0_4_trafo_4 | 0.63 MVA 20/0.4 kV | 33 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2577743.7863 | 1183482.7686 | 2577740.1182 | 1183482.5704 | 2577739.713 | 1183482.5469
1 | 2577756.0913 | 1183483.4335 | 2577743.7863 | 1183482.7686
2 | 2577739.713 | 1183482.5469 | 2577719.9894 | 1183481.4055
3 | 2577756.0913 | 1183483.4335 | 2577779.8554 | 1183485.3685
4 | 2577717.3799 | 1183481.2545 | 2577719.9894 | 1183481.4055
5 | 2577802.9344 | 1183487.2474 | 2577800.2202 | 1183487.0266 | 2577779.8554 | 1183485.3685
6 | 2577665.1085 | 1183476.3807 | 2577717.3799 | 1183481.2545
7 | 2577771.1492 | 1183414.8862 | 2577767.7592 | 1183430.3181
8 | 2577771.1492 | 1183414.8862 | 2577762.3759 | 1183413.254
9 | 2577773.9223 | 1183403.1141 | 2577771.1492 | 1183414.8862
10 | 2577839.3964 | 1183488.9932 | 2577819.6922 | 1183488.6106 | 2577802.9344 | 1183487.2474
11 | 2577665.1085 | 1183476.3807 | 2577665.9773 | 1183459.6799 | 2577672.0156 | 1183459.6573 | 2577672.7215 | 1183436.1424 | 2577681.9358 | 1183436.2191 | 2577683.8881 | 1183424.3115
12 | 2577753.6815 | 1183411.6365 | 2577762.3759 | 1183413.254
13 | 2577773.9223 | 1183403.1141 | 2577774.9616 | 1183398.8396
14 | 2577773.9223 | 1183403.1141 | 2577787.0037 | 1183405.2421
15 | 2577839.3964 | 1183488.9932 | 2577842.108 | 1183475.0425 | 2577845.0983 | 1183462.1358 | 2577847.1221 | 1183452.1009
16 | 2577787.0037 | 1183405.2421 | 2577808.8802 | 1183408.8007
17 | 2577808.8802 | 1183408.8007 | 2577825.4177 | 1183411.4908
18 | 2577825.4309 | 1183411.4929 | 2577825.4177 | 1183411.4908
19 | 2577781.238 | 1183373.0268 | 2577774.9616 | 1183398.8396
20 | 2577843.919 | 1183424.7529 | 2577839.5503 | 1183415.3543 | 2577832.7845 | 1183412.6891 | 2577825.4309 | 1183411.4929
21 | 2577834.1747 | 1183322.5259 | 2577826.1556 | 1183325.7018 | 2577818.0068 | 1183328.9226 | 2577807.5838 | 1183332.3187 | 2577794.1017 | 1183334.2143 | 2577786.1775 | 1183334.1771 | 2577782.8427 | 1183365.2612 | 2577781.238 | 1183373.0268
22 | 2577847.1221 | 1183452.1009 | 2577849.4459 | 1183440.5862 | 2577849.1685 | 1183435.7848 | 2577845.6373 | 1183428.4496 | 2577843.919 | 1183424.7529
23 | 2577753.6678 | 1183411.6339 | 2577753.6815 | 1183411.6365
24 | 2577834.1747 | 1183322.5259 | 2577844.1056 | 1183342.8441 | 2577848.4287 | 1183351.6659 | 2577867.212 | 1183391.7293
25 | 2577832.5557 | 1183449.7426 | 2577847.1221 | 1183452.1009
26 | 2577748.8903 | 1183410.7451 | 2577753.6678 | 1183411.6339
27 | 2577683.8881 | 1183424.3115 | 2577685.3317 | 1183415.5067 | 2577691.7278 | 1183408.2891
28 | 2577698.8913 | 1183389.2552 | 2577703.8615 | 1183395.7383 | 2577696.9852 | 1183402.3563 | 2577691.7278 | 1183408.2891
29 | 2577748.8903 | 1183410.7451 | 2577744.6976 | 1183409.9651
30 | 2577744.6976 | 1183409.9651 | 2577736.0973 | 1183408.3651
31 | 2577728.5609 | 1183406.963 | 2577736.0973 | 1183408.3651

## bus_geodata
| x | y | coords
0 | 2577743.7863 | 1183482.7686
1 | 2577739.713 | 1183482.5469
2 | 2577756.0913 | 1183483.4335
3 | 2577719.9894 | 1183481.4055
4 | 2577779.8554 | 1183485.3685
5 | 2577717.3799 | 1183481.2545
6 | 2577767.7592 | 1183430.3181
7 | 2577771.1492 | 1183414.8862
8 | 2577802.9344 | 1183487.2474
9 | 2577665.1085 | 1183476.3807
10 | 2577762.3759 | 1183413.254
11 | 2577773.9223 | 1183403.1141
12 | 2577839.3964 | 1183488.9932
13 | 2577787.0037 | 1183405.2421
14 | 2577808.8802 | 1183408.8007
15 | 2577825.4177 | 1183411.4908
16 | 2577774.9616 | 1183398.8396
17 | 2577825.4309 | 1183411.4929
18 | 2577781.238 | 1183373.0268
19 | 2577843.919 | 1183424.7529
20 | 2577753.6815 | 1183411.6365
21 | 2577834.1747 | 1183322.5259
22 | 2577847.1221 | 1183452.1009
23 | 2577832.5557 | 1183449.7426
24 | 2577867.212 | 1183391.7293
25 | 2577753.6678 | 1183411.6339
26 | 2577683.8881 | 1183424.3115
27 | 2577691.7278 | 1183408.2891
28 | 2577748.8903 | 1183410.7451
29 | 2577744.6976 | 1183409.9651
30 | 2577736.0973 | 1183408.3651
31 | 2577728.5609 | 1183406.963
32 | 2577698.8913 | 1183389.2552
33 | 2577771.1492 | 1183414.8862

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98075 | -0.36991 | 0.030445 | 0.0076302
1 | 0.98028 | -0.37903 | 0.03377 | 0.0084636
2 | 0.98163 | -0.35274 | 0 | 0
3 | 0.97863 | -0.4112 | 0.033405 | 0.0083721
4 | 0.98248 | -0.33617 | 0.059253 | 0.01485
5 | 0.9785 | -0.41388 | 0 | 0
6 | 1 | 0 | -0.55215 | -0.14061
7 | 0.99802 | -0.037506 | 0 | 0
8 | 0.98363 | -0.31392 | 0.066074 | 0.01656
9 | 0.97575 | -0.4676 | 0 | 0
10 | 0.99703 | -0.056526 | 0.0081454 | 0.0020414
11 | 0.99685 | -0.059862 | 0 | 0
12 | 0.98598 | -0.26812 | 0 | 0
13 | 0.99566 | -0.082424 | 0.013801 | 0.0034588
14 | 0.99375 | -0.11893 | 0.017317 | 0.00434
15 | 0.99236 | -0.14533 | 0.0036705 | 0.00091992
16 | 0.99671 | -0.062504 | 0.0087883 | 0.0022026
17 | 0.99236 | -0.14535 | 0.022701 | 0.0056895
18 | 0.99609 | -0.074374 | 0 | 0
19 | 0.99045 | -0.18208 | 0.025963 | 0.0065069
20 | 0.99612 | -0.074147 | 0.00948 | 0.0023759
21 | 0.99402 | -0.11428 | 0 | 0
22 | 0.98842 | -0.22106 | 0 | 0
23 | 0.98808 | -0.22765 | 0.025125 | 0.0062969
24 | 0.99224 | -0.14877 | 0.025446 | 0.0063773
25 | 0.99612 | -0.074173 | 0.0087762 | 0.0021995
26 | 0.97221 | -0.53739 | 0.035448 | 0.0088841
27 | 0.97185 | -0.5445 | 0.013609 | 0.0034108
28 | 0.9957 | -0.08231 | 0.040245 | 0.010086
29 | 0.99548 | -0.086437 | 0.0086533 | 0.0021687
30 | 0.99511 | -0.093576 | 0.0080575 | 0.0020194
31 | 0.99485 | -0.098749 | 0.038326 | 0.0096055
32 | 0.97168 | -0.54789 | 0.0071564 | 0.0017936
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12393 | 0.031268 | -0.12388 | -0.031234 | 5.4128e-05 | 3.459e-05 | 0.18811 | 0.18811 | 0.18811 | 0.98075 | -0.36991 | 0.98028 | -0.37903 | 51.6773
1 | -0.15438 | -0.038899 | 0.1545 | 0.038979 | 0.00012684 | 8.0865e-05 | 0.2343 | 0.2343 | 0.2343 | 0.98075 | -0.36991 | 0.98163 | -0.35274 | 32.1836
2 | 0.090106 | 0.02277 | -0.089968 | -0.022682 | 0.00013874 | 8.8544e-05 | 0.13684 | 0.13684 | 0.13684 | 0.98028 | -0.37903 | 0.97863 | -0.4112 | 37.5945
3 | -0.1545 | -0.038979 | 0.15463 | 0.039057 | 0.0001227 | 7.7324e-05 | 0.2343 | 0.2343 | 0.2343 | 0.98163 | -0.35274 | 0.98248 | -0.33617 | 16.0918
4 | 0.056562 | 0.014309 | -0.056555 | -0.014305 | 7.258e-06 | 4.6123e-06 | 0.086051 | 0.086051 | 0.086051 | 0.97863 | -0.4112 | 0.9785 | -0.41388 | 23.6405
5 | -0.21388 | -0.053907 | 0.21411 | 0.054052 | 0.00022794 | 0.00014471 | 0.32404 | 0.32404 | 0.32404 | 0.98248 | -0.33617 | 0.98363 | -0.31392 | 22.2553
6 | 0.056555 | 0.014305 | -0.05641 | -0.014212 | 0.00014536 | 9.2374e-05 | 0.086051 | 0.086052 | 0.086052 | 0.9785 | -0.41388 | 0.97575 | -0.4676 | 23.6405
7 | 0.5505 | 0.14061 | -0.5495 | -0.13998 | 0.00099621 | 0.00063674 | 0.82009 | 0.82009 | 0.82009 | 1 | 0 | 0.99802 | -0.037506 | 56.3248
8 | 0.12196 | 0.030675 | -0.12185 | -0.030604 | 0.0001107 | 7.0733e-05 | 0.18188 | 0.18188 | 0.18188 | 0.99802 | -0.037506 | 0.99703 | -0.056526 | 49.9671
9 | 0.42754 | 0.1093 | -0.42708 | -0.10901 | 0.00046185 | 0.00029496 | 0.63821 | 0.63821 | 0.63821 | 0.99802 | -0.037506 | 0.99685 | -0.059862 | 43.8331
10 | -0.28018 | -0.070611 | 0.2808 | 0.071003 | 0.00061551 | 0.00039207 | 0.42399 | 0.42399 | 0.42399 | 0.98363 | -0.31392 | 0.98598 | -0.26812 | 29.1204
11 | 0.05641 | 0.014212 | -0.056222 | -0.014093 | 0.00018763 | 0.00011924 | 0.086052 | 0.086052 | 0.086052 | 0.97575 | -0.4676 | 0.97221 | -0.53739 | 23.6406
12 | 0.11371 | 0.028563 | -0.11361 | -0.028502 | 9.553e-05 | 6.1024e-05 | 0.16972 | 0.16972 | 0.16972 | 0.99703 | -0.056526 | 0.99612 | -0.074147 | 46.6274
13 | 0.034343 | 0.0086473 | -0.034339 | -0.0086445 | 4.3379e-06 | 2.7189e-06 | 0.051279 | 0.051279 | 0.051279 | 0.99685 | -0.059862 | 0.99671 | -0.062504 | 14.0877
14 | 0.39274 | 0.10036 | -0.39231 | -0.10009 | 0.00042803 | 0.00027325 | 0.58693 | 0.58693 | 0.58693 | 0.99685 | -0.059862 | 0.99566 | -0.082424 | 40.3112
15 | -0.2808 | -0.071003 | 0.28143 | 0.071408 | 0.00063539 | 0.00040472 | 0.42399 | 0.42399 | 0.42399 | 0.98598 | -0.26812 | 0.98842 | -0.22106 | 29.1204
16 | 0.37851 | 0.096628 | -0.37784 | -0.096202 | 0.00066638 | 0.00042533 | 0.56631 | 0.56631 | 0.56631 | 0.99566 | -0.082424 | 0.99375 | -0.11893 | 38.8947
17 | 0.36052 | 0.091862 | -0.36006 | -0.09157 | 0.00045868 | 0.00029269 | 0.54038 | 0.54038 | 0.54038 | 0.99375 | -0.11893 | 0.99236 | -0.14533 | 37.1138
18 | 0.35639 | 0.09065 | -0.35639 | -0.090649 | 3.6053e-07 | 2.3004e-07 | 0.53487 | 0.53487 | 0.53487 | 0.99236 | -0.14533 | 0.99236 | -0.14535 | 36.7358
19 | 0.025551 | 0.006442 | -0.025536 | -0.006433 | 1.4505e-05 | 8.9374e-06 | 0.038159 | 0.038159 | 0.038159 | 0.99671 | -0.062504 | 0.99609 | -0.074374 | 10.4832
20 | 0.33369 | 0.08496 | -0.3331 | -0.084584 | 0.00058992 | 0.00037626 | 0.50083 | 0.50083 | 0.50083 | 0.99236 | -0.14535 | 0.99045 | -0.18208 | 34.398
21 | 0.025536 | 0.006433 | -0.025487 | -0.0064031 | 4.8642e-05 | 2.9974e-05 | 0.038159 | 0.038159 | 0.038159 | 0.99609 | -0.074374 | 0.99402 | -0.11428 | 10.4833
22 | 0.30714 | 0.078077 | -0.30656 | -0.07771 | 0.00057535 | 0.00036674 | 0.46183 | 0.46183 | 0.46183 | 0.99045 | -0.18208 | 0.98842 | -0.22106 | 31.719
23 | 0.10413 | 0.026126 | -0.10413 | -0.026126 | 1.2695e-07 | 8.106e-08 | 0.15556 | 0.15556 | 0.15556 | 0.99612 | -0.074147 | 0.99612 | -0.074173 | 42.737
24 | 0.025487 | 0.0064031 | -0.025446 | -0.0063773 | 4.1876e-05 | 2.5808e-05 | 0.038159 | 0.03816 | 0.03816 | 0.99402 | -0.11428 | 0.99224 | -0.14877 | 10.4834
25 | 0.025133 | 0.0063018 | -0.025125 | -0.0062969 | 7.8995e-06 | 4.8672e-06 | 0.037837 | 0.037837 | 0.037837 | 0.98842 | -0.22106 | 0.98808 | -0.22765 | 10.3949
26 | 0.095355 | 0.023926 | -0.095318 | -0.023903 | 3.698e-05 | 2.3604e-05 | 0.14245 | 0.14245 | 0.14245 | 0.99612 | -0.074173 | 0.9957 | -0.08231 | 39.1353
27 | 0.020774 | 0.0052091 | -0.020767 | -0.0052048 | 7.0391e-06 | 4.2749e-06 | 0.031797 | 0.031797 | 0.031797 | 0.97221 | -0.53739 | 0.97185 | -0.5445 | 8.7354
28 | 0.0071576 | 0.001794 | -0.0071564 | -0.0017936 | 1.1548e-06 | 4.2142e-07 | 0.010959 | 0.010959 | 0.010959 | 0.97185 | -0.5445 | 0.97168 | -0.54789 | 3.0108
29 | 0.055073 | 0.013816 | -0.055063 | -0.01381 | 1.0834e-05 | 6.8786e-06 | 0.082309 | 0.082309 | 0.082309 | 0.9957 | -0.08231 | 0.99548 | -0.086437 | 22.6124
30 | 0.046409 | 0.011641 | -0.046393 | -0.011631 | 1.5788e-05 | 9.9908e-06 | 0.069374 | 0.069374 | 0.069374 | 0.99548 | -0.086437 | 0.99511 | -0.093576 | 19.0589
31 | 0.038336 | 0.0096115 | -0.038326 | -0.0096055 | 9.4468e-06 | 5.9464e-06 | 0.057326 | 0.057326 | 0.057326 | 0.99511 | -0.093576 | 0.99485 | -0.098749 | 15.7489

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60503 | 0.15387

## res_load
| p_mw | q_mvar
0 | 0.030445 | 0.0076302
1 | 0.03377 | 0.0084636
2 | 0.033405 | 0.0083721
3 | 0.059253 | 0.01485
4 | 0.052883 | 0.013254
5 | 0.066074 | 0.01656
6 | 0.0081454 | 0.0020414
7 | 0.013801 | 0.0034588
8 | 0.017317 | 0.00434
9 | 0.0036705 | 0.00091992
10 | 0.0087883 | 0.0022026
11 | 0.022701 | 0.0056895
12 | 0.025963 | 0.0065069
13 | 0.00948 | 0.0023759
14 | 0.025125 | 0.0062969
15 | 0.025446 | 0.0063773
16 | 0.0087762 | 0.0021995
17 | 0.035448 | 0.0088841
18 | 0.013609 | 0.0034108
19 | 0.040245 | 0.010086
20 | 0.0086533 | 0.0021687
21 | 0.0080575 | 0.0020194
22 | 0.038326 | 0.0096055
23 | 0.0071564 | 0.0017936

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1