## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-48_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-48_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-48_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-48_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-48_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2196-48_0_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_2196-48_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2196-48_0_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_2196-48_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2196-48_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2196-48_0_4_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_2196-48_0_4_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_2196-48_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_2196-48_0_4_node_33 | 0.4 | n |  | TRUE
14 | bus_LV_2196-48_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2196-48_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2196-48_0_4_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_2196-48_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2196-48_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2196-48_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2196-48_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2196-48_0_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_2196-48_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_2196-48_0_4_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_2196-48_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_2196-48_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2196-48_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2196-48_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2196-48_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_MV_376_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-48_0_4_load_0 | 0 | 0.014054 | 0.0035224 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-48_0_4_load_1 | 1 | 0.015036 | 0.0037685 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-48_0_4_load_4 | 4 | 0.020278 | 0.0050821 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-48_0_4_load_15 | 7 | 0.036744 | 0.0092088 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-48_0_4_load_22 | 10 | 0.011917 | 0.0029868 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-48_0_4_load_29 | 11 | 0.048115 | 0.012059 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-48_0_4_load_28 | 12 | 0.021948 | 0.0055006 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-48_0_4_load_33 | 13 | 0.071323 | 0.017875 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-48_0_4_load_32 | 16 | 0.050239 | 0.012591 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-48_0_4_load_8 | 18 | 0.022136 | 0.0055477 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-48_0_4_load_21 | 19 | 0.011922 | 0.0029879 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-48_0_4_load_31 | 21 | 0.047264 | 0.011846 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-48_0_4_load_17 | 25 | 0.012786 | 0.0032045 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-48_0_4_load_18 | 26 | 0.0067032 | 0.00168 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-48_0_4_load_19 | 27 | 0.01576 | 0.0039498 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-48_0_4_load_23 | 28 | 0.027235 | 0.0068257 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-48_0_4_line_0 |  | 0 | 1 | 0.020317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-48_0_4_line_1 |  | 0 | 2 | 0.015571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-48_0_4_line_2 |  | 1 | 3 | 0.0008418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2196-48_0_4_line_3 |  | 2 | 4 | 0.025878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-48_0_4_line_4 |  | 3 | 5 | 0.038419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-48_0_4_line_5 |  | 3 | 6 | 0.026515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2196-48_0_4_line_6 |  | 4 | 7 | 0.011221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-48_0_4_line_7 |  | 5 | 11 | 0.02902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-48_0_4_line_8 |  | 5 | 12 | 0.0097003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-48_0_4_line_9 |  | 6 | 13 | 0.025043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-48_0_4_line_10 |  | 6 | 14 | 0.032293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2196-48_0_4_line_11 |  | 7 | 15 | 0.009828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-48_0_4_line_12 |  | 8 | 9 | 0.03041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-48_0_4_line_13 |  | 8 | 10 | 0.016739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-48_0_4_line_14 |  | 9 | 17 | 0.003987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-48_0_4_line_15 |  | 9 | 18 | 0.024526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-48_0_4_line_16 |  | 10 | 19 | 0.01703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-48_0_4_line_17 |  | 13 | 23 | 0.017108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-48_0_4_line_18 |  | 14 | 20 | 0.003484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2196-48_0_4_line_19 |  | 14 | 18 | 0.017839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-48_0_4_line_20 |  | 15 | 25 | 0.023755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-48_0_4_line_21 |  | 15 | 26 | 0.026743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-48_0_4_line_22 |  | 16 | 17 | 0.010388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-48_0_4_line_23 |  | 20 | 21 | 0.012504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-48_0_4_line_24 |  | 22 | 23 | 0.013538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-48_0_4_line_25 |  | 22 | 24 | 0.4016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-48_0_4_line_26 |  | 24 | 28 | 0.013208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-48_0_4_line_27 |  | 26 | 27 | 0.014358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-48_0_4_trafo_1 | 0.63 MVA 20/0.4 kV | 29 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2578230.0116 | 1182720.5723 | 2578213.0758 | 1182731.7948
1 | 2578242.9917 | 1182711.9709 | 2578230.0116 | 1182720.5723
2 | 2578213.0758 | 1182731.7948 | 2578212.3741 | 1182732.2598
3 | 2578242.9917 | 1182711.9709 | 2578258.3716 | 1182732.7828
4 | 2578212.3741 | 1182732.2598 | 2578199.4722 | 1182713.675 | 2578204.8616 | 1182709.2864 | 2578210.3187 | 1182704.6085 | 2578211.8659 | 1182703.9025
5 | 2578190.2719 | 1182746.9482 | 2578202.5595 | 1182739.5216 | 2578212.3741 | 1182732.2598
6 | 2578265.0405 | 1182741.8072 | 2578258.3716 | 1182732.7828
7 | 2578211.8659 | 1182703.9025 | 2578201.2011 | 1182689.534 | 2578190.7399 | 1182693.3221
8 | 2578211.8659 | 1182703.9025 | 2578220.0238 | 1182698.6541
9 | 2578190.2719 | 1182746.9482 | 2578180.5445 | 1182738.4015 | 2578174.157 | 1182732.8886 | 2578171.3886 | 1182730.4992
10 | 2578190.2719 | 1182746.9482 | 2578199.6206 | 1182754.2845 | 2578215.8821 | 1182766.7093
11 | 2578270.8815 | 1182749.7112 | 2578265.0405 | 1182741.8072
12 | 2578274.05 | 1182810.5312 | 2578249.7203 | 1182792.1992
13 | 2578274.05 | 1182810.5312 | 2578283.7173 | 1182796.8665
14 | 2578249.7203 | 1182792.1992 | 2578247.3653 | 1182795.4206
15 | 2578249.7203 | 1182792.1992 | 2578230.1309 | 1182777.4427
16 | 2578293.5531 | 1182782.9637 | 2578283.7173 | 1182796.8665
17 | 2578157.9698 | 1182719.9411 | 2578162.9214 | 1182723.1914 | 2578171.3886 | 1182730.4992
18 | 2578215.8821 | 1182766.7093 | 2578213.8004 | 1182769.5073
19 | 2578215.8821 | 1182766.7093 | 2578230.1309 | 1182777.4427
20 | 2578270.8815 | 1182749.7112 | 2578274.5876 | 1182754.8003 | 2578275.0169 | 1182759.4901 | 2578266.8607 | 1182769.3138
21 | 2578270.8815 | 1182749.7112 | 2578280.2758 | 1182742.3287 | 2578284.973 | 1182738.6319 | 2578291.9432 | 1182740.652 | 2578293.2528 | 1182741.5007
22 | 2578247.3653 | 1182795.4206 | 2578245.7928 | 1182797.5719 | 2578241.2325 | 1182803.8051
23 | 2578213.8004 | 1182769.5073 | 2578206.3371 | 1182779.5393
24 | 2578146.6354 | 1182712.4898 | 2578157.9698 | 1182719.9411
25 | 2578146.6354 | 1182712.4898 | 2578143.4749 | 1182710.467 | 2578133.8258 | 1182706.6337 | 2578148.01 | 1182700.0561 | 2578264.8047 | 1182661.8098 | 2578330.5005 | 1182640.2931 | 2578332.8359 | 1182637.9612 | 2578333.3082 | 1182635.5583 | 2578332.6318 | 1182632.2145 | 2578321.0961 | 1182634.4798 | 2578250.6464 | 1182648.3211 | 2578234.1883 | 1182651.1158 | 2578215.2046 | 1182654.3423 | 2578165.0108 | 1182664.1086
26 | 2578165.0108 | 1182664.1086 | 2578152.0504 | 1182666.6516
27 | 2578304.941 | 1182749.8247 | 2578297.8971 | 1182744.5102 | 2578293.2528 | 1182741.5007

## bus_geodata
| x | y | coords
0 | 2578230.0116 | 1182720.5723
1 | 2578213.0758 | 1182731.7948
2 | 2578242.9917 | 1182711.9709
3 | 2578212.3741 | 1182732.2598
4 | 2578258.3716 | 1182732.7828
5 | 2578211.8659 | 1182703.9025
6 | 2578190.2719 | 1182746.9482
7 | 2578265.0405 | 1182741.8072
8 | 2578274.05 | 1182810.5312
9 | 2578249.7203 | 1182792.1992
10 | 2578283.7173 | 1182796.8665
11 | 2578190.7399 | 1182693.3221
12 | 2578220.0238 | 1182698.6541
13 | 2578171.3886 | 1182730.4992
14 | 2578215.8821 | 1182766.7093
15 | 2578270.8815 | 1182749.7112
16 | 2578241.2325 | 1182803.8051
17 | 2578247.3653 | 1182795.4206
18 | 2578230.1309 | 1182777.4427
19 | 2578293.5531 | 1182782.9637
20 | 2578213.8004 | 1182769.5073
21 | 2578206.3371 | 1182779.5393
22 | 2578146.6354 | 1182712.4898
23 | 2578157.9698 | 1182719.9411
24 | 2578165.0108 | 1182664.1086
25 | 2578266.8607 | 1182769.3138
26 | 2578293.2528 | 1182741.5007
27 | 2578304.941 | 1182749.8247
28 | 2578152.0504 | 1182666.6516
29 | 2578212.3741 | 1182732.2598

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99803 | -0.037726 | 0.014054 | 0.0035224
1 | 1 | 0 | -0.42242 | -0.10636
2 | 0.99672 | -0.062902 | 0 | 0
3 | 0.99992 | -0.0015266 | 0 | 0
4 | 0.99454 | -0.10489 | 0.020278 | 0.0050821
5 | 0.99747 | -0.048566 | 0 | 0
6 | 0.99797 | -0.038894 | 0 | 0
7 | 0.9938 | -0.11913 | 0.036744 | 0.0092088
8 | 0.99196 | -0.15466 | 0 | 0
9 | 0.99262 | -0.14182 | 0 | 0
10 | 0.99159 | -0.16173 | 0.011917 | 0.0029868
11 | 0.9962 | -0.073058 | 0.048115 | 0.012059
12 | 0.99728 | -0.052296 | 0.021948 | 0.0055006
13 | 0.99571 | -0.082193 | 0.071323 | 0.017875
14 | 0.99585 | -0.079525 | 0 | 0
15 | 0.99349 | -0.12525 | 0 | 0
16 | 0.99196 | -0.15461 | 0.050239 | 0.012591
17 | 0.99244 | -0.14537 | 0 | 0
18 | 0.99428 | -0.10974 | 0.022136 | 0.0055477
19 | 0.99141 | -0.16533 | 0.011922 | 0.0029879
20 | 0.9957 | -0.082419 | 0 | 0
21 | 0.99516 | -0.092815 | 0.047264 | 0.011846
22 | 0.99494 | -0.096885 | 0 | 0
23 | 0.99528 | -0.090392 | 0 | 0
24 | 0.98486 | -0.29148 | 0 | 0
25 | 0.99321 | -0.13061 | 0.012786 | 0.0032045
26 | 0.99294 | -0.13586 | 0.0067032 | 0.00168
27 | 0.99273 | -0.13987 | 0.01576 | 0.0039498
28 | 0.98453 | -0.29795 | 0.027235 | 0.0068257
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.1067 | -0.026885 | 0.10689 | 0.027008 | 0.00019293 | 0.00012321 | 0.15913 | 0.15913 | 0.15913 | 0.99803 | -0.037726 | 1 | 0 | 43.718
1 | 0.092644 | 0.023363 | -0.092533 | -0.023292 | 0.00011149 | 7.1152e-05 | 0.13818 | 0.13818 | 0.13818 | 0.99803 | -0.037726 | 0.99672 | -0.062902 | 37.9614
2 | 0.31388 | 0.079349 | -0.31386 | -0.079335 | 2.2978e-05 | 1.4673e-05 | 0.4673 | 0.4673 | 0.4673 | 1 | 0 | 0.99992 | -0.0015266 | 42.7932
3 | 0.092533 | 0.023292 | -0.092348 | -0.023173 | 0.00018529 | 0.00011825 | 0.13818 | 0.13818 | 0.13818 | 0.99672 | -0.062902 | 0.99454 | -0.10489 | 37.9614
4 | 0.070281 | 0.017698 | -0.070123 | -0.017597 | 0.00015768 | 0.00010041 | 0.10462 | 0.10462 | 0.10462 | 0.99992 | -0.0015266 | 0.99747 | -0.048566 | 28.7409
5 | 0.24358 | 0.061637 | -0.24314 | -0.061359 | 0.00043597 | 0.00027798 | 0.36268 | 0.36269 | 0.36269 | 0.99992 | -0.0015266 | 0.99797 | -0.038894 | 33.2129
6 | 0.07207 | 0.018091 | -0.072021 | -0.01806 | 4.8936e-05 | 3.1174e-05 | 0.10784 | 0.10784 | 0.10784 | 0.99454 | -0.10489 | 0.9938 | -0.11913 | 29.6264
7 | 0.048172 | 0.012094 | -0.048115 | -0.012059 | 5.621e-05 | 3.5596e-05 | 0.071869 | 0.07187 | 0.07187 | 0.99747 | -0.048566 | 0.9962 | -0.073058 | 19.7444
8 | 0.021951 | 0.0055029 | -0.021948 | -0.0055006 | 3.9009e-06 | 2.37e-06 | 0.032747 | 0.032747 | 0.032747 | 0.99747 | -0.048566 | 0.99728 | -0.052296 | 8.9965
9 | 0.099046 | 0.025007 | -0.098841 | -0.024876 | 0.000205 | 0.00013087 | 0.14775 | 0.14775 | 0.14775 | 0.99797 | -0.038894 | 0.99571 | -0.082193 | 40.5898
10 | 0.1441 | 0.036352 | -0.14382 | -0.036174 | 0.00027973 | 0.00017818 | 0.21494 | 0.21494 | 0.21494 | 0.99797 | -0.038894 | 0.99585 | -0.079525 | 29.5246
11 | 0.035277 | 0.0088512 | -0.035267 | -0.0088448 | 1.0284e-05 | 6.4544e-06 | 0.052824 | 0.052824 | 0.052824 | 0.9938 | -0.11913 | 0.99349 | -0.12525 | 14.5121
12 | -0.023849 | -0.0059806 | 0.023864 | 0.0059896 | 1.4596e-05 | 8.9489e-06 | 0.035777 | 0.035777 | 0.035777 | 0.99196 | -0.15466 | 0.99262 | -0.14182 | 9.8288
13 | 0.023849 | 0.0059806 | -0.023841 | -0.0059757 | 8.0344e-06 | 4.926e-06 | 0.035777 | 0.035777 | 0.035777 | 0.99196 | -0.15466 | 0.99159 | -0.16173 | 9.8288
14 | 0.05027 | 0.012611 | -0.050262 | -0.012605 | 8.4917e-06 | 5.3831e-06 | 0.075363 | 0.075363 | 0.075363 | 0.99262 | -0.14182 | 0.99244 | -0.14537 | 20.7041
15 | -0.074134 | -0.0186 | 0.074247 | 0.018673 | 0.0001136 | 7.2388e-05 | 0.11114 | 0.11114 | 0.11114 | 0.99262 | -0.14182 | 0.99428 | -0.10974 | 30.5328
16 | 0.011924 | 0.0029889 | -0.011922 | -0.0029879 | 2.0447e-06 | 1.089e-06 | 0.017893 | 0.017893 | 0.017893 | 0.99159 | -0.16173 | 0.99141 | -0.16533 | 4.9158
17 | 0.027518 | 0.0070011 | -0.027507 | -0.0069943 | 1.0869e-05 | 6.7336e-06 | 0.04116 | 0.04116 | 0.04116 | 0.99571 | -0.082193 | 0.99528 | -0.090392 | 11.3078
18 | 0.047294 | 0.011865 | -0.047288 | -0.01186 | 6.5254e-06 | 4.1309e-06 | 0.070672 | 0.070672 | 0.070672 | 0.99585 | -0.079525 | 0.9957 | -0.082419 | 19.4154
19 | 0.096522 | 0.024309 | -0.096383 | -0.02422 | 0.00013923 | 8.8876e-05 | 0.14427 | 0.14427 | 0.14427 | 0.99585 | -0.079525 | 0.99428 | -0.10974 | 39.6337
20 | 0.012789 | 0.0032063 | -0.012786 | -0.0032045 | 3.2689e-06 | 1.7846e-06 | 0.019156 | 0.019156 | 0.019156 | 0.99349 | -0.12525 | 0.99321 | -0.13061 | 5.2627
21 | 0.022478 | 0.0056385 | -0.022466 | -0.0056315 | 1.1368e-05 | 6.9293e-06 | 0.033668 | 0.033668 | 0.033668 | 0.99349 | -0.12525 | 0.99294 | -0.13586 | 9.2495
22 | -0.050239 | -0.012591 | 0.050262 | 0.012605 | 2.2125e-05 | 1.4026e-05 | 0.075363 | 0.075363 | 0.075363 | 0.99196 | -0.15461 | 0.99244 | -0.14537 | 20.7041
23 | 0.047288 | 0.01186 | -0.047264 | -0.011846 | 2.3419e-05 | 1.4826e-05 | 0.070672 | 0.070672 | 0.070672 | 0.9957 | -0.082419 | 0.99516 | -0.092815 | 19.4154
24 | -0.027498 | -0.006989 | 0.027507 | 0.0069943 | 8.6009e-06 | 5.3287e-06 | 0.04116 | 0.04116 | 0.04116 | 0.99494 | -0.096885 | 0.99528 | -0.090392 | 11.3078
25 | 0.027498 | 0.006989 | -0.027243 | -0.0068309 | 0.00025515 | 0.00015813 | 0.04116 | 0.041162 | 0.041162 | 0.99494 | -0.096885 | 0.98486 | -0.29148 | 11.3083
26 | 0.027243 | 0.0068309 | -0.027235 | -0.0068257 | 8.3917e-06 | 5.2027e-06 | 0.041162 | 0.041162 | 0.041162 | 0.98486 | -0.29148 | 0.98453 | -0.29795 | 11.3083
27 | 0.015763 | 0.0039516 | -0.01576 | -0.0039498 | 3.0046e-06 | 1.7373e-06 | 0.023623 | 0.023623 | 0.023623 | 0.99294 | -0.13586 | 0.99273 | -0.13987 | 6.4898

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43746 | 0.11013

## res_load
| p_mw | q_mvar
0 | 0.014054 | 0.0035224
1 | 0.015036 | 0.0037685
2 | 0.020278 | 0.0050821
3 | 0.036744 | 0.0092088
4 | 0.011917 | 0.0029868
5 | 0.048115 | 0.012059
6 | 0.021948 | 0.0055006
7 | 0.071323 | 0.017875
8 | 0.050239 | 0.012591
9 | 0.022136 | 0.0055477
10 | 0.011922 | 0.0029879
11 | 0.047264 | 0.011846
12 | 0.012786 | 0.0032045
13 | 0.0067032 | 0.00168
14 | 0.01576 | 0.0039498
15 | 0.027235 | 0.0068257

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1