## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-51_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-51_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2196-51_0_6_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_2196-51_0_6_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2196-51_0_6_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_2196-51_0_6_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_2196-51_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2196-51_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2196-51_0_6_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_2196-51_0_6_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_2196-51_0_6_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_2196-51_0_6_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_2196-51_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2196-51_0_6_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_2196-51_0_6_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2196-51_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2196-51_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2196-51_0_6_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2196-51_0_6_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2196-51_0_6_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2196-51_0_6_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_2196-51_0_6_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_2196-51_0_6_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_2196-51_0_6_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_2196-51_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2196-51_0_6_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2196-51_0_6_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_2196-51_0_6_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_2196-51_0_6_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2196-51_0_6_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2196-51_0_6_node_31 | 0.4 | n |  | TRUE
31 | bus_MV_507_0_node_79 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-51_0_6_load_0 | 0 | 0.0054224 | 0.001359 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-51_0_6_load_33 | 5 | 0.094272 | 0.023627 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-51_0_6_load_19 | 8 | 0.032621 | 0.0081755 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-51_0_6_load_29 | 9 | 0.084172 | 0.021096 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-51_0_6_load_34 | 10 | 0.088228 | 0.022112 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-51_0_6_load_32 | 11 | 0.012574 | 0.0031514 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-51_0_6_load_24 | 14 | 0.0058382 | 0.0014632 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-51_0_6_load_14 | 16 | 0.043162 | 0.010817 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-51_0_6_load_11 | 17 | 0.011064 | 0.0027729 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-51_0_6_load_23 | 20 | 0.01101 | 0.0027595 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-51_0_6_load_20 | 21 | 0.0060633 | 0.0015196 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-51_0_6_load_27 | 23 | 0.038709 | 0.0097014 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-51_0_6_load_21 | 25 | 0.011187 | 0.0028036 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-51_0_6_load_17 | 28 | 0.041581 | 0.010421 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-51_0_6_load_30 | 29 | 0.010425 | 0.0026127 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-51_0_6_load_31 | 30 | 0.082404 | 0.020652 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-51_0_6_line_0 |  | 0 | 1 | 0.0079918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-51_0_6_line_1 |  | 1 | 2 | 0.007102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-51_0_6_line_2 |  | 2 | 11 | 0.0046979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-51_0_6_line_3 |  | 3 | 4 | 0.047219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-51_0_6_line_4 |  | 3 | 5 | 0.024989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-51_0_6_line_5 |  | 4 | 10 | 0.023341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-51_0_6_line_6 |  | 5 | 7 | 0.030074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2196-51_0_6_line_7 |  | 6 | 7 | 0.11367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-51_0_6_line_8 |  | 6 | 8 | 0.011528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-51_0_6_line_9 |  | 7 | 9 | 0.010932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2196-51_0_6_line_10 |  | 8 | 24 | 0.026519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-51_0_6_line_11 |  | 9 | 22 | 0.035302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2196-51_0_6_line_12 |  | 11 | 27 | 0.0076607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-51_0_6_line_13 |  | 12 | 13 | 0.00756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-51_0_6_line_14 |  | 12 | 14 | 0.030549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-51_0_6_line_15 |  | 13 | 25 | 0.01115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-51_0_6_line_16 |  | 15 | 16 | 0.037301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2196-51_0_6_line_17 |  | 15 | 17 | 0.062106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2196-51_0_6_line_18 |  | 16 | 23 | 0.029525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2196-51_0_6_line_19 |  | 17 | 18 | 0.02656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2196-51_0_6_line_20 |  | 18 | 19 | 0.022677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2196-51_0_6_line_21 |  | 19 | 20 | 0.029501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-51_0_6_line_22 |  | 19 | 21 | 0.01386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-51_0_6_line_23 |  | 20 | 26 | 0.012279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-51_0_6_line_24 |  | 21 | 25 | 0.0052222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-51_0_6_line_25 |  | 22 | 23 | 0.033762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2196-51_0_6_line_26 |  | 24 | 28 | 0.015414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-51_0_6_line_27 |  | 26 | 27 | 0.019772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-51_0_6_line_28 |  | 27 | 29 | 0.024928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-51_0_6_line_29 |  | 29 | 30 | 0.027914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-51_0_6_trafo_28 | 0.63 MVA 20/0.4 kV | 31 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2578820.0301 | 1183618.3109 | 2578825.9643 | 1183623.664
1 | 2578820.0301 | 1183618.3109 | 2578813.0969 | 1183619.9364
2 | 2578813.0969 | 1183619.9364 | 2578809.2528 | 1183620.8394 | 2578808.5286 | 1183621.0311
3 | 2578813.27 | 1183715.9413 | 2578820.0775 | 1183709.0469 | 2578850.7384 | 1183725.4911 | 2578852.1422 | 1183723.1405
4 | 2578813.27 | 1183715.9413 | 2578797.4332 | 1183735.2714
5 | 2578852.1422 | 1183723.1405 | 2578864.1418 | 1183703.1202
6 | 2578776.7145 | 1183757.0148 | 2578791.3198 | 1183742.7332 | 2578797.4332 | 1183735.2714
7 | 2578704.983 | 1183788.9981 | 2578714.65 | 1183774.9229 | 2578717.9852 | 1183772.5987 | 2578720.59 | 1183773.1119 | 2578725.0444 | 1183776.42 | 2578730.2274 | 1183782.816 | 2578736.8261 | 1183785.9385 | 2578740.1414 | 1183788.7393 | 2578753.0413 | 1183788.5932 | 2578759.2829 | 1183787.8929 | 2578772.6728 | 1183783.8987 | 2578771.2829 | 1183779.4347 | 2578767.7345 | 1183771.1652 | 2578768.2266 | 1183765.7384 | 2578776.7145 | 1183757.0148
8 | 2578704.983 | 1183788.9981 | 2578695.3226 | 1183782.7067
9 | 2578776.7145 | 1183757.0148 | 2578777.5841 | 1183746.1171
10 | 2578673.1005 | 1183768.2345 | 2578695.3226 | 1183782.7067
11 | 2578772.9106 | 1183719.8645 | 2578773.531 | 1183722.6082 | 2578773.9964 | 1183724.6743 | 2578782.8994 | 1183725.343 | 2578777.5841 | 1183746.1171
12 | 2578801.1231 | 1183622.9916 | 2578808.5286 | 1183621.0311
13 | 2578781.9054 | 1183576.8359 | 2578775.0697 | 1183580.1064
14 | 2578781.9054 | 1183576.8359 | 2578760.7547 | 1183554.7933
15 | 2578775.0697 | 1183580.1064 | 2578765.0133 | 1183584.9229
16 | 2578685.5351 | 1183676.32 | 2578700.9712 | 1183691.6173 | 2578713.3431 | 1183701.0689
17 | 2578685.5351 | 1183676.32 | 2578720.095 | 1183624.7182
18 | 2578713.3431 | 1183701.0689 | 2578718.1782 | 1183704.7627 | 2578738.0485 | 1183713.4297 | 2578739.7669 | 1183713.8219
19 | 2578734.875 | 1183602.6501 | 2578720.095 | 1183624.7182
20 | 2578747.8031 | 1183593.1658 | 2578744.283 | 1183588.5981 | 2578734.875 | 1183602.6501
21 | 2578747.8031 | 1183593.1658 | 2578773.1769 | 1183608.2148
22 | 2578747.8031 | 1183593.1658 | 2578760.3034 | 1183587.1787
23 | 2578783.6961 | 1183614.5492 | 2578777.9126 | 1183611.0235 | 2578773.1769 | 1183608.2148
24 | 2578760.3034 | 1183587.1787 | 2578765.0133 | 1183584.9229
25 | 2578772.9106 | 1183719.8645 | 2578762.4115 | 1183718.9903 | 2578739.7669 | 1183713.8219
26 | 2578673.1005 | 1183768.2345 | 2578663.5505 | 1183756.1358
27 | 2578801.1231 | 1183622.9916 | 2578797.5889 | 1183623.0375 | 2578783.6961 | 1183614.5492
28 | 2578801.1231 | 1183622.9916 | 2578798.8623 | 1183633.394 | 2578792.4299 | 1183646.1469
29 | 2578779.859 | 1183671.07 | 2578792.4299 | 1183646.1469

## bus_geodata
| x | y | coords
0 | 2578825.9643 | 1183623.664
1 | 2578820.0301 | 1183618.3109
2 | 2578813.0969 | 1183619.9364
3 | 2578813.27 | 1183715.9413
4 | 2578852.1422 | 1183723.1405
5 | 2578797.4332 | 1183735.2714
6 | 2578704.983 | 1183788.9981
7 | 2578776.7145 | 1183757.0148
8 | 2578695.3226 | 1183782.7067
9 | 2578777.5841 | 1183746.1171
10 | 2578864.1418 | 1183703.1202
11 | 2578808.5286 | 1183621.0311
12 | 2578781.9054 | 1183576.8359
13 | 2578775.0697 | 1183580.1064
14 | 2578760.7547 | 1183554.7933
15 | 2578685.5351 | 1183676.32
16 | 2578713.3431 | 1183701.0689
17 | 2578720.095 | 1183624.7182
18 | 2578734.875 | 1183602.6501
19 | 2578747.8031 | 1183593.1658
20 | 2578773.1769 | 1183608.2148
21 | 2578760.3034 | 1183587.1787
22 | 2578772.9106 | 1183719.8645
23 | 2578739.7669 | 1183713.8219
24 | 2578673.1005 | 1183768.2345
25 | 2578765.0133 | 1183584.9229
26 | 2578783.6961 | 1183614.5492
27 | 2578801.1231 | 1183622.9916
28 | 2578663.5505 | 1183756.1358
29 | 2578792.4299 | 1183646.1469
30 | 2578779.859 | 1183671.07
31 | 2578813.27 | 1183715.9413

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98138 | -0.35741 | 0.0054224 | 0.001359
1 | 0.98142 | -0.35663 | 0 | 0
2 | 0.98146 | -0.35593 | 0 | 0
3 | 0.99092 | -0.17406 | 0 | 0
4 | 0.98708 | -0.2483 | 0 | 0
5 | 0.99295 | -0.135 | 0.094272 | 0.023627
6 | 0.98771 | -0.23613 | 0 | 0
7 | 0.99547 | -0.086613 | 0 | 0
8 | 0.98692 | -0.25142 | 0.032621 | 0.0081755
9 | 0.99632 | -0.070173 | 0.084172 | 0.021096
10 | 0.98519 | -0.28521 | 0.088228 | 0.022112
11 | 0.98148 | -0.35547 | 0.012574 | 0.0031514
12 | 0.98776 | -0.23382 | 0 | 0
13 | 0.9878 | -0.23303 | 0 | 0
14 | 0.9876 | -0.23701 | 0.0058382 | 0.0014632
15 | 0.99393 | -0.11533 | 0 | 0
16 | 0.99573 | -0.081174 | 0.043162 | 0.010817
17 | 0.99094 | -0.17248 | 0.011064 | 0.0027729
18 | 0.98976 | -0.19529 | 0 | 0
19 | 0.98824 | -0.22457 | 0 | 0
20 | 0.9849 | -0.28894 | 0.01101 | 0.0027595
21 | 0.98794 | -0.23028 | 0.0060633 | 0.0015196
22 | 1 | 0 | -0.58648 | -0.14893
23 | 0.99754 | -0.046777 | 0.038709 | 0.0097014
24 | 0.98591 | -0.27118 | 0 | 0
25 | 0.98786 | -0.23187 | 0.011187 | 0.0028036
26 | 0.98364 | -0.31342 | 0 | 0
27 | 0.98161 | -0.35298 | 0 | 0
28 | 0.98532 | -0.28268 | 0.041581 | 0.010421
29 | 0.97946 | -0.39493 | 0.010425 | 0.0026127
30 | 0.97733 | -0.43681 | 0.082404 | 0.020652
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0054224 | -0.001359 | 0.0054226 | 0.001359 | 2.0258e-07 | 2.8667e-08 | 0.0082217 | 0.0082216 | 0.0082217 | 0.98138 | -0.35741 | 0.98142 | -0.35663 | 2.2587
1 | -0.0054226 | -0.001359 | 0.0054228 | 0.001359 | 1.8002e-07 | 2.5467e-08 | 0.0082216 | 0.0082216 | 0.0082216 | 0.98142 | -0.35663 | 0.98146 | -0.35593 | 2.2587
2 | -0.0054228 | -0.001359 | 0.0054229 | 0.001359 | 1.1908e-07 | 1.6842e-08 | 0.0082216 | 0.0082216 | 0.0082216 | 0.98146 | -0.35593 | 0.98148 | -0.35547 | 2.2587
3 | 0.088698 | 0.022412 | -0.088383 | -0.022211 | 0.00031444 | 0.00020064 | 0.13326 | 0.13326 | 0.13326 | 0.99092 | -0.17406 | 0.98708 | -0.2483 | 36.6094
4 | -0.088698 | -0.022412 | 0.088864 | 0.022518 | 0.00016641 | 0.00010618 | 0.13326 | 0.13326 | 0.13326 | 0.99092 | -0.17406 | 0.99295 | -0.135 | 36.6094
5 | 0.088383 | 0.022211 | -0.088228 | -0.022112 | 0.00015543 | 9.9179e-05 | 0.13326 | 0.13326 | 0.13326 | 0.98708 | -0.2483 | 0.98519 | -0.28521 | 36.6095
6 | -0.18314 | -0.046145 | 0.18356 | 0.046416 | 0.00042499 | 0.00027121 | 0.27453 | 0.27453 | 0.27453 | 0.99295 | -0.135 | 0.99547 | -0.086613 | 37.7105
7 | -0.074317 | -0.01867 | 0.074852 | 0.019011 | 0.00053447 | 0.00034059 | 0.11198 | 0.11198 | 0.11198 | 0.98771 | -0.23613 | 0.99547 | -0.086613 | 30.7632
8 | 0.074317 | 0.01867 | -0.074263 | -0.018636 | 5.4208e-05 | 3.4546e-05 | 0.11198 | 0.11198 | 0.11198 | 0.98771 | -0.23613 | 0.98692 | -0.25142 | 30.7632
9 | -0.25841 | -0.065427 | 0.25862 | 0.065557 | 0.00020415 | 0.00013023 | 0.38651 | 0.38651 | 0.38651 | 0.99547 | -0.086613 | 0.99632 | -0.070173 | 35.3946
10 | 0.041643 | 0.01046 | -0.041603 | -0.010435 | 3.9213e-05 | 2.4758e-05 | 0.062794 | 0.062795 | 0.062795 | 0.98692 | -0.25142 | 0.98591 | -0.27118 | 17.2512
11 | -0.34279 | -0.086653 | 0.34395 | 0.087392 | 0.0011578 | 0.00073959 | 0.51222 | 0.51222 | 0.51222 | 0.99632 | -0.070173 | 1 | 0 | 46.9067
12 | -0.017997 | -0.0045104 | 0.017999 | 0.0045117 | 2.1387e-06 | 1.2719e-06 | 0.027285 | 0.027285 | 0.027285 | 0.98148 | -0.35547 | 0.98161 | -0.35298 | 7.4959
13 | -0.0058391 | -0.0014634 | 0.0058393 | 0.0014634 | 2.1936e-07 | 4.3618e-08 | 0.0087964 | 0.0087963 | 0.0087964 | 0.98776 | -0.23382 | 0.9878 | -0.23303 | 2.4166
14 | 0.0058391 | 0.0014634 | -0.0058382 | -0.0014632 | 8.8642e-07 | 1.7635e-07 | 0.0087964 | 0.0087965 | 0.0087965 | 0.98776 | -0.23382 | 0.9876 | -0.23701 | 2.4166
15 | -0.0058393 | -0.0014634 | 0.0058397 | 0.0014635 | 3.2353e-07 | 6.4316e-08 | 0.0087963 | 0.0087963 | 0.0087963 | 0.9878 | -0.23303 | 0.98786 | -0.23187 | 2.4166
16 | -0.15787 | -0.040294 | 0.15813 | 0.04046 | 0.00026104 | 0.00016561 | 0.23661 | 0.23661 | 0.23661 | 0.99393 | -0.11533 | 0.99573 | -0.081174 | 21.6676
17 | 0.15787 | 0.040294 | -0.15744 | -0.040018 | 0.00043462 | 0.00027575 | 0.23661 | 0.23661 | 0.23661 | 0.99393 | -0.11533 | 0.99094 | -0.17248 | 21.6677
18 | -0.2013 | -0.051277 | 0.20163 | 0.05149 | 0.00033463 | 0.00021301 | 0.30111 | 0.30111 | 0.30111 | 0.99573 | -0.081174 | 0.99754 | -0.046777 | 27.5742
19 | 0.14637 | 0.037246 | -0.14621 | -0.037144 | 0.00016069 | 0.00010181 | 0.22 | 0.22 | 0.22 | 0.99094 | -0.17248 | 0.98976 | -0.19529 | 20.1464
20 | 0.14621 | 0.037144 | -0.14601 | -0.037013 | 0.00020579 | 0.00013113 | 0.22 | 0.22 | 0.22 | 0.98976 | -0.19529 | 0.98824 | -0.22457 | 30.2196
21 | 0.12291 | 0.031221 | -0.12253 | -0.030979 | 0.00037953 | 0.00024252 | 0.18522 | 0.18522 | 0.18522 | 0.98824 | -0.22457 | 0.9849 | -0.28894 | 50.8846
22 | 0.023097 | 0.0057913 | -0.023091 | -0.0057875 | 6.2868e-06 | 3.846e-06 | 0.034779 | 0.034779 | 0.034779 | 0.98824 | -0.22457 | 0.98794 | -0.23028 | 9.5547
23 | 0.11152 | 0.028219 | -0.11139 | -0.028136 | 0.00013087 | 8.3602e-05 | 0.16859 | 0.16859 | 0.16859 | 0.9849 | -0.28894 | 0.98364 | -0.31342 | 46.3146
24 | 0.017028 | 0.0042679 | -0.017026 | -0.0042671 | 1.2881e-06 | 7.5752e-07 | 0.025647 | 0.025647 | 0.025647 | 0.98794 | -0.23028 | 0.98786 | -0.23187 | 7.0458
25 | 0.24088 | 0.061538 | -0.24034 | -0.061192 | 0.00054347 | 0.00034649 | 0.35885 | 0.35885 | 0.35885 | 1 | 0 | 0.99754 | -0.046777 | 32.8619
26 | 0.041603 | 0.010435 | -0.041581 | -0.010421 | 2.2792e-05 | 1.439e-05 | 0.062795 | 0.062795 | 0.062795 | 0.98591 | -0.27118 | 0.98532 | -0.28268 | 17.2513
27 | 0.11139 | 0.028136 | -0.11118 | -0.028001 | 0.00021073 | 0.00013462 | 0.16859 | 0.16859 | 0.16859 | 0.98364 | -0.31342 | 0.98161 | -0.35298 | 46.3146
28 | 0.09318 | 0.023489 | -0.092994 | -0.02337 | 0.00018664 | 0.00011914 | 0.1413 | 0.1413 | 0.1413 | 0.98161 | -0.35298 | 0.97946 | -0.39493 | 38.8188
29 | 0.082569 | 0.020758 | -0.082404 | -0.020652 | 0.00016477 | 0.0001051 | 0.12546 | 0.12546 | 0.12546 | 0.97946 | -0.39493 | 0.97733 | -0.43681 | 34.4679

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58648 | 0.14893

## res_load
| p_mw | q_mvar
0 | 0.0054224 | 0.001359
1 | 0.094272 | 0.023627
2 | 0.032621 | 0.0081755
3 | 0.084172 | 0.021096
4 | 0.088228 | 0.022112
5 | 0.012574 | 0.0031514
6 | 0.0058382 | 0.0014632
7 | 0.043162 | 0.010817
8 | 0.011064 | 0.0027729
9 | 0.01101 | 0.0027595
10 | 0.0060633 | 0.0015196
11 | 0.038709 | 0.0097014
12 | 0.011187 | 0.0028036
13 | 0.041581 | 0.010421
14 | 0.010425 | 0.0026127
15 | 0.082404 | 0.020652

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1