## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-56_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-56_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-56_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-56_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-56_0_6_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_2196-56_0_6_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_2196-56_0_6_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_2196-56_0_6_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_2196-56_0_6_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_2196-56_0_6_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_2196-56_0_6_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_2196-56_0_6_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2196-56_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2196-56_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2196-56_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2196-56_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2196-56_0_6_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_2196-56_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2196-56_0_6_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_2196-56_0_6_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2196-56_0_6_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2196-56_0_6_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2196-56_0_6_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2196-56_0_6_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2196-56_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2196-56_0_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2196-56_0_6_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_2196-56_0_6_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2196-56_0_6_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2196-56_0_6_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2196-56_0_6_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2196-56_0_6_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2196-56_0_6_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2196-56_0_6_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2196-56_0_6_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_2196-56_0_6_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_2196-56_0_6_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2196-56_0_6_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_2196-56_0_6_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_2196-56_0_6_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_2196-56_0_6_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_2196-56_0_6_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_2196-56_0_6_node_52 | 0.4 | n |  | TRUE
43 | bus_LV_2196-56_0_6_node_61 | 0.4 | n |  | TRUE
44 | bus_LV_2196-56_0_6_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_2196-56_0_6_node_51 | 0.4 | n |  | TRUE
46 | bus_LV_2196-56_0_6_node_58 | 0.4 | n |  | TRUE
47 | bus_LV_2196-56_0_6_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_2196-56_0_6_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_2196-56_0_6_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_2196-56_0_6_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_2196-56_0_6_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2196-56_0_6_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_2196-56_0_6_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_2196-56_0_6_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_2196-56_0_6_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_2196-56_0_6_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_2196-56_0_6_node_59 | 0.4 | n |  | TRUE
58 | bus_LV_2196-56_0_6_node_49 | 0.4 | n |  | TRUE
59 | bus_MV_382_0_node_82 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-56_0_6_load_0 | 0 | 0.0016803 | 0.00042112 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-56_0_6_load_1 | 1 | 0.0022176 | 0.00055577 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-56_0_6_load_2 | 2 | 0.00070685 | 0.00017715 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-56_0_6_load_28 | 4 | 0.0017556 | 0.00044 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-56_0_6_load_31 | 9 | 0.027221 | 0.0068224 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-56_0_6_load_41 | 10 | 0.0011075 | 0.00027757 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-56_0_6_load_5 | 11 | 0.0026511 | 0.00066443 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-56_0_6_load_6 | 12 | 0.0016367 | 0.00041019 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-56_0_6_load_7 | 13 | 0.025064 | 0.0062818 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-56_0_6_load_8 | 14 | 0.036766 | 0.0092143 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-56_0_6_load_9 | 15 | 0.0083695 | 0.0020976 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-56_0_6_load_43 | 16 | 0.00083675 | 0.00020971 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-56_0_6_load_42 | 18 | 0.00096763 | 0.00024251 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-56_0_6_load_16 | 19 | 0.0014816 | 0.00037133 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-56_0_6_load_17 | 20 | 0.0059644 | 0.0014948 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-56_0_6_load_10 | 21 | 0.0027984 | 0.00070134 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-56_0_6_load_11 | 22 | 0.001918 | 0.00048068 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-56_0_6_load_12 | 23 | 0.0018966 | 0.00047532 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-56_0_6_load_30 | 29 | 0.0021175 | 0.0005307 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-56_0_6_load_27 | 30 | 0.0029976 | 0.00075128 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-56_0_6_load_18 | 33 | 0.0042067 | 0.0010543 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-56_0_6_load_56 | 34 | 0.019739 | 0.0049471 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-56_0_6_load_57 | 35 | 0.040211 | 0.010078 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-56_0_6_load_20 | 36 | 0.0043151 | 0.0010815 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2196-56_0_6_load_55 | 38 | 0.022504 | 0.0056402 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2196-56_0_6_load_32 | 40 | 0.027746 | 0.0069537 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2196-56_0_6_load_34 | 41 | 0.039963 | 0.010016 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2196-56_0_6_load_61 | 43 | 0.0305 | 0.0076439 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2196-56_0_6_load_53 | 44 | 0.043205 | 0.010828 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2196-56_0_6_load_58 | 46 | 0.065456 | 0.016405 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2196-56_0_6_load_37 | 48 | 0.0089866 | 0.0022523 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2196-56_0_6_load_54 | 52 | 0.015862 | 0.0039753 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2196-56_0_6_load_46 | 53 | 0.0080936 | 0.0020284 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2196-56_0_6_load_44 | 54 | 0.010883 | 0.0027275 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2196-56_0_6_load_60 | 55 | 0.0080886 | 0.0020272 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2196-56_0_6_load_59 | 57 | 0.011447 | 0.002869 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2196-56_0_6_load_49 | 58 | 0.066392 | 0.016639 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-56_0_6_line_0 |  | 0 | 1 | 0.029891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-56_0_6_line_1 |  | 0 | 2 | 0.063784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-56_0_6_line_2 |  | 1 | 3 | 0.017857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-56_0_6_line_3 |  | 3 | 4 | 0.013807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-56_0_6_line_4 |  | 4 | 5 | 0.015426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-56_0_6_line_5 |  | 5 | 29 | 0.013157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-56_0_6_line_6 |  | 6 | 7 | 0.011086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-56_0_6_line_7 |  | 6 | 8 | 0.067648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2196-56_0_6_line_8 |  | 6 | 9 | 0.0045277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2196-56_0_6_line_9 |  | 7 | 43 | 0.072953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-56_0_6_line_10 |  | 8 | 10 | 0.015386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2196-56_0_6_line_11 |  | 9 | 40 | 0.038888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2196-56_0_6_line_12 |  | 10 | 18 | 0.029077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2196-56_0_6_line_13 |  | 11 | 12 | 0.027357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2196-56_0_6_line_14 |  | 11 | 13 | 0.024868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2196-56_0_6_line_15 |  | 12 | 14 | 0.0012295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2196-56_0_6_line_16 |  | 13 | 15 | 0.0025663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2196-56_0_6_line_17 |  | 14 | 16 | 0.025537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2196-56_0_6_line_18 |  | 15 | 17 | 0.011948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2196-56_0_6_line_19 |  | 16 | 18 | 0.03203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2196-56_0_6_line_20 |  | 17 | 19 | 0.023723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-56_0_6_line_21 |  | 17 | 20 | 0.021277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2196-56_0_6_line_22 |  | 20 | 25 | 0.032451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2196-56_0_6_line_23 |  | 21 | 22 | 0.022975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-56_0_6_line_24 |  | 21 | 23 | 0.028322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-56_0_6_line_25 |  | 22 | 24 | 0.031368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-56_0_6_line_26 |  | 23 | 25 | 0.0218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-56_0_6_line_27 |  | 24 | 26 | 0.013694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-56_0_6_line_28 |  | 24 | 27 | 0.090445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-56_0_6_line_29 |  | 25 | 28 | 0.041669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2196-56_0_6_line_30 |  | 26 | 29 | 0.049739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-56_0_6_line_31 |  | 27 | 30 | 0.018254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2196-56_0_6_line_32 |  | 28 | 34 | 0.047877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2196-56_0_6_line_33 |  | 28 | 35 | 0.046584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2196-56_0_6_line_34 |  | 30 | 31 | 0.032209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2196-56_0_6_line_35 |  | 31 | 32 | 0.02367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2196-56_0_6_line_36 |  | 32 | 33 | 0.0073314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2196-56_0_6_line_37 |  | 33 | 36 | 0.0086995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2196-56_0_6_line_38 |  | 34 | 38 | 0.042029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2196-56_0_6_line_39 |  | 37 | 38 | 0.053683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2196-56_0_6_line_40 |  | 37 | 39 | 0.009697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2196-56_0_6_line_41 |  | 39 | 56 | 0.032583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2196-56_0_6_line_42 |  | 39 | 54 | 0.052135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2196-56_0_6_line_43 |  | 40 | 41 | 0.057908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2196-56_0_6_line_44 |  | 41 | 42 | 0.00895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2196-56_0_6_line_45 |  | 42 | 44 | 0.033036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2196-56_0_6_line_46 |  | 42 | 45 | 0.016549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2196-56_0_6_line_47 |  | 44 | 51 | 0.028206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2196-56_0_6_line_48 |  | 45 | 46 | 0.09554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2196-56_0_6_line_49 |  | 45 | 47 | 0.012009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2196-56_0_6_line_50 |  | 47 | 58 | 0.029741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2196-56_0_6_line_51 |  | 48 | 49 | 0.0083816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2196-56_0_6_line_52 |  | 49 | 50 | 0.042085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2196-56_0_6_line_53 |  | 50 | 53 | 0.019698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2196-56_0_6_line_54 |  | 50 | 54 | 0.024372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2196-56_0_6_line_55 |  | 51 | 52 | 0.017723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2196-56_0_6_line_56 |  | 53 | 55 | 0.017791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2196-56_0_6_line_57 |  | 56 | 57 | 0.041538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-56_0_6_trafo_51 | 0.63 MVA 20/0.4 kV | 59 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2579896.9024 | 1184429.9627 | 2579883.3778 | 1184432.0213 | 2579872.5701 | 1184434.2589 | 2579867.532 | 1184435.4381
1 | 2579896.9024 | 1184429.9627 | 2579901.2288 | 1184429.3042 | 2579919.5211 | 1184428.431 | 2579947.8774 | 1184428.8358 | 2579960.6091 | 1184429.1457
2 | 2579850.2874 | 1184440.0594 | 2579862.3048 | 1184436.6615 | 2579867.532 | 1184435.4381
3 | 2579850.2874 | 1184440.0594 | 2579837.2498 | 1184444.6029
4 | 2579822.7211 | 1184449.7798 | 2579824.4207 | 1184449.0737 | 2579837.2498 | 1184444.6029
5 | 2579822.7211 | 1184449.7798 | 2579810.6266 | 1184454.9602
6 | 2580012.6382 | 1184528.626 | 2580022.0686 | 1184534.4975
7 | 2580000.5296 | 1184493.426 | 2580036.9007 | 1184512.3696 | 2580022.0686 | 1184534.4975
8 | 2580022.0686 | 1184534.4975 | 2580019.3583 | 1184538.1243
9 | 2579939.6874 | 1184526.3252 | 2580000.2278 | 1184526.3108 | 2580012.6382 | 1184528.626
10 | 2580000.5296 | 1184493.426 | 2579985.5046 | 1184490.1121
11 | 2580019.3583 | 1184538.1243 | 2579996.079 | 1184569.2752
12 | 2579985.5046 | 1184490.1121 | 2579977.2944 | 1184488.3013 | 2579966.5808 | 1184486.7365 | 2579957.083 | 1184485.8235 | 2579956.7829 | 1184485.8159
13 | 2579872.1543 | 1184498.1961 | 2579876.1534 | 1184496.3903 | 2579884.0814 | 1184493.5065 | 2579896.4284 | 1184490.5633 | 2579898.247 | 1184490.2818
14 | 2579872.1543 | 1184498.1961 | 2579867.1989 | 1184500.4337 | 2579860.3045 | 1184504.2701 | 2579853.9463 | 1184508.6939 | 2579851.0606 | 1184511.1581
15 | 2579898.247 | 1184490.2818 | 2579899.4621 | 1184490.0937
16 | 2579849.109 | 1184512.8246 | 2579851.0606 | 1184511.1581
17 | 2579924.8093 | 1184487.0773 | 2579909.641 | 1184488.5178 | 2579899.4621 | 1184490.0937
18 | 2579840.4558 | 1184521.057 | 2579847.3328 | 1184514.3414 | 2579849.109 | 1184512.8246
19 | 2579956.7829 | 1184485.8159 | 2579946.9691 | 1184485.5684 | 2579929.0594 | 1184486.6737 | 2579924.8093 | 1184487.0773
20 | 2579840.4558 | 1184521.057 | 2579828.9403 | 1184508.0669 | 2579827.598 | 1184506.1149 | 2579827.0733 | 1184504.4269 | 2579827.3253 | 1184502.2138
21 | 2579840.4558 | 1184521.057 | 2579834.0594 | 1184527.7154 | 2579827.4425 | 1184536.8537 | 2579827.0589 | 1184537.5114
22 | 2579820.1561 | 1184566.9162 | 2579822.4692 | 1184562.5616 | 2579822.1934 | 1184559.9946 | 2579819.5105 | 1184554.3118 | 2579819.7368 | 1184551.2761 | 2579822.2521 | 1184545.7536 | 2579827.0589 | 1184537.5114
23 | 2579791.755 | 1184525.6176 | 2579782.534 | 1184512.2595 | 2579778.3609 | 1184506.9631
24 | 2579807.8436 | 1184548.9264 | 2579807.6765 | 1184548.6822 | 2579791.755 | 1184525.6176
25 | 2579758.9474 | 1184482.3239 | 2579778.3609 | 1184506.9631
26 | 2579820.1561 | 1184566.9162 | 2579807.8436 | 1184548.9264
27 | 2579758.9474 | 1184482.3239 | 2579766.8678 | 1184479.4622 | 2579764.9048 | 1184474.5441
28 | 2579736.2581 | 1184539.0861 | 2579731.2724 | 1184529.5869 | 2579724.1087 | 1184519.3059 | 2579721.5868 | 1184516.1017 | 2579718.4492 | 1184511.4211 | 2579717.3215 | 1184509.7351 | 2579716.1803 | 1184506.3261 | 2579716.6333 | 1184502.6449 | 2579718.2016 | 1184499.2267 | 2579720.8493 | 1184496.7386 | 2579725.5055 | 1184494.6106 | 2579758.9474 | 1184482.3239
29 | 2579852.0043 | 1184593.5113 | 2579829.0976 | 1184577.1246 | 2579820.1561 | 1184566.9162
30 | 2579764.9048 | 1184474.5441 | 2579810.6266 | 1184454.9602
31 | 2579736.2581 | 1184539.0861 | 2579741.4696 | 1184556.5806
32 | 2579852.0043 | 1184593.5113 | 2579870.4195 | 1184608.8571 | 2579857.1961 | 1184628.7729
33 | 2579852.0043 | 1184593.5113 | 2579825.197 | 1184631.6094
34 | 2579746.7593 | 1184588.2204 | 2579746.5156 | 1184581.6401 | 2579744.1716 | 1184565.6508 | 2579741.4696 | 1184556.5806
35 | 2579758.8299 | 1184600.6193 | 2579757.198 | 1184598.7683 | 2579755.7145 | 1184586.7115 | 2579753.8914 | 1184587.0178 | 2579746.7593 | 1184588.2204
36 | 2579758.8299 | 1184600.6193 | 2579761.8984 | 1184593.961
37 | 2579761.1668 | 1184585.2923 | 2579761.8984 | 1184593.961
38 | 2579848.1658 | 1184668.1277 | 2579848.3371 | 1184642.1156 | 2579857.1961 | 1184628.7729
39 | 2579850.2578 | 1184718.1265 | 2579853.4611 | 1184712.9463 | 2579847.8983 | 1184708.7518 | 2579848.1658 | 1184668.1277
40 | 2579850.2578 | 1184718.1265 | 2579858.9427 | 1184722.4884
41 | 2579858.9427 | 1184722.4884 | 2579858.2852 | 1184726.6817 | 2579856.5109 | 1184754.9579
42 | 2579858.9427 | 1184722.4884 | 2579877.9033 | 1184732.2072 | 2579905.5327 | 1184745.8824
43 | 2579967.3203 | 1184619.1491 | 2579968.0681 | 1184615.9099 | 2579973.4387 | 1184603.7855 | 2579986.4555 | 1184582.1528 | 2579996.079 | 1184569.2752
44 | 2579965.3072 | 1184627.8698 | 2579967.3203 | 1184619.1491
45 | 2579965.3072 | 1184627.8698 | 2579959.7582 | 1184660.4361
46 | 2579950.1863 | 1184631.9894 | 2579955.8503 | 1184627.7237 | 2579960.4529 | 1184627.7972 | 2579965.3072 | 1184627.8698
47 | 2579955.642 | 1184688.3338 | 2579957.5232 | 1184673.5531 | 2579959.7582 | 1184660.4361
48 | 2579950.1863 | 1184631.9894 | 2579940.2846 | 1184626.6977 | 2579910.9573 | 1184625.4847 | 2579894.9461 | 1184616.8452 | 2579872.4601 | 1184645.9344
49 | 2579950.1863 | 1184631.9894 | 2579949.287 | 1184636.9395 | 2579948.0355 | 1184643.8028
50 | 2579948.0355 | 1184643.8028 | 2579931.3579 | 1184668.4273
51 | 2579968.2989 | 1184766.3763 | 2579976.6429 | 1184767.1689
52 | 2579927.4795 | 1184756.4751 | 2579936.4886 | 1184759.6798 | 2579945.4946 | 1184761.984 | 2579955.2019 | 1184764.0413 | 2579968.2989 | 1184766.3763
53 | 2579927.4795 | 1184756.4751 | 2579925.0452 | 1184761.1079 | 2579923.9349 | 1184764.569 | 2579923.2228 | 1184768.4178 | 2579922.3925 | 1184775.2836
54 | 2579927.4795 | 1184756.4751 | 2579920.6689 | 1184753.3741 | 2579905.5327 | 1184745.8824
55 | 2579973.1753 | 1184691.2431 | 2579955.642 | 1184688.3338
56 | 2579922.3925 | 1184775.2836 | 2579920.2564 | 1184792.9463
57 | 2579856.5109 | 1184754.9579 | 2579859.0953 | 1184758.64 | 2579861.1322 | 1184760.6342 | 2579863.1754 | 1184762.2392 | 2579866.0654 | 1184763.7191 | 2579869.3582 | 1184764.7197 | 2579886.141 | 1184766.9086 | 2579888.2652 | 1184767.6685 | 2579889.7884 | 1184768.9641 | 2579890.6263 | 1184770.7288 | 2579890.6628 | 1184772.4963

## bus_geodata
| x | y | coords
0 | 2579896.9024 | 1184429.9627
1 | 2579867.532 | 1184435.4381
2 | 2579960.6091 | 1184429.1457
3 | 2579850.2874 | 1184440.0594
4 | 2579837.2498 | 1184444.6029
5 | 2579822.7211 | 1184449.7798
6 | 2580022.0686 | 1184534.4975
7 | 2580012.6382 | 1184528.626
8 | 2580000.5296 | 1184493.426
9 | 2580019.3583 | 1184538.1243
10 | 2579985.5046 | 1184490.1121
11 | 2579872.1543 | 1184498.1961
12 | 2579898.247 | 1184490.2818
13 | 2579851.0606 | 1184511.1581
14 | 2579899.4621 | 1184490.0937
15 | 2579849.109 | 1184512.8246
16 | 2579924.8093 | 1184487.0773
17 | 2579840.4558 | 1184521.057
18 | 2579956.7829 | 1184485.8159
19 | 2579827.3253 | 1184502.2138
20 | 2579827.0589 | 1184537.5114
21 | 2579791.755 | 1184525.6176
22 | 2579778.3609 | 1184506.9631
23 | 2579807.8436 | 1184548.9264
24 | 2579758.9474 | 1184482.3239
25 | 2579820.1561 | 1184566.9162
26 | 2579764.9048 | 1184474.5441
27 | 2579736.2581 | 1184539.0861
28 | 2579852.0043 | 1184593.5113
29 | 2579810.6266 | 1184454.9602
30 | 2579741.4696 | 1184556.5806
31 | 2579746.7593 | 1184588.2204
32 | 2579758.8299 | 1184600.6193
33 | 2579761.8984 | 1184593.961
34 | 2579857.1961 | 1184628.7729
35 | 2579825.197 | 1184631.6094
36 | 2579761.1668 | 1184585.2923
37 | 2579850.2578 | 1184718.1265
38 | 2579848.1658 | 1184668.1277
39 | 2579858.9427 | 1184722.4884
40 | 2579996.079 | 1184569.2752
41 | 2579967.3203 | 1184619.1491
42 | 2579965.3072 | 1184627.8698
43 | 2579939.6874 | 1184526.3252
44 | 2579959.7582 | 1184660.4361
45 | 2579950.1863 | 1184631.9894
46 | 2579872.4601 | 1184645.9344
47 | 2579948.0355 | 1184643.8028
48 | 2579976.6429 | 1184767.1689
49 | 2579968.2989 | 1184766.3763
50 | 2579927.4795 | 1184756.4751
51 | 2579955.642 | 1184688.3338
52 | 2579973.1753 | 1184691.2431
53 | 2579922.3925 | 1184775.2836
54 | 2579905.5327 | 1184745.8824
55 | 2579920.2564 | 1184792.9463
56 | 2579856.5109 | 1184754.9579
57 | 2579890.6628 | 1184772.4963
58 | 2579931.3579 | 1184668.4273
59 | 2579955.8503 | 1184627.7237

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97259 | -0.52829 | 0.0016803 | 0.00042112
1 | 0.97266 | -0.52697 | 0.0022176 | 0.00055577
2 | 0.97255 | -0.52912 | 0.00070685 | 0.00017715
3 | 0.97274 | -0.52545 | 0 | 0
4 | 0.9728 | -0.52428 | 0.0017556 | 0.00044
5 | 0.97289 | -0.52247 | 0 | 0
6 | 0.99023 | -0.18542 | 0 | 0
7 | 0.98992 | -0.19143 | 0 | 0
8 | 0.98643 | -0.2583 | 0 | 0
9 | 0.99052 | -0.17995 | 0.027221 | 0.0068224
10 | 0.98557 | -0.27495 | 0.0011075 | 0.00027757
11 | 0.97941 | -0.39446 | 0.0026511 | 0.00066443
12 | 0.98068 | -0.36962 | 0.0016367 | 0.00041019
13 | 0.97826 | -0.4168 | 0.025064 | 0.0062818
14 | 0.98074 | -0.36849 | 0.036766 | 0.0092143
15 | 0.97816 | -0.41881 | 0.0083695 | 0.0020976
16 | 0.98216 | -0.34093 | 0.00083675 | 0.00020971
17 | 0.97771 | -0.42774 | 0 | 0
18 | 0.98394 | -0.30636 | 0.00096763 | 0.00024251
19 | 0.97767 | -0.42839 | 0.0014816 | 0.00037133
20 | 0.9769 | -0.44353 | 0.0059644 | 0.0014948
21 | 0.97452 | -0.49024 | 0.0027984 | 0.00070134
22 | 0.97405 | -0.49949 | 0.001918 | 0.00048068
23 | 0.97517 | -0.47739 | 0.0018966 | 0.00047532
24 | 0.97347 | -0.51103 | 0 | 0
25 | 0.97571 | -0.46676 | 0 | 0
26 | 0.97336 | -0.51317 | 0 | 0
27 | 0.97249 | -0.53022 | 0 | 0
28 | 0.97445 | -0.49159 | 0 | 0
29 | 0.97297 | -0.52093 | 0.0021175 | 0.0005307
30 | 0.9723 | -0.53409 | 0.0029976 | 0.00075128
31 | 0.97204 | -0.53916 | 0 | 0
32 | 0.97185 | -0.54288 | 0 | 0
33 | 0.9718 | -0.54403 | 0.0042067 | 0.0010543
34 | 0.97345 | -0.51133 | 0.019739 | 0.0049471
35 | 0.97271 | -0.52603 | 0.040211 | 0.010078
36 | 0.97176 | -0.54472 | 0.0043151 | 0.0010815
37 | 0.97217 | -0.53663 | 0 | 0
38 | 0.97276 | -0.52487 | 0.022504 | 0.0056402
39 | 0.97206 | -0.53875 | 0 | 0
40 | 0.99322 | -0.12841 | 0.027746 | 0.0069537
41 | 0.99761 | -0.045138 | 0.039963 | 0.010016
42 | 0.99837 | -0.03077 | 0 | 0
43 | 0.98788 | -0.23109 | 0.0305 | 0.0076439
44 | 0.9966 | -0.064953 | 0.043205 | 0.010828
45 | 1 | 0 | -0.56662 | -0.14436
46 | 0.9943 | -0.10963 | 0.065456 | 0.016405
47 | 0.99928 | -0.013907 | 0 | 0
48 | 0.97123 | -0.55515 | 0.0089866 | 0.0022523
49 | 0.9713 | -0.55375 | 0 | 0
50 | 0.97148 | -0.55026 | 0 | 0
51 | 0.99619 | -0.072808 | 0 | 0
52 | 0.99593 | -0.077747 | 0.015862 | 0.0039753
53 | 0.97138 | -0.55222 | 0.0080936 | 0.0020284
54 | 0.97162 | -0.54743 | 0.010883 | 0.0027275
55 | 0.97125 | -0.55488 | 0.0080886 | 0.0020272
56 | 0.97171 | -0.54564 | 0 | 0
57 | 0.97127 | -0.55442 | 0.011447 | 0.002869
58 | 0.99748 | -0.048434 | 0.066392 | 0.016639
59 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0023872 | -0.00059751 | 0.0023873 | 0.00059723 | 1.4949e-07 | -2.753e-07 | 0.003652 | 0.0036519 | 0.003652 | 0.97259 | -0.52829 | 0.97266 | -0.52697 | 1.0033
1 | 0.00070688 | 0.00017638 | -0.00070685 | -0.00017715 | 2.7969e-08 | -7.7363e-07 | 0.0010812 | 0.0010815 | 0.0010815 | 0.97259 | -0.52829 | 0.97255 | -0.52912 | 0.29711
2 | -0.0046049 | -0.001153 | 0.0046052 | 0.001153 | 3.3229e-07 | -8.987e-09 | 0.0070444 | 0.0070443 | 0.0070444 | 0.97266 | -0.52697 | 0.97274 | -0.52545 | 1.9353
3 | -0.0046052 | -0.001153 | 0.0046055 | 0.001153 | 2.5692e-07 | -6.9758e-09 | 0.0070443 | 0.0070442 | 0.0070443 | 0.97274 | -0.52545 | 0.9728 | -0.52428 | 1.9352
4 | -0.0063611 | -0.001593 | 0.0063617 | 0.0015932 | 5.4763e-07 | 1.5895e-07 | 0.0097297 | 0.0097296 | 0.0097297 | 0.9728 | -0.52428 | 0.97289 | -0.52247 | 2.673
5 | -0.0063617 | -0.0015932 | 0.0063621 | 0.0015933 | 4.6708e-07 | 1.3553e-07 | 0.0097296 | 0.0097296 | 0.0097296 | 0.97289 | -0.52247 | 0.97297 | -0.52093 | 2.673
6 | 0.030566 | 0.0076854 | -0.030557 | -0.0076799 | 8.7739e-06 | 5.4727e-06 | 0.04594 | 0.04594 | 0.04594 | 0.99023 | -0.18542 | 0.98992 | -0.19143 | 12.621
7 | 0.24489 | 0.062689 | -0.24402 | -0.062141 | 0.00086099 | 0.00054757 | 0.36846 | 0.36846 | 0.36846 | 0.99023 | -0.18542 | 0.98643 | -0.2583 | 25.3062
8 | -0.27545 | -0.070374 | 0.27552 | 0.070421 | 7.2892e-05 | 4.6418e-05 | 0.4144 | 0.4144 | 0.4144 | 0.99023 | -0.18542 | 0.99052 | -0.17995 | 28.4613
9 | 0.030557 | 0.0076799 | -0.0305 | -0.0076439 | 5.7738e-05 | 3.6017e-05 | 0.04594 | 0.045941 | 0.045941 | 0.98992 | -0.19143 | 0.98788 | -0.23109 | 12.621
10 | 0.24402 | 0.062141 | -0.24383 | -0.062017 | 0.00019583 | 0.00012455 | 0.36846 | 0.36846 | 0.36846 | 0.98643 | -0.2583 | 0.98557 | -0.27495 | 25.3062
11 | -0.30275 | -0.077243 | 0.3035 | 0.077725 | 0.00075573 | 0.00048166 | 0.45529 | 0.45529 | 0.45529 | 0.99052 | -0.17995 | 0.99322 | -0.12841 | 31.2699
12 | 0.24272 | 0.061739 | -0.24235 | -0.061506 | 0.00036673 | 0.00023322 | 0.36679 | 0.36679 | 0.36679 | 0.98557 | -0.27495 | 0.98394 | -0.30636 | 25.1914
13 | -0.20118 | -0.050813 | 0.20142 | 0.050966 | 0.00023983 | 0.00015211 | 0.30579 | 0.30579 | 0.30579 | 0.97941 | -0.39446 | 0.98068 | -0.36962 | 21.0022
14 | 0.19853 | 0.050149 | -0.19832 | -0.050014 | 0.0002123 | 0.00013462 | 0.30176 | 0.30176 | 0.30176 | 0.97941 | -0.39446 | 0.97826 | -0.4168 | 20.7256
15 | -0.20305 | -0.051376 | 0.20307 | 0.051383 | 1.0955e-05 | 6.9488e-06 | 0.30827 | 0.30827 | 0.30827 | 0.98068 | -0.36962 | 0.98074 | -0.36849 | 21.1727
16 | 0.17325 | 0.043733 | -0.17323 | -0.043722 | 1.6722e-05 | 1.0574e-05 | 0.26364 | 0.26364 | 0.26364 | 0.97826 | -0.4168 | 0.97816 | -0.41881 | 18.1071
17 | -0.23983 | -0.060597 | 0.24015 | 0.060799 | 0.0003173 | 0.00020178 | 0.36406 | 0.36406 | 0.36406 | 0.98074 | -0.36849 | 0.98216 | -0.34093 | 25.0039
18 | 0.16486 | 0.041625 | -0.16479 | -0.04158 | 7.0516e-05 | 4.4531e-05 | 0.25091 | 0.25091 | 0.25091 | 0.97816 | -0.41881 | 0.97771 | -0.42774 | 17.2327
19 | -0.24099 | -0.061009 | 0.24139 | 0.061263 | 0.00040076 | 0.00025486 | 0.36532 | 0.36532 | 0.36532 | 0.98216 | -0.34093 | 0.98394 | -0.30636 | 25.0909
20 | 0.0014817 | 0.00037106 | -0.0014816 | -0.00037133 | 4.5237e-08 | -2.6855e-07 | 0.0022549 | 0.002255 | 0.002255 | 0.97771 | -0.42774 | 0.97767 | -0.42839 | 0.61952
21 | 0.16331 | 0.041209 | -0.16319 | -0.041131 | 0.00012333 | 7.7864e-05 | 0.24865 | 0.24865 | 0.24865 | 0.97771 | -0.42774 | 0.9769 | -0.44353 | 17.0778
22 | 0.15722 | 0.039636 | -0.15705 | -0.039526 | 0.00017461 | 0.00011012 | 0.23957 | 0.23957 | 0.23957 | 0.9769 | -0.44353 | 0.97571 | -0.46676 | 16.4539
23 | 0.021959 | 0.0055146 | -0.021949 | -0.0055087 | 9.6878e-06 | 5.9141e-06 | 0.033533 | 0.033533 | 0.033533 | 0.97452 | -0.49024 | 0.97405 | -0.49949 | 9.2124
24 | -0.024757 | -0.0062159 | 0.024772 | 0.0062253 | 1.518e-05 | 9.3622e-06 | 0.037806 | 0.037806 | 0.037806 | 0.97452 | -0.49024 | 0.97517 | -0.47739 | 10.3862
25 | 0.020031 | 0.005028 | -0.02002 | -0.0050213 | 1.1017e-05 | 6.6606e-06 | 0.030603 | 0.030603 | 0.030603 | 0.97405 | -0.49949 | 0.97347 | -0.51103 | 8.4075
26 | -0.026669 | -0.0067006 | 0.026682 | 0.006709 | 1.3541e-05 | 8.3944e-06 | 0.0407 | 0.0407 | 0.0407 | 0.97517 | -0.47739 | 0.97571 | -0.46676 | 11.1813
27 | 0.0084837 | 0.0021258 | -0.0084828 | -0.0021254 | 8.6356e-07 | 3.8245e-07 | 0.012968 | 0.012968 | 0.012968 | 0.97347 | -0.51103 | 0.97336 | -0.51317 | 3.5626
28 | 0.011536 | 0.0028956 | -0.011526 | -0.00289 | 1.0549e-05 | 5.6279e-06 | 0.017636 | 0.017636 | 0.017636 | 0.97347 | -0.51103 | 0.97249 | -0.53022 | 4.845
29 | 0.13037 | 0.032817 | -0.13021 | -0.03272 | 0.0001545 | 9.6799e-05 | 0.19887 | 0.19887 | 0.19887 | 0.97571 | -0.46676 | 0.97445 | -0.49159 | 13.6587
30 | 0.0084828 | 0.0021254 | -0.0084797 | -0.002124 | 3.1367e-06 | 1.3895e-06 | 0.012968 | 0.012968 | 0.012968 | 0.97336 | -0.51317 | 0.97297 | -0.52093 | 3.5626
31 | 0.011526 | 0.00289 | -0.011524 | -0.0028888 | 2.1291e-06 | 1.1362e-06 | 0.017636 | 0.017636 | 0.017636 | 0.97249 | -0.53022 | 0.9723 | -0.53409 | 4.8451
32 | 0.089936 | 0.022601 | -0.089851 | -0.022549 | 8.4684e-05 | 5.1814e-05 | 0.13736 | 0.13736 | 0.13736 | 0.97445 | -0.49159 | 0.97345 | -0.51133 | 9.4339
33 | 0.040277 | 0.01012 | -0.040211 | -0.010078 | 6.6102e-05 | 4.1726e-05 | 0.061514 | 0.061514 | 0.061514 | 0.97445 | -0.49159 | 0.97271 | -0.52603 | 16.8994
34 | 0.0085259 | 0.0021375 | -0.0085239 | -0.0021366 | 2.0565e-06 | 9.1681e-07 | 0.013048 | 0.013049 | 0.013049 | 0.9723 | -0.53409 | 0.97204 | -0.53916 | 3.5848
35 | 0.0085239 | 0.0021366 | -0.0085224 | -0.0021359 | 1.5113e-06 | 6.739e-07 | 0.013049 | 0.013049 | 0.013049 | 0.97204 | -0.53916 | 0.97185 | -0.54288 | 3.5848
36 | 0.0085224 | 0.0021359 | -0.0085219 | -0.0021357 | 4.6811e-07 | 2.0875e-07 | 0.013049 | 0.013049 | 0.013049 | 0.97185 | -0.54288 | 0.9718 | -0.54403 | 3.5848
37 | 0.0043152 | 0.0010814 | -0.0043151 | -0.0010815 | 1.4243e-07 | -1.6625e-08 | 0.0066075 | 0.0066075 | 0.0066075 | 0.9718 | -0.54403 | 0.97176 | -0.54472 | 1.8153
38 | 0.070112 | 0.017602 | -0.070067 | -0.017575 | 4.5267e-05 | 2.6882e-05 | 0.10718 | 0.10718 | 0.10718 | 0.97345 | -0.51133 | 0.97276 | -0.52487 | 7.3616
39 | -0.047536 | -0.01192 | 0.047562 | 0.011935 | 2.6644e-05 | 1.4388e-05 | 0.072761 | 0.07276 | 0.072761 | 0.97217 | -0.53663 | 0.97276 | -0.52487 | 4.9973
40 | 0.047536 | 0.01192 | -0.047531 | -0.011918 | 4.8129e-06 | 2.5994e-06 | 0.072761 | 0.072761 | 0.072761 | 0.97217 | -0.53663 | 0.97206 | -0.53875 | 4.9973
41 | 0.011456 | 0.0028735 | -0.011452 | -0.0028715 | 3.758e-06 | 2.0014e-06 | 0.017537 | 0.017538 | 0.017538 | 0.97206 | -0.53875 | 0.97171 | -0.54564 | 4.818
42 | 0.036075 | 0.0090442 | -0.03606 | -0.0090373 | 1.4906e-05 | 6.9558e-06 | 0.055224 | 0.055225 | 0.055225 | 0.97206 | -0.53875 | 0.97162 | -0.54743 | 3.7929
43 | -0.33125 | -0.084678 | 0.33259 | 0.085533 | 0.0013402 | 0.00085472 | 0.49686 | 0.49686 | 0.49686 | 0.99322 | -0.12841 | 0.99761 | -0.045138 | 34.1248
44 | -0.37255 | -0.095549 | 0.37281 | 0.095715 | 0.00025982 | 0.00016581 | 0.55646 | 0.55646 | 0.55646 | 0.99761 | -0.045138 | 0.99837 | -0.03077 | 38.2185
45 | 0.059173 | 0.01487 | -0.059077 | -0.014809 | 9.639e-05 | 6.1259e-05 | 0.088208 | 0.088208 | 0.088208 | 0.99837 | -0.03077 | 0.9966 | -0.064953 | 24.2331
46 | -0.43198 | -0.11059 | 0.43263 | 0.111 | 0.00064478 | 0.00041179 | 0.64467 | 0.64467 | 0.64467 | 0.99837 | -0.03077 | 1 | 0 | 44.2767
47 | 0.015871 | 0.0039809 | -0.015865 | -0.0039775 | 5.9404e-06 | 3.4345e-06 | 0.023698 | 0.023699 | 0.023699 | 0.9966 | -0.064953 | 0.99619 | -0.072808 | 6.5106
48 | 0.0658 | 0.016624 | -0.065456 | -0.016405 | 0.00034379 | 0.00021878 | 0.097958 | 0.097958 | 0.097958 | 1 | 0 | 0.9943 | -0.10963 | 26.9116
49 | 0.066546 | 0.016737 | -0.066502 | -0.016709 | 4.4175e-05 | 2.8115e-05 | 0.099042 | 0.099042 | 0.099042 | 1 | 0 | 0.99928 | -0.013907 | 27.2094
50 | 0.066502 | 0.016709 | -0.066392 | -0.016639 | 0.0001094 | 6.9628e-05 | 0.099042 | 0.099042 | 0.099042 | 0.99928 | -0.013907 | 0.99748 | -0.048434 | 27.2095
51 | -0.0089866 | -0.0022523 | 0.0089872 | 0.0022525 | 5.9582e-07 | 2.7759e-07 | 0.013768 | 0.013768 | 0.013768 | 0.97123 | -0.55515 | 0.9713 | -0.55375 | 3.7825
52 | -0.0089872 | -0.0022525 | 0.0089887 | 0.0022525 | 1.4958e-06 | -8.4653e-08 | 0.013768 | 0.013768 | 0.013768 | 0.9713 | -0.55375 | 0.97148 | -0.55026 | 1.8912
53 | 0.016185 | 0.0040563 | -0.016183 | -0.0040561 | 1.5132e-06 | 2.3684e-07 | 0.02479 | 0.02479 | 0.02479 | 0.97148 | -0.55026 | 0.97138 | -0.55222 | 2.2702
54 | -0.025173 | -0.0063088 | 0.025177 | 0.0063097 | 3.397e-06 | 9.6681e-07 | 0.038558 | 0.038558 | 0.038558 | 0.97148 | -0.55026 | 0.97162 | -0.54743 | 2.6482
55 | 0.015865 | 0.0039775 | -0.015862 | -0.0039753 | 3.7326e-06 | 2.1582e-06 | 0.023699 | 0.023699 | 0.023699 | 0.99619 | -0.072808 | 0.99593 | -0.077747 | 6.5106
56 | 0.0080896 | 0.0020276 | -0.0080886 | -0.0020272 | 1.0246e-06 | 4.3551e-07 | 0.012392 | 0.012392 | 0.012392 | 0.97138 | -0.55222 | 0.97125 | -0.55488 | 3.4045
57 | 0.011452 | 0.0028715 | -0.011447 | -0.002869 | 4.7909e-06 | 2.5519e-06 | 0.017538 | 0.017538 | 0.017538 | 0.97171 | -0.54564 | 0.97127 | -0.55442 | 4.8181

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56662 | 0.14436

## res_load
| p_mw | q_mvar
0 | 0.0016803 | 0.00042112
1 | 0.0022176 | 0.00055577
2 | 0.00070685 | 0.00017715
3 | 0.0017556 | 0.00044
4 | 0.027221 | 0.0068224
5 | 0.0011075 | 0.00027757
6 | 0.0026511 | 0.00066443
7 | 0.0016367 | 0.00041019
8 | 0.025064 | 0.0062818
9 | 0.036766 | 0.0092143
10 | 0.0083695 | 0.0020976
11 | 0.00083675 | 0.00020971
12 | 0.00096763 | 0.00024251
13 | 0.0014816 | 0.00037133
14 | 0.0059644 | 0.0014948
15 | 0.0027984 | 0.00070134
16 | 0.001918 | 0.00048068
17 | 0.0018966 | 0.00047532
18 | 0.0021175 | 0.0005307
19 | 0.0029976 | 0.00075128
20 | 0.0042067 | 0.0010543
21 | 0.019739 | 0.0049471
22 | 0.040211 | 0.010078
23 | 0.0043151 | 0.0010815
24 | 0.022504 | 0.0056402
25 | 0.027746 | 0.0069537
26 | 0.039963 | 0.010016
27 | 0.0305 | 0.0076439
28 | 0.043205 | 0.010828
29 | 0.065456 | 0.016405
30 | 0.0089866 | 0.0022523
31 | 0.015862 | 0.0039753
32 | 0.0080936 | 0.0020284
33 | 0.010883 | 0.0027275
34 | 0.0080886 | 0.0020272
35 | 0.011447 | 0.002869
36 | 0.066392 | 0.016639

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1