## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-58_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-58_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-58_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-58_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-58_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2196-58_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2196-58_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2196-58_0_4_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_2196-58_0_4_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_2196-58_0_4_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_2196-58_0_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_2196-58_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_2196-58_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_2196-58_0_4_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_2196-58_0_4_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_2196-58_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2196-58_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2196-58_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2196-58_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2196-58_0_4_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2196-58_0_4_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_2196-58_0_4_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_2196-58_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2196-58_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2196-58_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2196-58_0_4_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_2196-58_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2196-58_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2196-58_0_4_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_2196-58_0_4_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_2196-58_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2196-58_0_4_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_2196-58_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2196-58_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2196-58_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_2196-58_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_2196-58_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_2196-58_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_MV_507_0_node_64 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-58_0_4_load_0 | 0 | 0.038364 | 0.0096148 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-58_0_4_load_3 | 3 | 0.022719 | 0.0056939 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-58_0_4_load_4 | 4 | 0.060672 | 0.015206 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-58_0_4_load_5 | 5 | 0.017174 | 0.0043042 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-58_0_4_load_6 | 6 | 0.0079446 | 0.0019911 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-58_0_4_load_30 | 9 | 0.02381 | 0.0059673 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-58_0_4_load_35 | 10 | 0.014219 | 0.0035637 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-58_0_4_load_29 | 13 | 0.0079714 | 0.0019978 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-58_0_4_load_36 | 14 | 0.021244 | 0.0053244 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-58_0_4_load_7 | 15 | 0.0033703 | 0.00084468 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-58_0_4_load_18 | 19 | 0.004371 | 0.0010955 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-58_0_4_load_38 | 20 | 0.077572 | 0.019441 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-58_0_4_load_33 | 21 | 0.030143 | 0.0075547 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-58_0_4_load_19 | 23 | 0.0031561 | 0.000791 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-58_0_4_load_27 | 25 | 0.032449 | 0.0081325 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-58_0_4_load_34 | 28 | 0.0089248 | 0.0022368 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-58_0_4_load_20 | 30 | 0.0081185 | 0.0020347 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-58_0_4_load_32 | 31 | 0.014754 | 0.0036977 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-58_0_4_load_22 | 32 | 0.00082978 | 0.00020796 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-58_0_4_load_23 | 33 | 0.009644 | 0.002417 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-58_0_4_load_24 | 34 | 0.010501 | 0.0026317 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-58_0_4_load_25 | 35 | 0.024275 | 0.006084 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-58_0_4_load_26 | 36 | 0.01936 | 0.004852 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-58_0_4_load_31 | 37 | 0.0058278 | 0.0014606 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-58_0_4_line_0 |  | 0 | 1 | 0.032962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2196-58_0_4_line_1 |  | 0 | 2 | 0.013089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2196-58_0_4_line_2 |  | 1 | 3 | 0.0086862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-58_0_4_line_3 |  | 1 | 4 | 0.023814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2196-58_0_4_line_4 |  | 2 | 5 | 0.00178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2196-58_0_4_line_5 |  | 2 | 6 | 0.008415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-58_0_4_line_6 |  | 3 | 7 | 0.058879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-58_0_4_line_7 |  | 4 | 8 | 0.054922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-58_0_4_line_8 |  | 5 | 9 | 0.015331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-58_0_4_line_9 |  | 6 | 10 | 0.0081874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-58_0_4_line_10 |  | 7 | 11 | 0.017662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-58_0_4_line_11 |  | 8 | 12 | 0.049919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-58_0_4_line_12 |  | 9 | 13 | 0.010605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-58_0_4_line_13 |  | 10 | 14 | 0.012667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-58_0_4_line_14 |  | 11 | 21 | 0.042488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-58_0_4_line_15 |  | 12 | 29 | 0.005537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-58_0_4_line_16 |  | 13 | 36 | 0.00041019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-58_0_4_line_17 |  | 15 | 16 | 0.077776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-58_0_4_line_18 |  | 16 | 17 | 0.09938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2196-58_0_4_line_19 |  | 17 | 18 | 0.029108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-58_0_4_line_20 |  | 17 | 19 | 0.010449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-58_0_4_line_21 |  | 18 | 20 | 0.014568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-58_0_4_line_22 |  | 19 | 22 | 0.063924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-58_0_4_line_23 |  | 20 | 29 | 0.06525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-58_0_4_line_24 |  | 22 | 23 | 0.014657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-58_0_4_line_25 |  | 22 | 24 | 0.1044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-58_0_4_line_26 |  | 24 | 25 | 0.007423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-58_0_4_line_27 |  | 26 | 27 | 0.060557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-58_0_4_line_28 |  | 26 | 28 | 0.016621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-58_0_4_line_29 |  | 27 | 30 | 0.036818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-58_0_4_line_30 |  | 28 | 31 | 0.010686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-58_0_4_line_31 |  | 31 | 37 | 0.0074579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2196-58_0_4_line_32 |  | 32 | 33 | 0.006526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2196-58_0_4_line_33 |  | 32 | 34 | 0.00038282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2196-58_0_4_line_34 |  | 33 | 35 | 0.0013777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2196-58_0_4_line_35 |  | 34 | 36 | 0.0057689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2196-58_0_4_line_36 |  | 35 | 37 | 0.0059815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-58_0_4_trafo_4 | 0.63 MVA 20/0.4 kV | 38 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2578648.0052 | 1183820.3291 | 2578647.8247 | 1183823.2201 | 2578647.5053 | 1183840.6081 | 2578646.8558 | 1183853.2659
1 | 2578646.1852 | 1183866.3374 | 2578646.8558 | 1183853.2659
2 | 2578648.0052 | 1183820.3291 | 2578655.908 | 1183823.9339
3 | 2578648.0052 | 1183820.3291 | 2578625.1278 | 1183813.8521 | 2578625.0911 | 1183813.844
4 | 2578646.1852 | 1183866.3374 | 2578647.9427 | 1183866.6195
5 | 2578646.1852 | 1183866.3374 | 2578637.8651 | 1183865.0772
6 | 2578709.4772 | 1183848.3685 | 2578655.908 | 1183823.9339
7 | 2578572.4184 | 1183798.6665 | 2578598.7184 | 1183808.0215 | 2578625.0911 | 1183813.844
8 | 2578647.9427 | 1183866.6195 | 2578663.08 | 1183869.05
9 | 2578637.8651 | 1183865.0772 | 2578629.7701 | 1183863.8511
10 | 2578709.4772 | 1183848.3685 | 2578718.6524 | 1183837.6413 | 2578720.9708 | 1183834.9316
11 | 2578552.3162 | 1183844.3737 | 2578572.4184 | 1183798.6665
12 | 2578663.08 | 1183869.05 | 2578667.1811 | 1183869.7085 | 2578673.4957 | 1183871.0301
13 | 2578629.7701 | 1183863.8511 | 2578617.246 | 1183861.9542
14 | 2578720.9708 | 1183834.9316 | 2578714.3326 | 1183829.2746 | 2578688.9742 | 1183807.7872 | 2578688.5434 | 1183807.4811
15 | 2578546.9449 | 1183842.97 | 2578552.3162 | 1183844.3737
16 | 2578673.4957 | 1183871.0301 | 2578673.8972 | 1183871.1141
17 | 2578409.4909 | 1183827.9023 | 2578436.5869 | 1183754.9991
18 | 2578409.4909 | 1183827.9023 | 2578406.588 | 1183829.4025 | 2578402.5884 | 1183829.4726 | 2578396.3177 | 1183828.428 | 2578388.6872 | 1183827.1105 | 2578390.5188 | 1183814.3417 | 2578393.0417 | 1183800.6699 | 2578404.2781 | 1183802.8081 | 2578443.3496 | 1183810.2374
19 | 2578443.3496 | 1183810.2374 | 2578458.7337 | 1183813.1611 | 2578472.0248 | 1183815.6923
20 | 2578443.3496 | 1183810.2374 | 2578446.1409 | 1183805.3359 | 2578448.1443 | 1183800.9649
21 | 2578472.0248 | 1183815.6923 | 2578485.9541 | 1183819.9579
22 | 2578477.449 | 1183745.0026 | 2578471.8688 | 1183749.2027 | 2578448.1443 | 1183800.9649
23 | 2578546.9449 | 1183842.97 | 2578506.0384 | 1183826.1084 | 2578485.9541 | 1183819.9579
24 | 2578477.449 | 1183745.0026 | 2578484.7962 | 1183748.1888 | 2578486.8069 | 1183749.0598 | 2578490.955 | 1183750.6909
25 | 2578477.449 | 1183745.0026 | 2578470.3898 | 1183741.2594 | 2578455.7973 | 1183733.5414 | 2578443.0594 | 1183725.7278 | 2578451.3392 | 1183722.9297 | 2578449.9423 | 1183712.3626 | 2578448.9474 | 1183705.3292 | 2578448.6497 | 1183703.2181 | 2578451.8427 | 1183701.7169 | 2578474.2991 | 1183701.3356 | 2578484.5924 | 1183702.2768
26 | 2578484.5924 | 1183702.2768 | 2578486.9478 | 1183701.3456 | 2578491.2579 | 1183699.0354
27 | 2578723.3992 | 1183892.9865 | 2578696.9187 | 1183926.9431 | 2578682.5587 | 1183937.0664
28 | 2578723.3992 | 1183892.9865 | 2578716.1984 | 1183887.954 | 2578709.5076 | 1183883.8756
29 | 2578682.5587 | 1183937.0664 | 2578659.9353 | 1183943.8508 | 2578646.7795 | 1183942.775
30 | 2578700.241 | 1183878.5953 | 2578702.092 | 1183879.3554 | 2578709.5076 | 1183883.8756
31 | 2578700.241 | 1183878.5953 | 2578693.3423 | 1183875.762
32 | 2578686.306 | 1183873.7113 | 2578679.9185 | 1183872.3744
33 | 2578679.5438 | 1183872.296 | 2578679.9185 | 1183872.3744
34 | 2578686.306 | 1183873.7113 | 2578687.6545 | 1183873.9935
35 | 2578679.5438 | 1183872.296 | 2578673.8972 | 1183871.1141
36 | 2578693.3423 | 1183875.762 | 2578690.4724 | 1183874.5833 | 2578687.6545 | 1183873.9935

## bus_geodata
| x | y | coords
0 | 2578646.8558 | 1183853.2659
1 | 2578648.0052 | 1183820.3291
2 | 2578646.1852 | 1183866.3374
3 | 2578655.908 | 1183823.9339
4 | 2578625.0911 | 1183813.844
5 | 2578647.9427 | 1183866.6195
6 | 2578637.8651 | 1183865.0772
7 | 2578709.4772 | 1183848.3685
8 | 2578572.4184 | 1183798.6665
9 | 2578663.08 | 1183869.05
10 | 2578629.7701 | 1183863.8511
11 | 2578720.9708 | 1183834.9316
12 | 2578552.3162 | 1183844.3737
13 | 2578673.4957 | 1183871.0301
14 | 2578617.246 | 1183861.9542
15 | 2578436.5869 | 1183754.9991
16 | 2578409.4909 | 1183827.9023
17 | 2578443.3496 | 1183810.2374
18 | 2578472.0248 | 1183815.6923
19 | 2578448.1443 | 1183800.9649
20 | 2578485.9541 | 1183819.9579
21 | 2578688.5434 | 1183807.4811
22 | 2578477.449 | 1183745.0026
23 | 2578490.955 | 1183750.6909
24 | 2578484.5924 | 1183702.2768
25 | 2578491.2579 | 1183699.0354
26 | 2578723.3992 | 1183892.9865
27 | 2578682.5587 | 1183937.0664
28 | 2578709.5076 | 1183883.8756
29 | 2578546.9449 | 1183842.97
30 | 2578646.7795 | 1183942.775
31 | 2578700.241 | 1183878.5953
32 | 2578679.9185 | 1183872.3744
33 | 2578686.306 | 1183873.7113
34 | 2578679.5438 | 1183872.296
35 | 2578687.6545 | 1183873.9935
36 | 2578673.8972 | 1183871.1141
37 | 2578693.3423 | 1183875.762
38 | 2578648.0052 | 1183820.3291

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99559 | -0.084535 | 0.038364 | 0.0096148
1 | 0.99793 | -0.03963 | 0 | 0
2 | 0.99481 | -0.099477 | 0 | 0
3 | 0.99751 | -0.04767 | 0.022719 | 0.0056939
4 | 1 | 0 | -0.41266 | -0.10466
5 | 0.99469 | -0.10185 | 0.017174 | 0.0043042
6 | 0.99448 | -0.10591 | 0.0079446 | 0.0019911
7 | 0.99589 | -0.078812 | 0 | 0
8 | 0.99383 | -0.11649 | 0 | 0
9 | 0.99281 | -0.13811 | 0.02381 | 0.0059673
10 | 0.99422 | -0.11103 | 0.014219 | 0.0035637
11 | 0.99541 | -0.088173 | 0 | 0
12 | 0.98823 | -0.22362 | 0 | 0
13 | 0.99174 | -0.1588 | 0.0079714 | 0.0019978
14 | 0.99397 | -0.11578 | 0.021244 | 0.0053244
15 | 0.97797 | -0.42293 | 0.0033703 | 0.00084468
16 | 0.97821 | -0.41816 | 0 | 0
17 | 0.97852 | -0.41205 | 0 | 0
18 | 0.9797 | -0.3891 | 0 | 0
19 | 0.97813 | -0.41966 | 0.004371 | 0.0010955
20 | 0.98029 | -0.37764 | 0.077572 | 0.019441
21 | 0.99424 | -0.11073 | 0.030143 | 0.0075547
22 | 0.97601 | -0.46122 | 0 | 0
23 | 0.97597 | -0.46206 | 0.0031561 | 0.000791
24 | 0.97285 | -0.52341 | 0 | 0
25 | 0.97263 | -0.52784 | 0.032449 | 0.0081325
26 | 0.99002 | -0.19216 | 0 | 0
27 | 0.98957 | -0.20091 | 0 | 0
28 | 0.99014 | -0.18976 | 0.0089248 | 0.0022368
29 | 0.98761 | -0.23558 | 0 | 0
30 | 0.9893 | -0.20623 | 0.0081185 | 0.0020347
31 | 0.99031 | -0.18652 | 0.014754 | 0.0036977
32 | 0.99124 | -0.16851 | 0.00082978 | 0.00020796
33 | 0.99081 | -0.1768 | 0.009644 | 0.002417
34 | 0.99126 | -0.16802 | 0.010501 | 0.0026317
35 | 0.99073 | -0.17831 | 0.024275 | 0.006084
36 | 0.9917 | -0.15954 | 0.01936 | 0.004852
37 | 0.99053 | -0.18231 | 0.0058278 | 0.0014606
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.23358 | -0.058779 | 0.23408 | 0.059099 | 0.00050241 | 0.00032026 | 0.3492 | 0.3492 | 0.3492 | 0.99559 | -0.084535 | 0.99793 | -0.03963 | 31.9776
1 | 0.19522 | 0.049164 | -0.19508 | -0.049075 | 0.00013936 | 8.8681e-05 | 0.29186 | 0.29186 | 0.29186 | 0.99559 | -0.084535 | 0.99481 | -0.099477 | 26.7269
2 | 0.052974 | 0.013318 | -0.052953 | -0.013305 | 2.0331e-05 | 1.2898e-05 | 0.079004 | 0.079004 | 0.079004 | 0.99793 | -0.03963 | 0.99751 | -0.04767 | 21.7044
3 | -0.28706 | -0.072417 | 0.2876 | 0.072765 | 0.0005458 | 0.00034838 | 0.4282 | 0.4282 | 0.4282 | 0.99793 | -0.03963 | 1 | 0 | 39.2124
4 | 0.15164 | 0.038179 | -0.15163 | -0.038168 | 1.718e-05 | 1.0949e-05 | 0.22688 | 0.22688 | 0.22688 | 0.99481 | -0.099477 | 0.99469 | -0.10185 | 31.1655
5 | 0.043435 | 0.010896 | -0.043422 | -0.010888 | 1.3321e-05 | 8.4164e-06 | 0.064973 | 0.064973 | 0.064973 | 0.99481 | -0.099477 | 0.99448 | -0.10591 | 17.8497
6 | 0.030234 | 0.0076113 | -0.030189 | -0.0075833 | 4.4937e-05 | 2.7992e-05 | 0.045113 | 0.045114 | 0.045114 | 0.99751 | -0.04767 | 0.99589 | -0.078812 | 12.3939
7 | 0.12341 | 0.031893 | -0.12271 | -0.031447 | 0.00069714 | 0.00044545 | 0.18398 | 0.18398 | 0.18398 | 1 | 0 | 0.99383 | -0.11649 | 50.5441
8 | 0.13445 | 0.033864 | -0.13422 | -0.033715 | 0.00023272 | 0.00014874 | 0.20119 | 0.20119 | 0.20119 | 0.99469 | -0.10185 | 0.99281 | -0.13811 | 55.2728
9 | 0.035477 | 0.0088964 | -0.035469 | -0.008891 | 8.6523e-06 | 5.4312e-06 | 0.053086 | 0.053086 | 0.053086 | 0.99448 | -0.10591 | 0.99422 | -0.11103 | 14.584
10 | 0.030189 | 0.0075833 | -0.030176 | -0.0075749 | 1.348e-05 | 8.3975e-06 | 0.045114 | 0.045114 | 0.045114 | 0.99589 | -0.078812 | 0.99541 | -0.088173 | 12.3939
11 | 0.12271 | 0.031447 | -0.12208 | -0.031042 | 0.00063364 | 0.00040489 | 0.18398 | 0.18398 | 0.18398 | 0.99383 | -0.11649 | 0.98823 | -0.22362 | 50.5441
12 | 0.11041 | 0.027748 | -0.1103 | -0.027678 | 0.00010894 | 6.9583e-05 | 0.16551 | 0.16551 | 0.16551 | 0.99281 | -0.13811 | 0.99174 | -0.1588 | 45.469
13 | 0.021249 | 0.0053273 | -0.021244 | -0.0053244 | 4.8047e-06 | 2.9108e-06 | 0.031804 | 0.031804 | 0.031804 | 0.99422 | -0.11103 | 0.99397 | -0.11578 | 8.7373
14 | 0.030176 | 0.0075749 | -0.030143 | -0.0075547 | 3.2428e-05 | 2.0202e-05 | 0.045114 | 0.045114 | 0.045114 | 0.99541 | -0.088173 | 0.99424 | -0.11073 | 12.3939
15 | 0.12208 | 0.031042 | -0.12201 | -0.030997 | 7.0283e-05 | 4.491e-05 | 0.18398 | 0.18398 | 0.18398 | 0.98823 | -0.22362 | 0.98761 | -0.23558 | 50.5442
16 | 0.10233 | 0.025681 | -0.10232 | -0.025678 | 3.6266e-06 | 2.3157e-06 | 0.15355 | 0.15355 | 0.15355 | 0.99174 | -0.1588 | 0.9917 | -0.15954 | 42.1832
17 | -0.0033703 | -0.00084468 | 0.0033711 | 0.00084419 | 7.6692e-07 | -4.8532e-07 | 0.005128 | 0.0051277 | 0.005128 | 0.97797 | -0.42293 | 0.97821 | -0.41816 | 1.4088
18 | -0.0033711 | -0.00084419 | 0.0033721 | 0.00084357 | 9.798e-07 | -6.2093e-07 | 0.0051277 | 0.0051272 | 0.0051277 | 0.97821 | -0.41816 | 0.97852 | -0.41205 | 1.4087
19 | -0.043538 | -0.010981 | 0.043585 | 0.011011 | 4.7882e-05 | 3.0278e-05 | 0.066231 | 0.066231 | 0.066231 | 0.97852 | -0.41205 | 0.9797 | -0.3891 | 18.1954
20 | 0.040165 | 0.010138 | -0.040151 | -0.010128 | 1.463e-05 | 9.2319e-06 | 0.061104 | 0.061104 | 0.061104 | 0.97852 | -0.41205 | 0.97813 | -0.41966 | 16.7869
21 | -0.043585 | -0.011011 | 0.043609 | 0.011027 | 2.3964e-05 | 1.5153e-05 | 0.066231 | 0.066231 | 0.066231 | 0.9797 | -0.3891 | 0.98029 | -0.37764 | 18.1954
22 | 0.03578 | 0.0090329 | -0.035709 | -0.0089882 | 7.1084e-05 | 4.4693e-05 | 0.054455 | 0.054455 | 0.054455 | 0.97813 | -0.41966 | 0.97601 | -0.46122 | 14.9602
23 | -0.12118 | -0.030468 | 0.12201 | 0.030997 | 0.00082825 | 0.00052925 | 0.18398 | 0.18398 | 0.18398 | 0.98029 | -0.37764 | 0.98761 | -0.23558 | 50.5442
24 | 0.0031562 | 0.00079089 | -0.0031561 | -0.000791 | 1.2727e-07 | -1.0172e-07 | 0.0048119 | 0.004812 | 0.004812 | 0.97601 | -0.46122 | 0.97597 | -0.46206 | 1.322
25 | 0.032553 | 0.0081973 | -0.032456 | -0.0081368 | 9.6484e-05 | 6.0449e-05 | 0.049643 | 0.049644 | 0.049644 | 0.97601 | -0.46122 | 0.97285 | -0.52341 | 13.6383
26 | 0.032456 | 0.0081368 | -0.032449 | -0.0081325 | 6.8602e-06 | 4.2984e-06 | 0.049644 | 0.049644 | 0.049644 | 0.97285 | -0.52341 | 0.97263 | -0.52784 | 13.6384
27 | 0.0081239 | 0.0020369 | -0.0081205 | -0.0020355 | 3.386e-06 | 1.3887e-06 | 0.012211 | 0.012211 | 0.012211 | 0.99002 | -0.19216 | 0.98957 | -0.20091 | 3.3547
28 | -0.0081239 | -0.0020369 | 0.0081249 | 0.0020373 | 9.2932e-07 | 3.8101e-07 | 0.012211 | 0.012211 | 0.012211 | 0.99002 | -0.19216 | 0.99014 | -0.18976 | 3.3546
29 | 0.0081205 | 0.0020355 | -0.0081185 | -0.0020347 | 2.0588e-06 | 8.4472e-07 | 0.012211 | 0.012211 | 0.012211 | 0.98957 | -0.20091 | 0.9893 | -0.20623 | 3.3547
30 | -0.01705 | -0.0042741 | 0.017052 | 0.0042756 | 2.6308e-06 | 1.5463e-06 | 0.025623 | 0.025623 | 0.025623 | 0.99014 | -0.18976 | 0.99031 | -0.18652 | 7.0393
31 | -0.031806 | -0.0079733 | 0.031813 | 0.0079773 | 6.3879e-06 | 3.9923e-06 | 0.047792 | 0.047792 | 0.047792 | 0.99031 | -0.18652 | 0.99053 | -0.18231 | 13.1297
32 | 0.0716 | 0.017964 | -0.071571 | -0.017946 | 2.8276e-05 | 1.8012e-05 | 0.10749 | 0.10749 | 0.10749 | 0.99124 | -0.16851 | 0.99081 | -0.1768 | 29.5302
33 | -0.072429 | -0.018172 | 0.072431 | 0.018173 | 1.6973e-06 | 1.0814e-06 | 0.10874 | 0.10874 | 0.10874 | 0.99124 | -0.16851 | 0.99126 | -0.16802 | 29.8724
34 | 0.061927 | 0.015529 | -0.061923 | -0.015526 | 4.4689e-06 | 2.8423e-06 | 0.093007 | 0.093007 | 0.093007 | 0.99081 | -0.1768 | 0.99073 | -0.17831 | 25.5512
35 | -0.082932 | -0.020805 | 0.082965 | 0.020826 | 3.3532e-05 | 2.1386e-05 | 0.1245 | 0.1245 | 0.1245 | 0.99126 | -0.16802 | 0.9917 | -0.15954 | 34.2028
36 | 0.037648 | 0.0094424 | -0.03764 | -0.0094379 | 7.1722e-06 | 4.5132e-06 | 0.056547 | 0.056547 | 0.056547 | 0.99073 | -0.17831 | 0.99053 | -0.18231 | 15.5348

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47334 | 0.11986

## res_load
| p_mw | q_mvar
0 | 0.038364 | 0.0096148
1 | 0.022719 | 0.0056939
2 | 0.060672 | 0.015206
3 | 0.017174 | 0.0043042
4 | 0.0079446 | 0.0019911
5 | 0.02381 | 0.0059673
6 | 0.014219 | 0.0035637
7 | 0.0079714 | 0.0019978
8 | 0.021244 | 0.0053244
9 | 0.0033703 | 0.00084468
10 | 0.004371 | 0.0010955
11 | 0.077572 | 0.019441
12 | 0.030143 | 0.0075547
13 | 0.0031561 | 0.000791
14 | 0.032449 | 0.0081325
15 | 0.0089248 | 0.0022368
16 | 0.0081185 | 0.0020347
17 | 0.014754 | 0.0036977
18 | 0.00082978 | 0.00020796
19 | 0.009644 | 0.002417
20 | 0.010501 | 0.0026317
21 | 0.024275 | 0.006084
22 | 0.01936 | 0.004852
23 | 0.0058278 | 0.0014606

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1