## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-71_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-71_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2196-71_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2196-71_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2196-71_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2196-71_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2196-71_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2196-71_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2196-71_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2196-71_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2196-71_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2196-71_0_4_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_2196-71_0_4_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_2196-71_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_2196-71_0_4_node_62 | 0.4 | n |  | TRUE
15 | bus_LV_2196-71_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_2196-71_0_4_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_2196-71_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2196-71_0_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2196-71_0_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_2196-71_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2196-71_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2196-71_0_4_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_2196-71_0_4_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2196-71_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_2196-71_0_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_2196-71_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_2196-71_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2196-71_0_4_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_2196-71_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_2196-71_0_4_node_61 | 0.4 | n |  | TRUE
31 | bus_LV_2196-71_0_4_node_50 | 0.4 | n |  | TRUE
32 | bus_LV_2196-71_0_4_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_2196-71_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_2196-71_0_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_2196-71_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_2196-71_0_4_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_2196-71_0_4_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_2196-71_0_4_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_2196-71_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_2196-71_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_2196-71_0_4_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_2196-71_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_2196-71_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_2196-71_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_2196-71_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_2196-71_0_4_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_2196-71_0_4_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_2196-71_0_4_node_59 | 0.4 | n |  | TRUE
49 | bus_LV_2196-71_0_4_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_2196-71_0_4_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_2196-71_0_4_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_2196-71_0_4_node_52 | 0.4 | n |  | TRUE
53 | bus_LV_2196-71_0_4_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_2196-71_0_4_node_53 | 0.4 | n |  | TRUE
55 | bus_LV_2196-71_0_4_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_2196-71_0_4_node_60 | 0.4 | n |  | TRUE
57 | bus_MV_508_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-71_0_4_load_0 | 0 | 0.0091764 | 0.0022998 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-71_0_4_load_4 | 3 | 0.0094999 | 0.0023809 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-71_0_4_load_5 | 4 | 0.0099901 | 0.0025038 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-71_0_4_load_6 | 5 | 0.014964 | 0.0037502 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-71_0_4_load_7 | 6 | 0.014964 | 0.0037502 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-71_0_4_load_9 | 8 | 0.013503 | 0.0033841 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-71_0_4_load_10 | 9 | 0.01705 | 0.0042731 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-71_0_4_load_27 | 11 | 0.019403 | 0.0048628 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-71_0_4_load_12 | 12 | 0.01428 | 0.0035788 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-71_0_4_load_13 | 13 | 0.015341 | 0.0038448 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-71_0_4_load_62 | 14 | 0.018392 | 0.0046095 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-71_0_4_load_19 | 15 | 0.014322 | 0.0035893 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-71_0_4_load_17 | 17 | 0.01418 | 0.0035538 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-71_0_4_load_21 | 18 | 0.016409 | 0.0041124 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-71_0_4_load_22 | 19 | 0.0066623 | 0.0016697 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-71_0_4_load_14 | 20 | 0.0065618 | 0.0016445 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-71_0_4_load_15 | 21 | 0.0065729 | 0.0016473 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-71_0_4_load_30 | 22 | 0.0039934 | 0.0010008 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-71_0_4_load_28 | 23 | 0.0053611 | 0.0013436 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-71_0_4_load_29 | 24 | 0.0054081 | 0.0013554 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-71_0_4_load_23 | 27 | 0.018881 | 0.0047319 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-71_0_4_load_35 | 29 | 0.0032987 | 0.00082673 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-71_0_4_load_61 | 30 | 0.0022373 | 0.00056071 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-71_0_4_load_56 | 32 | 0.0027475 | 0.0006886 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2196-71_0_4_load_33 | 33 | 0.0083477 | 0.0020921 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2196-71_0_4_load_31 | 34 | 0.0094711 | 0.0023737 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2196-71_0_4_load_32 | 35 | 0.011118 | 0.0027864 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2196-71_0_4_load_34 | 36 | 0.0092852 | 0.0023271 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2196-71_0_4_load_41 | 37 | 0.012142 | 0.003043 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2196-71_0_4_load_40 | 38 | 0.0066413 | 0.0016645 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2196-71_0_4_load_36 | 39 | 0.003564 | 0.00089323 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2196-71_0_4_load_37 | 40 | 0.0082154 | 0.002059 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2196-71_0_4_load_38 | 41 | 0.0061491 | 0.0015411 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2196-71_0_4_load_42 | 42 | 0.0061119 | 0.0015318 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2196-71_0_4_load_43 | 43 | 0.0052338 | 0.0013117 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2196-71_0_4_load_45 | 45 | 0.0052565 | 0.0013174 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2196-71_0_4_load_46 | 46 | 0.0061487 | 0.001541 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2196-71_0_4_load_47 | 47 | 0.0044981 | 0.0011273 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2196-71_0_4_load_59 | 48 | 0.0071675 | 0.0017963 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2196-71_0_4_load_48 | 49 | 0.0047126 | 0.0011811 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2196-71_0_4_load_51 | 51 | 0.0050317 | 0.0012611 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2196-71_0_4_load_52 | 52 | 0.0033739 | 0.00084558 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2196-71_0_4_load_53 | 54 | 0.0043091 | 0.00108 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2196-71_0_4_load_54 | 55 | 0.003969 | 0.00099472 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2196-71_0_4_load_60 | 56 | 0.012597 | 0.0031572 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-71_0_4_line_0 |  | 0 | 1 | 0.0045007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-71_0_4_line_1 |  | 1 | 2 | 0.024201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-71_0_4_line_2 |  | 2 | 3 | 0.014441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-71_0_4_line_3 |  | 3 | 4 | 0.016002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-71_0_4_line_4 |  | 4 | 5 | 0.015519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-71_0_4_line_5 |  | 5 | 6 | 0.015475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-71_0_4_line_6 |  | 6 | 7 | 0.015673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-71_0_4_line_7 |  | 7 | 8 | 0.014261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-71_0_4_line_8 |  | 7 | 9 | 0.045836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-71_0_4_line_9 |  | 8 | 10 | 0.011965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-71_0_4_line_10 |  | 9 | 11 | 0.035064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-71_0_4_line_11 |  | 10 | 12 | 0.015028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-71_0_4_line_12 |  | 10 | 13 | 0.006552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2196-71_0_4_line_13 |  | 11 | 14 | 0.058275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-71_0_4_line_14 |  | 12 | 15 | 0.014946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-71_0_4_line_15 |  | 13 | 16 | 0.025141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_2196-71_0_4_line_16 |  | 15 | 17 | 0.014893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-71_0_4_line_17 |  | 16 | 18 | 0.0066551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-71_0_4_line_18 |  | 16 | 19 | 0.015286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2196-71_0_4_line_19 |  | 17 | 21 | 0.014968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-71_0_4_line_20 |  | 18 | 24 | 0.022998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-71_0_4_line_21 |  | 19 | 25 | 0.048493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2196-71_0_4_line_22 |  | 20 | 21 | 0.015102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-71_0_4_line_23 |  | 22 | 23 | 0.018425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-71_0_4_line_24 |  | 23 | 24 | 0.017764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-71_0_4_line_25 |  | 25 | 26 | 0.009304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2196-71_0_4_line_26 |  | 25 | 27 | 0.016121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-71_0_4_line_27 |  | 26 | 28 | 0.036394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-71_0_4_line_28 |  | 26 | 29 | 0.0075517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-71_0_4_line_29 |  | 28 | 30 | 0.002998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-71_0_4_line_30 |  | 28 | 31 | 0.015078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-71_0_4_line_31 |  | 29 | 33 | 0.016808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2196-71_0_4_line_32 |  | 31 | 32 | 0.043165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2196-71_0_4_line_33 |  | 32 | 53 | 0.015063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2196-71_0_4_line_34 |  | 33 | 34 | 0.01981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2196-71_0_4_line_35 |  | 34 | 35 | 0.00011957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2196-71_0_4_line_36 |  | 35 | 36 | 0.02074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2196-71_0_4_line_37 |  | 36 | 37 | 0.019213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2196-71_0_4_line_38 |  | 37 | 38 | 0.023714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2196-71_0_4_line_39 |  | 38 | 41 | 0.021462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2196-71_0_4_line_40 |  | 39 | 40 | 0.003068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2196-71_0_4_line_41 |  | 39 | 41 | 0.01933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2196-71_0_4_line_42 |  | 42 | 43 | 0.028572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2196-71_0_4_line_43 |  | 42 | 44 | 0.015597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2196-71_0_4_line_44 |  | 43 | 45 | 0.02254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2196-71_0_4_line_45 |  | 44 | 46 | 0.0021409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2196-71_0_4_line_46 |  | 45 | 47 | 0.019947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2196-71_0_4_line_47 |  | 46 | 48 | 0.022447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2196-71_0_4_line_48 |  | 47 | 49 | 8.5261e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2196-71_0_4_line_49 |  | 48 | 50 | 0.0072932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2196-71_0_4_line_50 |  | 49 | 51 | 0.018749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2196-71_0_4_line_51 |  | 50 | 56 | 0.017269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2196-71_0_4_line_52 |  | 50 | 53 | 0.039008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2196-71_0_4_line_53 |  | 51 | 52 | 0.0015149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2196-71_0_4_line_54 |  | 52 | 54 | 0.017126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2196-71_0_4_line_55 |  | 54 | 55 | 0.003119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-71_0_4_trafo_13 | 0.63 MVA 20/0.4 kV | 57 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2577298.601 | 1183439.7332 | 2577301.4313 | 1183443.2325
1 | 2577298.601 | 1183439.7332 | 2577289.4431 | 1183428.4177 | 2577283.3608 | 1183420.9035
2 | 2577283.3608 | 1183420.9035 | 2577293.4508 | 1183410.5719
3 | 2577293.4508 | 1183410.5719 | 2577304.6316 | 1183399.1233
4 | 2577304.6316 | 1183399.1233 | 2577315.4745 | 1183388.0206
5 | 2577315.4745 | 1183388.0206 | 2577326.2866 | 1183376.9495
6 | 2577337.2371 | 1183365.7367 | 2577326.2866 | 1183376.9495
7 | 2577337.2371 | 1183365.7367 | 2577346.7068 | 1183355.0736
8 | 2577337.2371 | 1183365.7367 | 2577362.0034 | 1183386.3312 | 2577364.4902 | 1183389.857 | 2577364.3351 | 1183395.2604 | 2577363.5411 | 1183399.084
9 | 2577354.652 | 1183346.127 | 2577346.7068 | 1183355.0736
10 | 2577366.2286 | 1183433.5843 | 2577361.7636 | 1183407.6432 | 2577363.5411 | 1183399.084
11 | 2577354.652 | 1183346.127 | 2577368.4009 | 1183352.1936
12 | 2577354.652 | 1183346.127 | 2577358.2311 | 1183340.639
13 | 2577366.2286 | 1183433.5843 | 2577417.306 | 1183461.6387
14 | 2577382.075 | 1183358.2272 | 2577368.4009 | 1183352.1936
15 | 2577371.9644 | 1183319.5809 | 2577358.2311 | 1183340.639
16 | 2577382.075 | 1183358.2272 | 2577395.7003 | 1183364.2393
17 | 2577371.9644 | 1183319.5809 | 2577378.0273 | 1183322.3251
18 | 2577371.9644 | 1183319.5809 | 2577357.7376 | 1183313.9906
19 | 2577409.3945 | 1183370.2817 | 2577395.7003 | 1183364.2393
20 | 2577398.9795 | 1183331.8084 | 2577378.0273 | 1183322.3251
21 | 2577311.8956 | 1183298.2978 | 2577337.4148 | 1183306.0049 | 2577357.7376 | 1183313.9906
22 | 2577423.2115 | 1183376.3783 | 2577409.3945 | 1183370.2817
23 | 2577415.1627 | 1183339.1332 | 2577422.9934 | 1183342.6775 | 2577431.931 | 1183346.7697
24 | 2577415.1627 | 1183339.1332 | 2577398.9795 | 1183331.8084
25 | 2577311.8956 | 1183298.2978 | 2577302.7432 | 1183296.4872
26 | 2577311.8956 | 1183298.2978 | 2577309.5295 | 1183310.4576 | 2577307.4366 | 1183313.5487
27 | 2577267.6299 | 1183287.305 | 2577282.2376 | 1183290.3065 | 2577294.6298 | 1183294.8839 | 2577302.7432 | 1183296.4872
28 | 2577302.7432 | 1183296.4872 | 2577306.1299 | 1183289.7375
29 | 2577267.6299 | 1183287.305 | 2577268.3288 | 1183284.3897
30 | 2577252.6105 | 1183286.4506 | 2577260.7931 | 1183286.1526 | 2577267.6299 | 1183287.305
31 | 2577321.9551 | 1183284.0735 | 2577306.1299 | 1183289.7375
32 | 2577252.6105 | 1183286.4506 | 2577255.1846 | 1183276.8136 | 2577265.2037 | 1183245.1719
33 | 2577269.7507 | 1183230.8119 | 2577265.2037 | 1183245.1719
34 | 2577341.3577 | 1183280.1286 | 2577322.8943 | 1183283.7373 | 2577321.9551 | 1183284.0735
35 | 2577341.3577 | 1183280.1286 | 2577341.4751 | 1183280.1057
36 | 2577362.0483 | 1183278.8006 | 2577349.9827 | 1183278.4428 | 2577341.4751 | 1183280.1057
37 | 2577362.0483 | 1183278.8006 | 2577380.5604 | 1183279.3496 | 2577381.2353 | 1183279.5052
38 | 2577404.343 | 1183284.8319 | 2577381.2353 | 1183279.5052
39 | 2577425.2562 | 1183289.6528 | 2577404.343 | 1183284.8319
40 | 2577444.0569 | 1183294.1357 | 2577447.0188 | 1183294.9358
41 | 2577444.0569 | 1183294.1357 | 2577440.2954 | 1183293.1196 | 2577425.2562 | 1183289.6528
42 | 2577353.7806 | 1183210.072 | 2577371.368 | 1183204.6122 | 2577381.2221 | 1183207.0706
43 | 2577338.8849 | 1183214.6962 | 2577353.7806 | 1183210.072
44 | 2577381.2221 | 1183207.0706 | 2577403.0922 | 1183212.5267
45 | 2577338.8849 | 1183214.6962 | 2577336.8397 | 1183215.329
46 | 2577403.0922 | 1183212.5267 | 2577422.4459 | 1183217.3551
47 | 2577336.8397 | 1183215.329 | 2577336.666 | 1183215.3828 | 2577314.9947 | 1183220.4895
48 | 2577422.4459 | 1183217.3551 | 2577422.5286 | 1183217.3757
49 | 2577307.8959 | 1183222.1623 | 2577314.9947 | 1183220.4895
50 | 2577440.7294 | 1183221.8746 | 2577438.6576 | 1183221.3996 | 2577422.5286 | 1183217.3757
51 | 2577307.8959 | 1183222.1623 | 2577313.0277 | 1183238.6513
52 | 2577307.8959 | 1183222.1623 | 2577286.2116 | 1183227.2807 | 2577269.7507 | 1183230.8119
53 | 2577440.7294 | 1183221.8746 | 2577442.206 | 1183222.2133
54 | 2577458.8983 | 1183226.0412 | 2577442.206 | 1183222.2133
55 | 2577458.8983 | 1183226.0412 | 2577461.9383 | 1183226.7383

## bus_geodata
| x | y | coords
0 | 2577301.4313 | 1183443.2325
1 | 2577298.601 | 1183439.7332
2 | 2577283.3608 | 1183420.9035
3 | 2577293.4508 | 1183410.5719
4 | 2577304.6316 | 1183399.1233
5 | 2577315.4745 | 1183388.0206
6 | 2577326.2866 | 1183376.9495
7 | 2577337.2371 | 1183365.7367
8 | 2577346.7068 | 1183355.0736
9 | 2577363.5411 | 1183399.084
10 | 2577354.652 | 1183346.127
11 | 2577366.2286 | 1183433.5843
12 | 2577368.4009 | 1183352.1936
13 | 2577358.2311 | 1183340.639
14 | 2577417.306 | 1183461.6387
15 | 2577382.075 | 1183358.2272
16 | 2577371.9644 | 1183319.5809
17 | 2577395.7003 | 1183364.2393
18 | 2577378.0273 | 1183322.3251
19 | 2577357.7376 | 1183313.9906
20 | 2577423.2115 | 1183376.3783
21 | 2577409.3945 | 1183370.2817
22 | 2577431.931 | 1183346.7697
23 | 2577415.1627 | 1183339.1332
24 | 2577398.9795 | 1183331.8084
25 | 2577311.8956 | 1183298.2978
26 | 2577302.7432 | 1183296.4872
27 | 2577307.4366 | 1183313.5487
28 | 2577267.6299 | 1183287.305
29 | 2577306.1299 | 1183289.7375
30 | 2577268.3288 | 1183284.3897
31 | 2577252.6105 | 1183286.4506
32 | 2577265.2037 | 1183245.1719
33 | 2577321.9551 | 1183284.0735
34 | 2577341.3577 | 1183280.1286
35 | 2577341.4751 | 1183280.1057
36 | 2577362.0483 | 1183278.8006
37 | 2577381.2353 | 1183279.5052
38 | 2577404.343 | 1183284.8319
39 | 2577444.0569 | 1183294.1357
40 | 2577447.0188 | 1183294.9358
41 | 2577425.2562 | 1183289.6528
42 | 2577353.7806 | 1183210.072
43 | 2577381.2221 | 1183207.0706
44 | 2577338.8849 | 1183214.6962
45 | 2577403.0922 | 1183212.5267
46 | 2577336.8397 | 1183215.329
47 | 2577422.4459 | 1183217.3551
48 | 2577314.9947 | 1183220.4895
49 | 2577422.5286 | 1183217.3757
50 | 2577307.8959 | 1183222.1623
51 | 2577440.7294 | 1183221.8746
52 | 2577442.206 | 1183222.2133
53 | 2577269.7507 | 1183230.8119
54 | 2577458.8983 | 1183226.0412
55 | 2577461.9383 | 1183226.7383
56 | 2577313.0277 | 1183238.6513
57 | 2577358.2311 | 1183340.639

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9941 | -0.11342 | 0.0091764 | 0.0022998
1 | 0.99414 | -0.1127 | 0 | 0
2 | 0.99434 | -0.10878 | 0 | 0
3 | 0.99446 | -0.10644 | 0.0094999 | 0.0023809
4 | 0.99474 | -0.10118 | 0.0099901 | 0.0025038
5 | 0.99514 | -0.093344 | 0.014964 | 0.0037502
6 | 0.99576 | -0.081468 | 0.014964 | 0.0037502
7 | 0.99659 | -0.065338 | 0 | 0
8 | 0.99807 | -0.036988 | 0.013503 | 0.0033841
9 | 0.9943 | -0.10956 | 0.01705 | 0.0042731
10 | 0.99945 | -0.010447 | 0 | 0
11 | 0.99309 | -0.13295 | 0.019403 | 0.0048628
12 | 0.99869 | -0.025121 | 0.01428 | 0.0035788
13 | 1 | 0 | -0.39606 | -0.10008
14 | 0.99211 | -0.15191 | 0.018392 | 0.0046095
15 | 0.99813 | -0.036002 | 0.014322 | 0.0035893
16 | 0.99759 | -0.045761 | 0 | 0
17 | 0.99776 | -0.043122 | 0.01418 | 0.0035538
18 | 0.9974 | -0.049395 | 0.016409 | 0.0041124
19 | 0.99634 | -0.069509 | 0.0066623 | 0.0016697
20 | 0.99749 | -0.048301 | 0.0065618 | 0.0016445
21 | 0.99758 | -0.046565 | 0.0065729 | 0.0016473
22 | 0.99688 | -0.059551 | 0.0039934 | 0.0010008
23 | 0.99694 | -0.05826 | 0.0053611 | 0.0013436
24 | 0.99709 | -0.055346 | 0.0054081 | 0.0013554
25 | 0.99254 | -0.14238 | 0 | 0
26 | 0.99189 | -0.15487 | 0 | 0
27 | 0.99226 | -0.14777 | 0.018881 | 0.0047319
28 | 0.98941 | -0.20232 | 0 | 0
29 | 0.99134 | -0.16534 | 0.0032987 | 0.00082673
30 | 0.98941 | -0.20244 | 0.0022373 | 0.00056071
31 | 0.98842 | -0.22144 | 0 | 0
32 | 0.98557 | -0.2764 | 0.0027475 | 0.0006886
33 | 0.99019 | -0.18771 | 0.0083477 | 0.0020921
34 | 0.98898 | -0.21119 | 0.0094711 | 0.0023737
35 | 0.98897 | -0.21131 | 0.011118 | 0.0027864
36 | 0.98809 | -0.22832 | 0.0092852 | 0.0023271
37 | 0.98745 | -0.24093 | 0.012142 | 0.003043
38 | 0.98691 | -0.25135 | 0.0066413 | 0.0016645
39 | 0.98635 | -0.26231 | 0.003564 | 0.00089323
40 | 0.98632 | -0.26277 | 0.0082154 | 0.002059
41 | 0.98656 | -0.25824 | 0.0061491 | 0.0015411
42 | 0.98006 | -0.38381 | 0.0061119 | 0.0015318
43 | 0.9791 | -0.40269 | 0.0052338 | 0.0013117
44 | 0.98068 | -0.37179 | 0 | 0
45 | 0.97845 | -0.41547 | 0.0052565 | 0.0013174
46 | 0.98076 | -0.37014 | 0.0061487 | 0.001541
47 | 0.97797 | -0.42487 | 0.0044981 | 0.0011273
48 | 0.98177 | -0.35037 | 0.0071675 | 0.0017963
49 | 0.97797 | -0.42491 | 0.0047126 | 0.0011811
50 | 0.98215 | -0.34301 | 0 | 0
51 | 0.97768 | -0.43061 | 0.0050317 | 0.0012611
52 | 0.97766 | -0.43093 | 0.0033739 | 0.00084558
53 | 0.98462 | -0.29491 | 0 | 0
54 | 0.97753 | -0.43352 | 0.0043091 | 0.00108
55 | 0.97752 | -0.43374 | 0.003969 | 0.00099472
56 | 0.98195 | -0.34694 | 0.012597 | 0.0031572
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0091764 | -0.0022998 | 0.0091767 | 0.0023 | 3.1843e-07 | 1.4544e-07 | 0.013736 | 0.013736 | 0.013736 | 0.9941 | -0.11342 | 0.99414 | -0.1127 | 3.7735
1 | -0.0091767 | -0.0023 | 0.0091784 | 0.0023007 | 1.7122e-06 | 7.8195e-07 | 0.013736 | 0.013735 | 0.013736 | 0.99414 | -0.1127 | 0.99434 | -0.10878 | 3.7735
2 | -0.0091784 | -0.0023007 | 0.0091794 | 0.0023012 | 1.0217e-06 | 4.6654e-07 | 0.013735 | 0.013735 | 0.013735 | 0.99434 | -0.10878 | 0.99446 | -0.10644 | 3.7735
3 | -0.018679 | -0.0046821 | 0.018684 | 0.0046849 | 4.688e-06 | 2.7926e-06 | 0.02795 | 0.02795 | 0.02795 | 0.99446 | -0.10644 | 0.99474 | -0.10118 | 7.6786
4 | -0.028674 | -0.0071887 | 0.028685 | 0.0071953 | 1.0708e-05 | 6.6513e-06 | 0.042894 | 0.042894 | 0.042894 | 0.99474 | -0.10118 | 0.99514 | -0.093344 | 11.7841
5 | -0.043648 | -0.010946 | 0.043673 | 0.010961 | 2.4721e-05 | 1.562e-05 | 0.065269 | 0.065269 | 0.065269 | 0.99514 | -0.093344 | 0.99576 | -0.081468 | 17.931
6 | -0.058637 | -0.014711 | 0.058682 | 0.01474 | 4.5132e-05 | 2.8681e-05 | 0.08763 | 0.08763 | 0.08763 | 0.99576 | -0.081468 | 0.99659 | -0.065338 | 24.0741
7 | -0.1137 | -0.028596 | 0.11386 | 0.028694 | 0.0001542 | 9.8499e-05 | 0.1698 | 0.1698 | 0.1698 | 0.99659 | -0.065338 | 0.99807 | -0.036988 | 46.6492
8 | 0.05502 | 0.013856 | -0.054904 | -0.013782 | 0.00011606 | 7.3685e-05 | 0.082173 | 0.082174 | 0.082174 | 0.99659 | -0.065338 | 0.9943 | -0.10956 | 22.5752
9 | -0.12736 | -0.032078 | 0.12752 | 0.032182 | 0.00016187 | 0.00010344 | 0.18993 | 0.18993 | 0.18993 | 0.99807 | -0.036988 | 0.99945 | -0.010447 | 52.1798
10 | 0.037854 | 0.0095087 | -0.037811 | -0.0094822 | 4.221e-05 | 2.656e-05 | 0.056658 | 0.056658 | 0.056658 | 0.9943 | -0.10956 | 0.99309 | -0.13295 | 15.5653
11 | 0.055988 | 0.014059 | -0.055949 | -0.014035 | 3.9166e-05 | 2.487e-05 | 0.083367 | 0.083367 | 0.083367 | 0.99945 | -0.010447 | 0.99869 | -0.025121 | 22.903
12 | -0.18351 | -0.046241 | 0.1836 | 0.0463 | 9.1761e-05 | 5.8555e-05 | 0.2733 | 0.2733 | 0.2733 | 0.99945 | -0.010447 | 1 | 0 | 37.5414
13 | 0.018409 | 0.0046194 | -0.018392 | -0.0046095 | 1.6629e-05 | 9.8893e-06 | 0.027585 | 0.027585 | 0.027585 | 0.99309 | -0.13295 | 0.99211 | -0.15191 | 7.5784
14 | 0.04167 | 0.010456 | -0.041648 | -0.010442 | 2.1608e-05 | 1.3634e-05 | 0.062091 | 0.062091 | 0.062091 | 0.99869 | -0.025121 | 0.99813 | -0.036002 | 17.0579
15 | 0.21081 | 0.053782 | -0.21034 | -0.053486 | 0.00046482 | 0.00029683 | 0.31402 | 0.31402 | 0.31402 | 1 | 0 | 0.99759 | -0.045761 | 43.1343
16 | 0.027327 | 0.0068527 | -0.027317 | -0.006847 | 9.2694e-06 | 5.7378e-06 | 0.04074 | 0.04074 | 0.04074 | 0.99813 | -0.036002 | 0.99776 | -0.043122 | 11.1924
17 | 0.031182 | 0.0078185 | -0.031177 | -0.0078151 | 5.3992e-06 | 3.3686e-06 | 0.046513 | 0.046513 | 0.046513 | 0.99759 | -0.045761 | 0.9974 | -0.049395 | 12.7783
18 | 0.17916 | 0.045667 | -0.17895 | -0.045536 | 0.00020509 | 0.00013086 | 0.2675 | 0.26751 | 0.26751 | 0.99759 | -0.045761 | 0.99634 | -0.069509 | 36.7452
19 | 0.013137 | 0.0032932 | -0.013135 | -0.003292 | 2.1547e-06 | 1.1836e-06 | 0.019593 | 0.019593 | 0.019593 | 0.99776 | -0.043122 | 0.99758 | -0.046565 | 5.3827
20 | 0.014768 | 0.0037027 | -0.014764 | -0.0037004 | 4.1868e-06 | 2.3795e-06 | 0.022033 | 0.022033 | 0.022033 | 0.9974 | -0.049395 | 0.99709 | -0.055346 | 6.0531
21 | 0.17229 | 0.043867 | -0.17169 | -0.043482 | 0.00060315 | 0.00038476 | 0.25756 | 0.25756 | 0.25756 | 0.99634 | -0.069509 | 0.99254 | -0.14238 | 35.3785
22 | -0.0065618 | -0.0016445 | 0.0065624 | 0.0016447 | 5.4265e-07 | 1.5014e-07 | 0.0097887 | 0.0097886 | 0.0097887 | 0.99749 | -0.048301 | 0.99758 | -0.046565 | 2.6892
23 | -0.0039934 | -0.0010008 | 0.0039936 | 0.0010008 | 2.455e-07 | -8.3113e-08 | 0.0059609 | 0.0059608 | 0.0059609 | 0.99688 | -0.059551 | 0.99694 | -0.05826 | 1.6376
24 | -0.0093547 | -0.0023444 | 0.009356 | 0.002345 | 1.2987e-06 | 5.9948e-07 | 0.013963 | 0.013962 | 0.013963 | 0.99694 | -0.05826 | 0.99709 | -0.055346 | 3.8359
25 | 0.1528 | 0.038747 | -0.15271 | -0.038689 | 9.1677e-05 | 5.8433e-05 | 0.22924 | 0.22924 | 0.22924 | 0.99254 | -0.14238 | 0.99189 | -0.15487 | 31.4893
26 | 0.018885 | 0.0047348 | -0.018881 | -0.0047319 | 4.8464e-06 | 2.8934e-06 | 0.028314 | 0.028314 | 0.028314 | 0.99254 | -0.14238 | 0.99226 | -0.14777 | 7.7785
27 | 0.074203 | 0.018908 | -0.074034 | -0.0188 | 0.00016946 | 0.00010798 | 0.11143 | 0.11143 | 0.11143 | 0.99189 | -0.15487 | 0.98941 | -0.20232 | 30.6127
28 | 0.078507 | 0.019781 | -0.078467 | -0.019756 | 3.9306e-05 | 2.5058e-05 | 0.11781 | 0.11781 | 0.11781 | 0.99189 | -0.15487 | 0.99134 | -0.16534 | 32.366
29 | 0.0022373 | 0.00056068 | -0.0022373 | -0.00056071 | 1.2728e-08 | -3.0357e-08 | 0.0033647 | 0.0033647 | 0.0033647 | 0.98941 | -0.20232 | 0.98941 | -0.20244 | 0.92438
30 | 0.071797 | 0.018239 | -0.071731 | -0.018197 | 6.6031e-05 | 4.2067e-05 | 0.10807 | 0.10807 | 0.10807 | 0.98941 | -0.20232 | 0.98842 | -0.22144 | 29.6883
31 | 0.075169 | 0.018929 | -0.075089 | -0.018878 | 8.0286e-05 | 5.1167e-05 | 0.11286 | 0.11286 | 0.11286 | 0.99134 | -0.16534 | 0.99019 | -0.18771 | 31.0058
32 | 0.071731 | 0.018197 | -0.071542 | -0.018077 | 0.00018903 | 0.00012043 | 0.10807 | 0.10807 | 0.10807 | 0.98842 | -0.22144 | 0.98557 | -0.2764 | 29.6884
33 | 0.068794 | 0.017388 | -0.068733 | -0.017349 | 6.0998e-05 | 3.8847e-05 | 0.10392 | 0.10392 | 0.10392 | 0.98557 | -0.2764 | 0.98462 | -0.29491 | 28.5488
34 | 0.066741 | 0.016786 | -0.066666 | -0.016738 | 7.476e-05 | 4.7592e-05 | 0.10032 | 0.10032 | 0.10032 | 0.99019 | -0.18771 | 0.98898 | -0.21119 | 27.5595
35 | 0.057195 | 0.014364 | -0.057195 | -0.014364 | 3.3214e-07 | 2.1104e-07 | 0.086066 | 0.086066 | 0.086066 | 0.98898 | -0.21119 | 0.98897 | -0.21131 | 23.6446
36 | 0.046077 | 0.011578 | -0.046039 | -0.011554 | 3.7392e-05 | 2.3665e-05 | 0.069338 | 0.069338 | 0.069338 | 0.98897 | -0.21131 | 0.98809 | -0.22832 | 19.049
37 | 0.036754 | 0.0092269 | -0.036732 | -0.0092131 | 2.2077e-05 | 1.3883e-05 | 0.055355 | 0.055355 | 0.055355 | 0.98809 | -0.22832 | 0.98745 | -0.24093 | 15.2075
38 | 0.02459 | 0.0061701 | -0.024578 | -0.0061626 | 1.2213e-05 | 7.5129e-06 | 0.037059 | 0.037059 | 0.037059 | 0.98745 | -0.24093 | 0.98691 | -0.25135 | 10.181
39 | 0.017937 | 0.0044981 | -0.017931 | -0.0044946 | 5.8868e-06 | 3.4934e-06 | 0.027045 | 0.027045 | 0.027045 | 0.98691 | -0.25135 | 0.98656 | -0.25824 | 7.4301
40 | 0.0082156 | 0.0020591 | -0.0082154 | -0.002059 | 1.7674e-07 | 7.3954e-08 | 0.012394 | 0.012394 | 0.012394 | 0.98635 | -0.26231 | 0.98632 | -0.26277 | 3.405
41 | -0.01178 | -0.0029523 | 0.011782 | 0.0029535 | 2.2892e-06 | 1.2183e-06 | 0.017771 | 0.017771 | 0.017771 | 0.98635 | -0.26231 | 0.98656 | -0.25824 | 4.8821
42 | 0.036454 | 0.0091618 | -0.036421 | -0.0091411 | 3.2833e-05 | 2.0653e-05 | 0.055357 | 0.055357 | 0.055357 | 0.98006 | -0.38381 | 0.9791 | -0.40269 | 15.2079
43 | -0.042566 | -0.010694 | 0.04259 | 0.010709 | 2.4436e-05 | 1.5442e-05 | 0.064636 | 0.064636 | 0.064636 | 0.98006 | -0.38381 | 0.98068 | -0.37179 | 17.7572
44 | 0.031187 | 0.0078294 | -0.031168 | -0.0078175 | 1.8993e-05 | 1.1872e-05 | 0.047403 | 0.047403 | 0.047403 | 0.9791 | -0.40269 | 0.97845 | -0.41547 | 13.0227
45 | -0.04259 | -0.010709 | 0.042594 | 0.010711 | 3.3541e-06 | 2.1196e-06 | 0.064636 | 0.064636 | 0.064636 | 0.98068 | -0.37179 | 0.98076 | -0.37014 | 17.7572
46 | 0.025912 | 0.0065001 | -0.0259 | -0.0064929 | 1.1617e-05 | 7.1844e-06 | 0.039409 | 0.039409 | 0.039409 | 0.97845 | -0.41547 | 0.97797 | -0.42487 | 10.8266
47 | -0.048742 | -0.012252 | 0.048788 | 0.012281 | 4.6051e-05 | 2.9189e-05 | 0.073965 | 0.073965 | 0.073965 | 0.98076 | -0.37014 | 0.98177 | -0.35037 | 20.3201
48 | 0.021402 | 0.0053656 | -0.021402 | -0.0053656 | 3.3905e-08 | 2.0631e-08 | 0.032565 | 0.032565 | 0.032565 | 0.97797 | -0.42487 | 0.97797 | -0.42491 | 8.9463
49 | -0.055956 | -0.014078 | 0.055976 | 0.01409 | 1.968e-05 | 1.2503e-05 | 0.084828 | 0.084828 | 0.084828 | 0.98177 | -0.35037 | 0.98215 | -0.34301 | 23.3045
50 | 0.016689 | 0.0041845 | -0.016685 | -0.0041818 | 4.534e-06 | 2.6666e-06 | 0.025394 | 0.025394 | 0.025394 | 0.97797 | -0.42491 | 0.97768 | -0.43061 | 6.9765
51 | 0.0126 | 0.0031585 | -0.012597 | -0.0031572 | 2.3598e-06 | 1.2918e-06 | 0.019089 | 0.019089 | 0.019089 | 0.98215 | -0.34301 | 0.98195 | -0.34694 | 5.2444
52 | -0.068575 | -0.017249 | 0.068733 | 0.017349 | 0.00015797 | 0.0001006 | 0.10392 | 0.10392 | 0.10392 | 0.98215 | -0.34301 | 0.98462 | -0.29491 | 28.5488
53 | 0.011653 | 0.0029208 | -0.011653 | -0.0029207 | 1.7871e-07 | 9.5375e-08 | 0.017736 | 0.017736 | 0.017736 | 0.97768 | -0.43061 | 0.97766 | -0.43093 | 4.8726
54 | 0.0082791 | 0.0020751 | -0.0082781 | -0.0020747 | 1.0197e-06 | 4.3792e-07 | 0.012601 | 0.012601 | 0.012601 | 0.97766 | -0.43093 | 0.97753 | -0.43352 | 3.4618
55 | 0.003969 | 0.00099471 | -0.003969 | -0.00099472 | 4.2694e-08 | -1.1776e-08 | 0.0060417 | 0.0060418 | 0.0060418 | 0.97753 | -0.43352 | 0.97752 | -0.43374 | 1.6598

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4114 | 0.10393

## res_load
| p_mw | q_mvar
0 | 0.0091764 | 0.0022998
1 | 0.0094999 | 0.0023809
2 | 0.0099901 | 0.0025038
3 | 0.014964 | 0.0037502
4 | 0.014964 | 0.0037502
5 | 0.013503 | 0.0033841
6 | 0.01705 | 0.0042731
7 | 0.019403 | 0.0048628
8 | 0.01428 | 0.0035788
9 | 0.015341 | 0.0038448
10 | 0.018392 | 0.0046095
11 | 0.014322 | 0.0035893
12 | 0.01418 | 0.0035538
13 | 0.016409 | 0.0041124
14 | 0.0066623 | 0.0016697
15 | 0.0065618 | 0.0016445
16 | 0.0065729 | 0.0016473
17 | 0.0039934 | 0.0010008
18 | 0.0053611 | 0.0013436
19 | 0.0054081 | 0.0013554
20 | 0.018881 | 0.0047319
21 | 0.0032987 | 0.00082673
22 | 0.0022373 | 0.00056071
23 | 0.0027475 | 0.0006886
24 | 0.0083477 | 0.0020921
25 | 0.0094711 | 0.0023737
26 | 0.011118 | 0.0027864
27 | 0.0092852 | 0.0023271
28 | 0.012142 | 0.003043
29 | 0.0066413 | 0.0016645
30 | 0.003564 | 0.00089323
31 | 0.0082154 | 0.002059
32 | 0.0061491 | 0.0015411
33 | 0.0061119 | 0.0015318
34 | 0.0052338 | 0.0013117
35 | 0.0052565 | 0.0013174
36 | 0.0061487 | 0.001541
37 | 0.0044981 | 0.0011273
38 | 0.0071675 | 0.0017963
39 | 0.0047126 | 0.0011811
40 | 0.0050317 | 0.0012611
41 | 0.0033739 | 0.00084558
42 | 0.0043091 | 0.00108
43 | 0.003969 | 0.00099472
44 | 0.012597 | 0.0031572

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1