## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-79_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-79_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-79_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-79_0_4_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_2196-79_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2196-79_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2196-79_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2196-79_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_2196-79_0_4_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_2196-79_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2196-79_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_2196-79_0_4_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_2196-79_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2196-79_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2196-79_0_4_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_2196-79_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_2196-79_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2196-79_0_4_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_2196-79_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2196-79_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2196-79_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2196-79_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_2196-79_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_2196-79_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2196-79_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2196-79_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_MV_376_0_node_43 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-79_0_4_load_0 | 0 | 0.015631 | 0.0039174 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-79_0_4_load_1 | 1 | 0.015634 | 0.0039183 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-79_0_4_load_25 | 6 | 0.00042738 | 0.00010711 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-79_0_4_load_24 | 8 | 0.01107 | 0.0027744 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-79_0_4_load_21 | 11 | 0.074185 | 0.018593 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-79_0_4_load_22 | 14 | 0.082647 | 0.020713 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-79_0_4_load_26 | 15 | 0.013573 | 0.0034017 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-79_0_4_load_27 | 17 | 0.085612 | 0.021456 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-79_0_4_load_17 | 19 | 0.020515 | 0.0051414 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-79_0_4_load_23 | 22 | 0.084425 | 0.021159 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-79_0_4_load_18 | 24 | 0.0069053 | 0.0017306 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-79_0_4_load_19 | 25 | 0.066741 | 0.016727 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-79_0_4_line_0 |  | 0 | 1 | 0.012424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-79_0_4_line_1 |  | 0 | 2 | 0.073955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-79_0_4_line_2 |  | 2 | 3 | 0.050978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-79_0_4_line_3 |  | 3 | 15 | 0.021446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-79_0_4_line_4 |  | 3 | 16 | 0.088198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-79_0_4_line_5 |  | 4 | 5 | 0.048176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-79_0_4_line_6 |  | 4 | 6 | 0.0079388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-79_0_4_line_7 |  | 5 | 7 | 0.19949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-79_0_4_line_8 |  | 5 | 8 | 0.03862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-79_0_4_line_9 |  | 7 | 9 | 0.052738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-79_0_4_line_10 |  | 9 | 10 | 0.050744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-79_0_4_line_11 |  | 9 | 11 | 0.041632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-79_0_4_line_12 |  | 10 | 14 | 0.02872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2196-79_0_4_line_13 |  | 10 | 16 | 0.022727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2196-79_0_4_line_14 |  | 12 | 13 | 0.05691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-79_0_4_line_15 |  | 12 | 14 | 0.041497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-79_0_4_line_16 |  | 13 | 17 | 0.010064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-79_0_4_line_17 |  | 16 | 22 | 0.032963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2196-79_0_4_line_18 |  | 16 | 18 | 0.11152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2196-79_0_4_line_19 |  | 18 | 19 | 0.029972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-79_0_4_line_20 |  | 19 | 24 | 0.037106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-79_0_4_line_21 |  | 20 | 21 | 0.090938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-79_0_4_line_22 |  | 20 | 22 | 0.016374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-79_0_4_line_23 |  | 21 | 23 | 0.011649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-79_0_4_line_24 |  | 23 | 25 | 0.049869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-79_0_4_trafo_22 | 0.63 MVA 20/0.4 kV | 26 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2577439.6947 | 1182859.6963 | 2577452.0267 | 1182858.1899
1 | 2577495.6213 | 1182826.1789 | 2577499.1406 | 1182852.4348 | 2577452.0267 | 1182858.1899
2 | 2577464.5164 | 1182807.5754 | 2577465.1894 | 1182813.9651 | 2577470.3791 | 1182813.4563 | 2577475.5996 | 1182813.0364 | 2577494.2353 | 1182810.8984 | 2577494.9443 | 1182818.722 | 2577495.6213 | 1182826.1789
3 | 2577464.5164 | 1182807.5754 | 2577463.3874 | 1182799.7534 | 2577476.8718 | 1182798.1461
4 | 2577387.7088 | 1182794.6702 | 2577389.4219 | 1182803.5017 | 2577389.8889 | 1182805.8567 | 2577394.93 | 1182806.449 | 2577396.5644 | 1182808.6106 | 2577399.1445 | 1182810.513 | 2577402.7992 | 1182811.9332 | 2577407.7237 | 1182811.9701 | 2577409.2883 | 1182811.8419 | 2577429.6905 | 1182810.464 | 2577464.5164 | 1182807.5754
5 | 2577487.016 | 1182653.8995 | 2577491.4287 | 1182649.7807 | 2577498.0583 | 1182656.5481 | 2577502.153 | 1182653.1198 | 2577515.3536 | 1182665.2764 | 2577518.1522 | 1182662.3643 | 2577521.8559 | 1182658.515
6 | 2577521.8559 | 1182658.515 | 2577518.2463 | 1182651.4443
7 | 2577378.7316 | 1182680.178 | 2577373.5361 | 1182648.9593 | 2577374.8741 | 1182647.4534 | 2577378.6793 | 1182646.2495 | 2577399.8546 | 1182643.2455 | 2577395.6371 | 1182626.3193 | 2577404.0806 | 1182624.1307 | 2577416.1745 | 1182620.1495 | 2577458.7167 | 1182606.1815 | 2577467.5089 | 1182621.5118 | 2577479.7458 | 1182637.2293 | 2577480.853 | 1182647.386 | 2577487.016 | 1182653.8995
8 | 2577487.016 | 1182653.8995 | 2577490.4578 | 1182657.5328 | 2577515.3567 | 1182680.1173
9 | 2577378.7316 | 1182680.178 | 2577366.9821 | 1182682.3126 | 2577369.6285 | 1182699.6671 | 2577373.8074 | 1182722.5298
10 | 2577373.8074 | 1182722.5298 | 2577374.7275 | 1182727.5957 | 2577375.6864 | 1182732.8281 | 2577380.1716 | 1182755.912 | 2577383.3718 | 1182772.364
11 | 2577373.8074 | 1182722.5298 | 2577412.2875 | 1182720.7832 | 2577411.825 | 1182717.7057
12 | 2577383.3718 | 1182772.364 | 2577411.856 | 1182768.6902
13 | 2577387.7088 | 1182794.6702 | 2577383.3718 | 1182772.364
14 | 2577452.8184 | 1182770.756 | 2577454.5039 | 1182768.2594 | 2577456.9095 | 1182766.4272 | 2577459.7765 | 1182765.4714 | 2577462.7999 | 1182765.4933 | 2577465.6515 | 1182766.4942 | 2577468.0252 | 1182768.3529 | 2577469.6686 | 1182770.8813 | 2577474.6005 | 1182768.8394 | 2577487.3596 | 1182763.1772 | 2577486.3969 | 1182760.9575 | 2577486.9456 | 1182758.6653 | 2577491.5154 | 1182751.6889 | 2577492.3811 | 1182748.4395
15 | 2577452.8184 | 1182770.756 | 2577445.7251 | 1182768.5483 | 2577426.4409 | 1182766.8092 | 2577411.856 | 1182768.6902
16 | 2577492.3811 | 1182748.4395 | 2577482.3055 | 1182749.0334
17 | 2577387.7088 | 1182794.6702 | 2577376.7676 | 1182796.4904 | 2577377.4266 | 1182801.157 | 2577376.2932 | 1182802.2508 | 2577360.7095 | 1182802.2655
18 | 2577387.7088 | 1182794.6702 | 2577389.4219 | 1182803.5017 | 2577389.8889 | 1182805.8567 | 2577391.284 | 1182813.3776 | 2577389.4309 | 1182813.9404 | 2577387.8395 | 1182815.047 | 2577386.662 | 1182816.5967 | 2577386.0199 | 1182818.4112 | 2577385.9662 | 1182820.3458 | 2577386.5 | 1182822.1891 | 2577387.5672 | 1182823.7859 | 2577389.0758 | 1182824.9808 | 2577390.8725 | 1182825.6633 | 2577392.7892 | 1182825.7672 | 2577393.9546 | 1182831.11 | 2577405.3539 | 1182897.8571
19 | 2577405.3539 | 1182897.8571 | 2577435.2741 | 1182896.0886
20 | 2577435.2741 | 1182896.0886 | 2577463.4244 | 1182894.4247 | 2577467.2181 | 1182890.2082 | 2577468.413 | 1182887.2021
21 | 2577293.3554 | 1182845.6883 | 2577293.7495 | 1182832.869 | 2577293.9875 | 1182825.1974 | 2577298.7055 | 1182825.1572 | 2577298.3343 | 1182817.8882 | 2577324.4012 | 1182816.4773 | 2577356.689 | 1182814.7205
22 | 2577356.689 | 1182814.7205 | 2577356.7868 | 1182802.2692 | 2577360.7095 | 1182802.2655
23 | 2577292.9951 | 1182857.329 | 2577293.3554 | 1182845.6883
24 | 2577292.9951 | 1182857.329 | 2577342.8529 | 1182858.3846

## bus_geodata
| x | y | coords
0 | 2577452.0267 | 1182858.1899
1 | 2577439.6947 | 1182859.6963
2 | 2577495.6213 | 1182826.1789
3 | 2577464.5164 | 1182807.5754
4 | 2577521.8559 | 1182658.515
5 | 2577487.016 | 1182653.8995
6 | 2577518.2463 | 1182651.4443
7 | 2577378.7316 | 1182680.178
8 | 2577515.3567 | 1182680.1173
9 | 2577373.8074 | 1182722.5298
10 | 2577383.3718 | 1182772.364
11 | 2577411.825 | 1182717.7057
12 | 2577452.8184 | 1182770.756
13 | 2577492.3811 | 1182748.4395
14 | 2577411.856 | 1182768.6902
15 | 2577476.8718 | 1182798.1461
16 | 2577387.7088 | 1182794.6702
17 | 2577482.3055 | 1182749.0334
18 | 2577405.3539 | 1182897.8571
19 | 2577435.2741 | 1182896.0886
20 | 2577356.689 | 1182814.7205
21 | 2577293.3554 | 1182845.6883
22 | 2577360.7095 | 1182802.2655
23 | 2577292.9951 | 1182857.329
24 | 2577468.413 | 1182887.2021
25 | 2577342.8529 | 1182858.3846
26 | 2577383.3718 | 1182772.364

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98774 | -0.23575 | 0.015631 | 0.0039174
1 | 0.98756 | -0.23922 | 0.015634 | 0.0039183
2 | 0.98986 | -0.19453 | 0 | 0
3 | 0.99133 | -0.16622 | 0 | 0
4 | 0.99063 | -0.18 | 0 | 0
5 | 0.99065 | -0.17964 | 0 | 0
6 | 0.99063 | -0.18006 | 0.00042738 | 0.00010711
7 | 0.99275 | -0.13896 | 0 | 0
8 | 0.99026 | -0.18723 | 0.01107 | 0.0027744
9 | 0.9933 | -0.12824 | 0 | 0
10 | 0.99728 | -0.051724 | 0 | 0
11 | 0.99048 | -0.18295 | 0.074185 | 0.018593
12 | 0.99675 | -0.062125 | 0 | 0
13 | 0.99229 | -0.14798 | 0 | 0
14 | 1 | 0 | -0.40016 | -0.10133
15 | 0.99106 | -0.17138 | 0.013573 | 0.0034017
16 | 0.99495 | -0.096325 | 0 | 0
17 | 0.99151 | -0.16325 | 0.085612 | 0.021456
18 | 0.99216 | -0.15032 | 0 | 0
19 | 0.99141 | -0.16488 | 0.020515 | 0.0051414
20 | 0.99166 | -0.15965 | 0 | 0
21 | 0.98605 | -0.26783 | 0 | 0
22 | 0.99267 | -0.14029 | 0.084425 | 0.021159
23 | 0.98533 | -0.28178 | 0 | 0
24 | 0.99117 | -0.16943 | 0.0069053 | 0.0017306
25 | 0.98226 | -0.34172 | 0.066741 | 0.016727
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.015637 | 0.0039198 | -0.015634 | -0.0039183 | 2.5853e-06 | 1.4956e-06 | 0.023557 | 0.023557 | 0.023557 | 0.98774 | -0.23575 | 0.98756 | -0.23922 | 6.4716
1 | -0.031267 | -0.0078372 | 0.031329 | 0.0078756 | 6.1534e-05 | 3.8433e-05 | 0.047104 | 0.047104 | 0.047104 | 0.98774 | -0.23575 | 0.98986 | -0.19453 | 12.9407
2 | -0.031329 | -0.0078756 | 0.031371 | 0.0079021 | 4.2416e-05 | 2.649e-05 | 0.047104 | 0.047104 | 0.047104 | 0.98986 | -0.19453 | 0.99133 | -0.16622 | 12.9406
3 | 0.013576 | 0.0034036 | -0.013573 | -0.0034017 | 3.3399e-06 | 1.8611e-06 | 0.020379 | 0.020379 | 0.020379 | 0.99133 | -0.16622 | 0.99106 | -0.17138 | 5.5986
4 | -0.044948 | -0.011306 | 0.045098 | 0.011401 | 0.00015061 | 9.5252e-05 | 0.067482 | 0.067482 | 0.067482 | 0.99133 | -0.16622 | 0.99495 | -0.096325 | 18.5391
5 | -0.00042738 | -0.00010701 | 0.00042738 | 0.00010639 | 7.4419e-09 | -6.155e-07 | 0.00064192 | 0.00064171 | 0.00064192 | 0.99063 | -0.18 | 0.99065 | -0.17964 | 0.17635
6 | 0.00042738 | 0.00010701 | -0.00042738 | -0.00010711 | 1.2268e-09 | -1.0142e-07 | 0.00064192 | 0.00064196 | 0.00064196 | 0.99063 | -0.18 | 0.99063 | -0.18006 | 0.17636
7 | -0.011502 | -0.0028829 | 0.011524 | 0.0028946 | 2.2327e-05 | 1.1715e-05 | 0.017276 | 0.017275 | 0.017276 | 0.99065 | -0.17964 | 0.99275 | -0.13896 | 4.7462
8 | 0.011074 | 0.0027765 | -0.01107 | -0.0027744 | 4.0075e-06 | 2.0677e-06 | 0.016635 | 0.016635 | 0.016635 | 0.99065 | -0.17964 | 0.99026 | -0.18723 | 4.57
9 | -0.011524 | -0.0028946 | 0.01153 | 0.0028977 | 5.9021e-06 | 3.095e-06 | 0.017275 | 0.017275 | 0.017275 | 0.99275 | -0.13896 | 0.9933 | -0.12824 | 4.746
10 | -0.085909 | -0.021614 | 0.086224 | 0.021815 | 0.00031531 | 0.00020114 | 0.12872 | 0.12872 | 0.12872 | 0.9933 | -0.12824 | 0.99728 | -0.051724 | 35.364
11 | 0.074379 | 0.018716 | -0.074185 | -0.018593 | 0.00019392 | 0.00012357 | 0.11145 | 0.11145 | 0.11145 | 0.9933 | -0.12824 | 0.99048 | -0.18295 | 30.6182
12 | -0.31145 | -0.078954 | 0.31223 | 0.07945 | 0.00077632 | 0.00049572 | 0.46502 | 0.46502 | 0.46502 | 0.99728 | -0.051724 | 1 | 0 | 42.5843
13 | 0.22523 | 0.057139 | -0.22474 | -0.056831 | 0.00048193 | 0.00030785 | 0.3363 | 0.3363 | 0.3363 | 0.99728 | -0.051724 | 0.99495 | -0.096325 | 46.1946
14 | 0.086027 | 0.021721 | -0.085674 | -0.021496 | 0.0003523 | 0.00022473 | 0.12848 | 0.12848 | 0.12848 | 0.99675 | -0.062125 | 0.99229 | -0.14798 | 35.2976
15 | -0.086027 | -0.021721 | 0.086283 | 0.021885 | 0.00025689 | 0.00016386 | 0.12848 | 0.12848 | 0.12848 | 0.99675 | -0.062125 | 1 | 0 | 35.2975
16 | 0.085674 | 0.021496 | -0.085612 | -0.021456 | 6.2301e-05 | 3.9743e-05 | 0.12848 | 0.12848 | 0.12848 | 0.99229 | -0.14798 | 0.99151 | -0.16325 | 35.2976
17 | 0.15213 | 0.038502 | -0.15181 | -0.038298 | 0.00032033 | 0.00020416 | 0.22766 | 0.22766 | 0.22766 | 0.99495 | -0.096325 | 0.99267 | -0.14029 | 31.2718
18 | 0.027511 | 0.0069282 | -0.02744 | -0.0068843 | 7.0835e-05 | 4.389e-05 | 0.041157 | 0.041157 | 0.041157 | 0.99495 | -0.096325 | 0.99216 | -0.15032 | 11.3069
19 | 0.02744 | 0.0068843 | -0.027421 | -0.0068725 | 1.9039e-05 | 1.1798e-05 | 0.041157 | 0.041157 | 0.041157 | 0.99216 | -0.15032 | 0.99141 | -0.16488 | 11.3069
20 | 0.0069068 | 0.0017311 | -0.0069053 | -0.0017306 | 1.4954e-06 | 4.7868e-07 | 0.010367 | 0.010367 | 0.010367 | 0.99141 | -0.16488 | 0.99117 | -0.16943 | 2.848
21 | 0.067326 | 0.017099 | -0.066977 | -0.016877 | 0.00034859 | 0.00022193 | 0.1011 | 0.10111 | 0.10111 | 0.99166 | -0.15965 | 0.98605 | -0.26783 | 27.7761
22 | -0.067326 | -0.017099 | 0.067388 | 0.017139 | 6.2768e-05 | 3.996e-05 | 0.1011 | 0.1011 | 0.1011 | 0.99166 | -0.15965 | 0.99267 | -0.14029 | 27.776
23 | 0.066977 | 0.016877 | -0.066932 | -0.016849 | 4.4655e-05 | 2.843e-05 | 0.10111 | 0.10111 | 0.10111 | 0.98605 | -0.26783 | 0.98533 | -0.28178 | 27.7761
24 | 0.066932 | 0.016849 | -0.066741 | -0.016727 | 0.00019116 | 0.00012171 | 0.10111 | 0.10111 | 0.10111 | 0.98533 | -0.28178 | 0.98226 | -0.34172 | 27.7762

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48281 | 0.12205

## res_load
| p_mw | q_mvar
0 | 0.015631 | 0.0039174
1 | 0.015634 | 0.0039183
2 | 0.00042738 | 0.00010711
3 | 0.01107 | 0.0027744
4 | 0.074185 | 0.018593
5 | 0.082647 | 0.020713
6 | 0.013573 | 0.0034017
7 | 0.085612 | 0.021456
8 | 0.020515 | 0.0051414
9 | 0.084425 | 0.021159
10 | 0.0069053 | 0.0017306
11 | 0.066741 | 0.016727

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1