## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-81_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-81_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-81_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-81_0_4_node_36 | 0.4 | n |  | TRUE
4 | bus_LV_2196-81_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2196-81_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2196-81_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2196-81_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2196-81_0_4_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_2196-81_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2196-81_0_4_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_2196-81_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2196-81_0_4_node_32 | 0.4 | n |  | TRUE
13 | bus_LV_2196-81_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2196-81_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2196-81_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2196-81_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2196-81_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2196-81_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2196-81_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2196-81_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2196-81_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2196-81_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2196-81_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2196-81_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2196-81_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2196-81_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_2196-81_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2196-81_0_4_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_2196-81_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2196-81_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_2196-81_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2196-81_0_4_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_2196-81_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_2196-81_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_MV_376_0_node_54 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-81_0_4_load_0 | 0 | 0.00091086 | 0.00022828 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-81_0_4_load_1 | 1 | 0.0021004 | 0.0005264 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-81_0_4_load_36 | 3 | 0.035664 | 0.0089383 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-81_0_4_load_3 | 4 | 0.016399 | 0.00411 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-81_0_4_load_4 | 5 | 0.024443 | 0.0061259 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-81_0_4_load_5 | 6 | 0.0036836 | 0.00092321 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-81_0_4_load_6 | 7 | 0.03716 | 0.0093132 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-81_0_4_load_7 | 9 | 0.031461 | 0.0078848 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-81_0_4_load_31 | 10 | 0.015179 | 0.0038043 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-81_0_4_load_8 | 11 | 0.010081 | 0.0025266 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-81_0_4_load_32 | 12 | 0.0017895 | 0.00044849 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-81_0_4_load_10 | 14 | 0.0098687 | 0.0024733 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-81_0_4_load_11 | 15 | 0.0014719 | 0.0003689 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-81_0_4_load_12 | 16 | 0.0024212 | 0.00060682 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-81_0_4_load_13 | 17 | 0.0032813 | 0.00082238 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-81_0_4_load_14 | 18 | 0.0034934 | 0.00087553 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-81_0_4_load_15 | 19 | 0.0044702 | 0.0011203 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-81_0_4_load_18 | 22 | 0.0095736 | 0.0023994 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-81_0_4_load_21 | 23 | 0.054366 | 0.013626 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-81_0_4_load_30 | 28 | 0.017906 | 0.0044877 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-81_0_4_load_26 | 31 | 0.022231 | 0.0055717 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-81_0_4_load_37 | 32 | 0.029332 | 0.0073514 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-81_0_4_load_27 | 33 | 0.043227 | 0.010834 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-81_0_4_load_25 | 34 | 0.016511 | 0.004138 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-81_0_4_line_0 |  | 0 | 1 | 0.026143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-81_0_4_line_1 |  | 0 | 2 | 0.020882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2196-81_0_4_line_2 |  | 0 | 3 | 0.11209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-81_0_4_line_3 |  | 1 | 4 | 0.019778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-81_0_4_line_4 |  | 2 | 5 | 0.013868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2196-81_0_4_line_5 |  | 2 | 6 | 0.074702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-81_0_4_line_6 |  | 4 | 7 | 0.017057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-81_0_4_line_7 |  | 5 | 8 | 0.0027958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2196-81_0_4_line_8 |  | 7 | 9 | 0.029522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-81_0_4_line_9 |  | 8 | 10 | 0.008063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2196-81_0_4_line_10 |  | 9 | 11 | 0.041579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-81_0_4_line_11 |  | 9 | 12 | 0.17261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-81_0_4_line_12 |  | 10 | 28 | 0.00018774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2196-81_0_4_line_13 |  | 11 | 13 | 0.019474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-81_0_4_line_14 |  | 13 | 14 | 0.027545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-81_0_4_line_15 |  | 14 | 15 | 0.036754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-81_0_4_line_16 |  | 15 | 16 | 0.01934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-81_0_4_line_17 |  | 16 | 17 | 0.020177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-81_0_4_line_18 |  | 17 | 18 | 0.019045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2196-81_0_4_line_19 |  | 19 | 20 | 0.045686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2196-81_0_4_line_20 |  | 19 | 21 | 0.020463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2196-81_0_4_line_21 |  | 20 | 22 | 0.043582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2196-81_0_4_line_22 |  | 21 | 23 | 0.02584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2196-81_0_4_line_23 |  | 22 | 24 | 0.050322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2196-81_0_4_line_24 |  | 23 | 27 | 0.0036102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2196-81_0_4_line_25 |  | 24 | 25 | 0.046162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2196-81_0_4_line_26 |  | 25 | 26 | 0.075015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_2196-81_0_4_line_27 |  | 26 | 33 | 0.068415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-81_0_4_line_28 |  | 26 | 30 | 0.055756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-81_0_4_line_29 |  | 27 | 28 | 0.021087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2196-81_0_4_line_30 |  | 29 | 30 | 0.015669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-81_0_4_line_31 |  | 29 | 31 | 0.029669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2196-81_0_4_line_32 |  | 30 | 32 | 0.018912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2196-81_0_4_line_33 |  | 31 | 34 | 0.054577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-81_0_4_trafo_0 | 0.63 MVA 20/0.4 kV | 35 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2577772.5799 | 1182557.3018 | 2577763.9246 | 1182539.4132 | 2577760.4893 | 1182534.1676
1 | 2577781.675 | 1182576.0995 | 2577772.5799 | 1182557.3018
2 | 2577772.5799 | 1182557.3018 | 2577870.0062 | 1182501.8792
3 | 2577760.4893 | 1182534.1676 | 2577749.654 | 1182517.6222
4 | 2577781.675 | 1182576.0995 | 2577787.7136 | 1182588.5837
5 | 2577709.0902 | 1182594.602 | 2577781.675 | 1182576.0995
6 | 2577749.654 | 1182517.6222 | 2577740.3094 | 1182503.3531
7 | 2577788.4808 | 1182591.271 | 2577787.7457 | 1182588.6501 | 2577787.7136 | 1182588.5837
8 | 2577740.3094 | 1182503.3531 | 2577736.189 | 1182497.0613 | 2577721.6137 | 1182480.5809
9 | 2577788.4808 | 1182591.271 | 2577790.6647 | 1182599.0326
10 | 2577721.6137 | 1182480.5809 | 2577695.4136 | 1182450.9562 | 2577693.8608 | 1182449.6478
11 | 2577721.6137 | 1182480.5809 | 2577857.9062 | 1182374.6647
12 | 2577790.7156 | 1182599.2133 | 2577790.6647 | 1182599.0326
13 | 2577678.9692 | 1182437.0993 | 2577693.8608 | 1182449.6478
14 | 2577678.9692 | 1182437.0993 | 2577657.9064 | 1182419.3489
15 | 2577657.9064 | 1182419.3489 | 2577648.4086 | 1182411.3447 | 2577627.724 | 1182398.5275
16 | 2577627.724 | 1182398.5275 | 2577611.2841 | 1182388.3405
17 | 2577611.2841 | 1182388.3405 | 2577606.9833 | 1182385.6755 | 2577592.5797 | 1182381.084
18 | 2577574.4347 | 1182375.2998 | 2577592.5797 | 1182381.084
19 | 2577822.3077 | 1182711.5411 | 2577809.9372 | 1182667.5622
20 | 2577804.3963 | 1182647.8634 | 2577809.9372 | 1182667.5622
21 | 2577822.3077 | 1182711.5411 | 2577817.4213 | 1182713.5492 | 2577816.4784 | 1182722.8019 | 2577788.6134 | 1182730.8309
22 | 2577804.3963 | 1182647.8634 | 2577797.4039 | 1182622.9871
23 | 2577740.2588 | 1182744.7637 | 2577788.6134 | 1182730.8309
24 | 2577796.4269 | 1182619.5117 | 2577797.4039 | 1182622.9871
25 | 2577711.2246 | 1182730.6203 | 2577715.6679 | 1182744.9111 | 2577717.9398 | 1182752.2287 | 2577740.2588 | 1182744.7637
26 | 2577693.737 | 1182658.059 | 2577693.3273 | 1182658.7609 | 2577693.1257 | 1182659.9845 | 2577693.2324 | 1182661.974 | 2577694.5771 | 1182666.3157 | 2577696.6609 | 1182674.3565 | 2577711.2246 | 1182730.6203
27 | 2577693.737 | 1182658.059 | 2577688.8249 | 1182659.3335 | 2577685.9025 | 1182659.8003 | 2577682.9408 | 1182659.967 | 2577679.6577 | 1182659.9348 | 2577663.0366 | 1182663.9768 | 2577627.4944 | 1182674.3536
28 | 2577693.737 | 1182658.059 | 2577693.9873 | 1182657.6356 | 2577694.8025 | 1182657.1656 | 2577704.3059 | 1182654.5955 | 2577707.5412 | 1182654.1054 | 2577713.3377 | 1182654.5506 | 2577703.6746 | 1182620.5023
29 | 2577796.4269 | 1182619.5117 | 2577790.7156 | 1182599.2133
30 | 2577703.6746 | 1182620.5023 | 2577701.6071 | 1182612.7505 | 2577708.967 | 1182610.6775
31 | 2577708.967 | 1182610.6775 | 2577717.4811 | 1182639.0988
32 | 2577703.6746 | 1182620.5023 | 2577685.3926 | 1182625.5399
33 | 2577749.0959 | 1182661.3603 | 2577726.285 | 1182668.4873 | 2577717.4811 | 1182639.0988

## bus_geodata
| x | y | coords
0 | 2577772.5799 | 1182557.3018
1 | 2577760.4893 | 1182534.1676
2 | 2577781.675 | 1182576.0995
3 | 2577870.0062 | 1182501.8792
4 | 2577749.654 | 1182517.6222
5 | 2577787.7136 | 1182588.5837
6 | 2577709.0902 | 1182594.602
7 | 2577740.3094 | 1182503.3531
8 | 2577788.4808 | 1182591.271
9 | 2577721.6137 | 1182480.5809
10 | 2577790.6647 | 1182599.0326
11 | 2577693.8608 | 1182449.6478
12 | 2577857.9062 | 1182374.6647
13 | 2577678.9692 | 1182437.0993
14 | 2577657.9064 | 1182419.3489
15 | 2577627.724 | 1182398.5275
16 | 2577611.2841 | 1182388.3405
17 | 2577592.5797 | 1182381.084
18 | 2577574.4347 | 1182375.2998
19 | 2577809.9372 | 1182667.5622
20 | 2577822.3077 | 1182711.5411
21 | 2577804.3963 | 1182647.8634
22 | 2577788.6134 | 1182730.8309
23 | 2577797.4039 | 1182622.9871
24 | 2577740.2588 | 1182744.7637
25 | 2577711.2246 | 1182730.6203
26 | 2577693.737 | 1182658.059
27 | 2577796.4269 | 1182619.5117
28 | 2577790.7156 | 1182599.2133
29 | 2577708.967 | 1182610.6775
30 | 2577703.6746 | 1182620.5023
31 | 2577717.4811 | 1182639.0988
32 | 2577685.3926 | 1182625.5399
33 | 2577627.4944 | 1182674.3536
34 | 2577749.0959 | 1182661.3603
35 | 2577781.675 | 1182576.0995

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.4024 | -0.10222
1 | 0.99714 | -0.054626 | 0.0021004 | 0.0005264
2 | 0.99768 | -0.043953 | 0 | 0
3 | 0.99636 | -0.069932 | 0.035664 | 0.0089383
4 | 0.99502 | -0.095428 | 0.016399 | 0.00411
5 | 0.99616 | -0.072805 | 0.024443 | 0.0061259
6 | 0.99743 | -0.048774 | 0.0036836 | 0.00092321
7 | 0.99344 | -0.12582 | 0.03716 | 0.0093132
8 | 0.99588 | -0.078032 | 0 | 0
9 | 0.99172 | -0.15918 | 0.031461 | 0.0078848
10 | 0.99509 | -0.093123 | 0.015179 | 0.0038043
11 | 0.99055 | -0.18177 | 0.010081 | 0.0025266
12 | 0.99144 | -0.16466 | 0.0017895 | 0.00044849
13 | 0.99019 | -0.18888 | 0 | 0
14 | 0.98967 | -0.19894 | 0.0098687 | 0.0024733
15 | 0.98931 | -0.20592 | 0.0014719 | 0.0003689
16 | 0.98915 | -0.20909 | 0.0024212 | 0.00060682
17 | 0.98902 | -0.21153 | 0.0032813 | 0.00082238
18 | 0.98896 | -0.21271 | 0.0034934 | 0.00087553
19 | 0.99031 | -0.18404 | 0.0044702 | 0.0011203
20 | 0.98773 | -0.23325 | 0 | 0
21 | 0.99151 | -0.16127 | 0 | 0
22 | 0.98528 | -0.28043 | 0.0095736 | 0.0023994
23 | 0.99302 | -0.1326 | 0.054366 | 0.013626
24 | 0.98266 | -0.33085 | 0 | 0
25 | 0.98026 | -0.37734 | 0 | 0
26 | 0.97637 | -0.45337 | 0 | 0
27 | 0.99332 | -0.12687 | 0 | 0
28 | 0.99507 | -0.093449 | 0.017906 | 0.0044877
29 | 0.97226 | -0.53421 | 0 | 0
30 | 0.97283 | -0.52303 | 0 | 0
31 | 0.97119 | -0.55543 | 0.022231 | 0.0055717
32 | 0.97231 | -0.53325 | 0.029332 | 0.0073514
33 | 0.97362 | -0.5076 | 0.043227 | 0.010834
34 | 0.97034 | -0.5721 | 0.016511 | 0.004138
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12038 | 0.030495 | -0.12006 | -0.030293 | 0.00031495 | 0.00020123 | 0.17924 | 0.17924 | 0.17924 | 1 | 0 | 0.99714 | -0.054626 | 49.2414
1 | 0.24459 | 0.062713 | -0.24407 | -0.062381 | 0.00052008 | 0.0003323 | 0.36445 | 0.36445 | 0.36445 | 1 | 0 | 0.99768 | -0.043953 | 50.0624
2 | 0.035783 | 0.0090131 | -0.035664 | -0.0089383 | 0.00011924 | 7.485e-05 | 0.053262 | 0.053263 | 0.053263 | 1 | 0 | 0.99636 | -0.069932 | 14.6326
3 | 0.11796 | 0.029767 | -0.11773 | -0.02962 | 0.00023001 | 0.00014695 | 0.1761 | 0.1761 | 0.1761 | 0.99714 | -0.054626 | 0.99502 | -0.095428 | 48.3803
4 | 0.24038 | 0.061458 | -0.24005 | -0.061244 | 0.00033504 | 0.00021407 | 0.35896 | 0.35896 | 0.35896 | 0.99768 | -0.043953 | 0.99616 | -0.072805 | 49.3076
5 | 0.0036845 | 0.00092277 | -0.0036836 | -0.00092321 | 8.4595e-07 | -4.3384e-07 | 0.0054951 | 0.0054955 | 0.0054955 | 0.99768 | -0.043953 | 0.99743 | -0.048774 | 1.5097
6 | 0.10133 | 0.02551 | -0.10119 | -0.025416 | 0.00014696 | 9.3835e-05 | 0.15158 | 0.15158 | 0.15158 | 0.99502 | -0.095428 | 0.99344 | -0.12582 | 41.6429
7 | 0.21561 | 0.055118 | -0.21555 | -0.055084 | 5.4504e-05 | 3.481e-05 | 0.32245 | 0.32245 | 0.32245 | 0.99616 | -0.072805 | 0.99588 | -0.078032 | 44.2923
8 | 0.064026 | 0.016103 | -0.063924 | -0.016038 | 0.00010186 | 6.4809e-05 | 0.095921 | 0.095921 | 0.095921 | 0.99344 | -0.12582 | 0.99172 | -0.15918 | 26.3519
9 | 0.21555 | 0.055084 | -0.2154 | -0.054983 | 0.00015719 | 0.00010039 | 0.32245 | 0.32245 | 0.32245 | 0.99588 | -0.078032 | 0.99509 | -0.093123 | 44.2923
10 | 0.030674 | 0.0077069 | -0.030641 | -0.0076863 | 3.3038e-05 | 2.0608e-05 | 0.046031 | 0.046031 | 0.046031 | 0.99172 | -0.15918 | 0.99055 | -0.18177 | 12.646
11 | 0.00179 | 0.00044657 | -0.0017895 | -0.00044849 | 4.6679e-07 | -1.9278e-06 | 0.002685 | 0.0026858 | 0.0026858 | 0.99172 | -0.15918 | 0.99144 | -0.16466 | 0.73786
12 | 0.20022 | 0.051179 | -0.20021 | -0.051177 | 3.1628e-06 | 2.0193e-06 | 0.29975 | 0.29975 | 0.29975 | 0.99509 | -0.093123 | 0.99507 | -0.093449 | 41.1745
13 | 0.020559 | 0.0051597 | -0.020552 | -0.0051555 | 6.9667e-06 | 4.2081e-06 | 0.030887 | 0.030887 | 0.030887 | 0.99055 | -0.18177 | 0.99019 | -0.18888 | 8.4854
14 | 0.020552 | 0.0051555 | -0.020543 | -0.0051495 | 9.8543e-06 | 5.9526e-06 | 0.030887 | 0.030887 | 0.030887 | 0.99019 | -0.18888 | 0.98967 | -0.19894 | 8.4855
15 | 0.010674 | 0.0026762 | -0.01067 | -0.0026744 | 3.5501e-06 | 1.8e-06 | 0.016049 | 0.016049 | 0.016049 | 0.98967 | -0.19894 | 0.98931 | -0.20592 | 4.4091
16 | 0.0091984 | 0.0023055 | -0.009197 | -0.0023049 | 1.3883e-06 | 6.402e-07 | 0.013835 | 0.013835 | 0.013835 | 0.98931 | -0.20592 | 0.98915 | -0.20909 | 3.8009
17 | 0.0067757 | 0.001698 | -0.006775 | -0.0016978 | 7.8614e-07 | 2.4417e-07 | 0.010193 | 0.010193 | 0.010193 | 0.98915 | -0.20909 | 0.98902 | -0.21153 | 2.8003
18 | 0.0034936 | 0.00087542 | -0.0034934 | -0.00087553 | 1.9731e-07 | -1.181e-07 | 0.0052562 | 0.0052563 | 0.0052563 | 0.98902 | -0.21153 | 0.98896 | -0.21271 | 1.444
19 | 0.12281 | 0.031521 | -0.12251 | -0.031334 | 0.00029251 | 0.00018604 | 0.18479 | 0.18479 | 0.18479 | 0.99031 | -0.18404 | 0.98773 | -0.23325 | 25.3836
20 | -0.12728 | -0.032641 | 0.12742 | 0.03273 | 0.00014072 | 8.9532e-05 | 0.19151 | 0.19151 | 0.19151 | 0.99031 | -0.18404 | 0.99151 | -0.16127 | 26.3061
21 | 0.12251 | 0.031334 | -0.12223 | -0.031157 | 0.00027905 | 0.00017748 | 0.18479 | 0.18479 | 0.18479 | 0.98773 | -0.23325 | 0.98528 | -0.28043 | 25.3836
22 | -0.12742 | -0.03273 | 0.12759 | 0.032843 | 0.00017769 | 0.00011306 | 0.19151 | 0.19151 | 0.19151 | 0.99151 | -0.16127 | 0.99302 | -0.1326 | 26.3061
23 | 0.11266 | 0.028758 | -0.11239 | -0.028584 | 0.00027376 | 0.00017393 | 0.17033 | 0.17033 | 0.17033 | 0.98528 | -0.28043 | 0.98266 | -0.33085 | 23.3976
24 | -0.18196 | -0.046469 | 0.18201 | 0.046501 | 5.044e-05 | 3.2188e-05 | 0.27297 | 0.27297 | 0.27297 | 0.99302 | -0.1326 | 0.99332 | -0.12687 | 37.4964
25 | 0.11239 | 0.028584 | -0.11214 | -0.028424 | 0.00025113 | 0.00015955 | 0.17033 | 0.17034 | 0.17034 | 0.98266 | -0.33085 | 0.98026 | -0.37734 | 23.3977
26 | 0.11214 | 0.028424 | -0.11173 | -0.028165 | 0.00040809 | 0.0002593 | 0.17034 | 0.17034 | 0.17034 | 0.98026 | -0.37734 | 0.97637 | -0.45337 | 23.3978
27 | 0.043339 | 0.010905 | -0.043227 | -0.010834 | 0.00011198 | 7.0814e-05 | 0.066066 | 0.066066 | 0.066066 | 0.97637 | -0.45337 | 0.97362 | -0.5076 | 18.15
28 | 0.068389 | 0.01726 | -0.068162 | -0.017115 | 0.00022733 | 0.00014479 | 0.10427 | 0.10427 | 0.10427 | 0.97637 | -0.45337 | 0.97283 | -0.52303 | 28.6457
29 | -0.18201 | -0.046501 | 0.18231 | 0.046689 | 0.00029461 | 0.000188 | 0.27297 | 0.27297 | 0.27297 | 0.99332 | -0.12687 | 0.99507 | -0.093449 | 37.4964
30 | -0.038794 | -0.0097421 | 0.038815 | 0.0097552 | 2.0719e-05 | 1.3066e-05 | 0.059381 | 0.059381 | 0.059381 | 0.97226 | -0.53421 | 0.97283 | -0.52303 | 16.3134
31 | 0.038794 | 0.0097421 | -0.038755 | -0.0097174 | 3.9231e-05 | 2.474e-05 | 0.059381 | 0.059381 | 0.059381 | 0.97226 | -0.53421 | 0.97119 | -0.55543 | 16.3134
32 | 0.029347 | 0.0073603 | -0.029332 | -0.0073514 | 1.4291e-05 | 8.9116e-06 | 0.04489 | 0.04489 | 0.04489 | 0.97283 | -0.52303 | 0.97231 | -0.53325 | 12.3324
33 | 0.016524 | 0.0041457 | -0.016511 | -0.004138 | 1.312e-05 | 7.7221e-06 | 0.025319 | 0.025319 | 0.025319 | 0.97119 | -0.55543 | 0.97034 | -0.5721 | 6.9558

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40331 | 0.10245

## res_load
| p_mw | q_mvar
0 | 0.00091086 | 0.00022828
1 | 0.0021004 | 0.0005264
2 | 0.035664 | 0.0089383
3 | 0.016399 | 0.00411
4 | 0.024443 | 0.0061259
5 | 0.0036836 | 0.00092321
6 | 0.03716 | 0.0093132
7 | 0.031461 | 0.0078848
8 | 0.015179 | 0.0038043
9 | 0.010081 | 0.0025266
10 | 0.0017895 | 0.00044849
11 | 0.0098687 | 0.0024733
12 | 0.0014719 | 0.0003689
13 | 0.0024212 | 0.00060682
14 | 0.0032813 | 0.00082238
15 | 0.0034934 | 0.00087553
16 | 0.0044702 | 0.0011203
17 | 0.0095736 | 0.0023994
18 | 0.054366 | 0.013626
19 | 0.017906 | 0.0044877
20 | 0.022231 | 0.0055717
21 | 0.029332 | 0.0073514
22 | 0.043227 | 0.010834
23 | 0.016511 | 0.004138

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1