## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-84_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-84_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-84_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-84_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2196-84_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2196-84_0_4_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_2196-84_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_2196-84_0_4_node_45 | 0.4 | n |  | TRUE
8 | bus_LV_2196-84_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2196-84_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_2196-84_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_2196-84_0_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_2196-84_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2196-84_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_2196-84_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2196-84_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2196-84_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2196-84_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2196-84_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_2196-84_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2196-84_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2196-84_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_2196-84_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2196-84_0_4_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_2196-84_0_4_node_39 | 0.4 | n |  | TRUE
25 | bus_LV_2196-84_0_4_node_40 | 0.4 | n |  | TRUE
26 | bus_LV_2196-84_0_4_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_2196-84_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2196-84_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2196-84_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_2196-84_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2196-84_0_4_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_2196-84_0_4_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_2196-84_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_2196-84_0_4_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_2196-84_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_2196-84_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2196-84_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2196-84_0_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_2196-84_0_4_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_2196-84_0_4_node_44 | 0.4 | n |  | TRUE
41 | bus_MV_382_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-84_0_4_load_0 | 0 | 0.021962 | 0.0055041 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-84_0_4_load_2 | 2 | 0.051369 | 0.012874 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-84_0_4_load_13 | 5 | 0.0089145 | 0.0022342 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-84_0_4_load_10 | 6 | 0.015661 | 0.003925 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-84_0_4_load_45 | 7 | 0.013681 | 0.0034287 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-84_0_4_load_12 | 10 | 0.015854 | 0.0039734 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-84_0_4_load_28 | 11 | 0.008447 | 0.002117 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-84_0_4_load_8 | 12 | 0.010488 | 0.0026285 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-84_0_4_load_17 | 13 | 0.0083977 | 0.0021047 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-84_0_4_load_7 | 14 | 0.0092851 | 0.0023271 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-84_0_4_load_9 | 15 | 0.006958 | 0.0017438 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-84_0_4_load_11 | 16 | 0.006886 | 0.0017258 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-84_0_4_load_22 | 17 | 0.0079948 | 0.0020037 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-84_0_4_load_24 | 18 | 0.0047502 | 0.0011905 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-84_0_4_load_14 | 19 | 0.024967 | 0.0062572 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-84_0_4_load_15 | 20 | 0.0075191 | 0.0018845 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-84_0_4_load_16 | 21 | 0.0085719 | 0.0021483 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-84_0_4_load_18 | 22 | 0.011682 | 0.0029278 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-84_0_4_load_39 | 24 | 0.020277 | 0.005082 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-84_0_4_load_40 | 25 | 0.016435 | 0.0041189 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-84_0_4_load_41 | 26 | 0.013814 | 0.0034621 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-84_0_4_load_23 | 27 | 0.0059127 | 0.0014819 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-84_0_4_load_26 | 29 | 0.026101 | 0.0065415 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-84_0_4_load_27 | 30 | 0.0060341 | 0.0015123 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2196-84_0_4_load_42 | 31 | 0.017887 | 0.004483 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2196-84_0_4_load_35 | 32 | 0.010691 | 0.0026795 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2196-84_0_4_load_34 | 34 | 0.010784 | 0.0027028 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2196-84_0_4_load_32 | 35 | 0.0096421 | 0.0024165 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2196-84_0_4_load_30 | 36 | 0.0081344 | 0.0020387 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2196-84_0_4_load_31 | 37 | 0.0081438 | 0.002041 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2196-84_0_4_load_36 | 38 | 0.020659 | 0.0051776 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2196-84_0_4_load_43 | 39 | 0.012603 | 0.0031587 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2196-84_0_4_load_44 | 40 | 0.02517 | 0.0063083 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-84_0_4_line_0 |  | 0 | 1 | 0.013628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2196-84_0_4_line_1 |  | 0 | 2 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2196-84_0_4_line_2 |  | 1 | 3 | 0.0149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2196-84_0_4_line_3 |  | 2 | 4 | 0.011921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-84_0_4_line_4 |  | 3 | 5 | 0.014457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2196-84_0_4_line_5 |  | 3 | 6 | 0.012364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-84_0_4_line_6 |  | 4 | 7 | 0.016664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2196-84_0_4_line_7 |  | 5 | 11 | 0.0055719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-84_0_4_line_8 |  | 6 | 12 | 0.00059053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-84_0_4_line_9 |  | 8 | 9 | 0.004261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-84_0_4_line_10 |  | 8 | 10 | 0.012886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-84_0_4_line_11 |  | 9 | 13 | 0.010293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2196-84_0_4_line_12 |  | 12 | 14 | 0.01925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-84_0_4_line_13 |  | 13 | 20 | 0.00096862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-84_0_4_line_14 |  | 14 | 15 | 0.00026338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2196-84_0_4_line_15 |  | 15 | 16 | 4.5714e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2196-84_0_4_line_16 |  | 16 | 17 | 0.00051631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2196-84_0_4_line_17 |  | 17 | 18 | 1.2713e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2196-84_0_4_line_18 |  | 18 | 27 | 0.00010532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2196-84_0_4_line_19 |  | 19 | 20 | 0.018382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-84_0_4_line_20 |  | 19 | 21 | 0.0012473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-84_0_4_line_21 |  | 21 | 22 | 0.00078413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2196-84_0_4_line_22 |  | 22 | 23 | 0.014619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2196-84_0_4_line_23 |  | 23 | 24 | 0.0090163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2196-84_0_4_line_24 |  | 23 | 25 | 0.0022737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2196-84_0_4_line_25 |  | 24 | 26 | 0.0091833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-84_0_4_line_26 |  | 25 | 31 | 0.010614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2196-84_0_4_line_27 |  | 27 | 28 | 0.014808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2196-84_0_4_line_28 |  | 28 | 29 | 0.0064413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2196-84_0_4_line_29 |  | 28 | 30 | 0.0056152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-84_0_4_line_30 |  | 29 | 31 | 0.016184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2196-84_0_4_line_31 |  | 30 | 32 | 0.0063165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2196-84_0_4_line_32 |  | 32 | 33 | 0.0051969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2196-84_0_4_line_33 |  | 33 | 38 | 0.0065866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2196-84_0_4_line_34 |  | 33 | 37 | 0.0020681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2196-84_0_4_line_35 |  | 34 | 35 | 0.0046766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2196-84_0_4_line_36 |  | 35 | 36 | 0.0060679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2196-84_0_4_line_37 |  | 36 | 37 | 0.0057765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2196-84_0_4_line_38 |  | 38 | 39 | 0.0098863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2196-84_0_4_line_39 |  | 39 | 40 | 0.012848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-84_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 41 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2579062.2605 | 1183899.2245 | 2579050.7954 | 1183906.5918
1 | 2579036.7401 | 1183915.8561 | 2579039.9075 | 1183913.5882 | 2579050.7954 | 1183906.5918
2 | 2579058.0121 | 1183884.9431 | 2579062.2605 | 1183899.2245
3 | 2579036.7401 | 1183915.8561 | 2579029.0109 | 1183921.1193 | 2579026.8634 | 1183922.5721
4 | 2579058.0121 | 1183884.9431 | 2579072.3449 | 1183883.0515
5 | 2579058.0121 | 1183884.9431 | 2579056.2298 | 1183879.5243 | 2579054.8814 | 1183873.003
6 | 2579026.8634 | 1183922.5721 | 2579018.6238 | 1183928.1262 | 2579013.1077 | 1183931.9775
7 | 2579072.3449 | 1183883.0515 | 2579077.8689 | 1183882.3225
8 | 2579054.7619 | 1183872.4247 | 2579054.8814 | 1183873.003
9 | 2579024.5215 | 1183890.4414 | 2579025.1406 | 1183892.8293 | 2579026.8331 | 1183892.2342
10 | 2579026.8331 | 1183892.2342 | 2579030.7216 | 1183890.9865 | 2579039.2052 | 1183888.6414
11 | 2579024.5215 | 1183890.4414 | 2579021.9509 | 1183880.4748
12 | 2579050.8642 | 1183853.5739 | 2579050.9262 | 1183853.874 | 2579054.7619 | 1183872.4247
13 | 2579021.9509 | 1183880.4748 | 2579021.709 | 1183879.5369
14 | 2579050.8109 | 1183853.3159 | 2579050.8642 | 1183853.5739
15 | 2579050.81 | 1183853.3115 | 2579050.8109 | 1183853.3159
16 | 2579050.7055 | 1183852.8058 | 2579050.81 | 1183853.3115
17 | 2579050.7029 | 1183852.7934 | 2579050.7055 | 1183852.8058
18 | 2579050.6816 | 1183852.6902 | 2579050.7029 | 1183852.7934
19 | 2579021.709 | 1183879.5369 | 2579017.1182 | 1183861.7375
20 | 2579016.8067 | 1183860.5297 | 2579017.1182 | 1183861.7375
21 | 2579016.8067 | 1183860.5297 | 2579016.6109 | 1183859.7705
22 | 2579012.9597 | 1183845.6143 | 2579016.6109 | 1183859.7705
23 | 2579012.9597 | 1183845.6143 | 2579004.1293 | 1183847.4354
24 | 2579012.9597 | 1183845.6143 | 2579015.1831 | 1183845.1388
25 | 2578995.1352 | 1183849.2904 | 2579004.1293 | 1183847.4354
26 | 2579015.1831 | 1183845.1388 | 2579025.5629 | 1183842.9193
27 | 2579047.688 | 1183838.1883 | 2579048.5966 | 1183842.5986 | 2579050.6816 | 1183852.6902
28 | 2579047.688 | 1183838.1883 | 2579041.3892 | 1183839.5352
29 | 2579047.688 | 1183838.1883 | 2579053.1182 | 1183836.7589
30 | 2579025.5629 | 1183842.9193 | 2579041.3892 | 1183839.5352
31 | 2579053.1182 | 1183836.7589 | 2579059.2266 | 1183835.1509
32 | 2579064.2523 | 1183833.8279 | 2579059.2266 | 1183835.1509
33 | 2579064.2523 | 1183833.8279 | 2579068.6088 | 1183828.8879 | 2579068.6088 | 1183828.8879
34 | 2579064.2523 | 1183833.8279 | 2579066.2326 | 1183833.2321
35 | 2579077.5749 | 1183829.8197 | 2579078.1226 | 1183829.6549 | 2579081.8616 | 1183827.9613
36 | 2579071.7642 | 1183831.5679 | 2579077.5749 | 1183829.8197
37 | 2579071.7642 | 1183831.5679 | 2579066.2326 | 1183833.2321
38 | 2579068.6088 | 1183828.8879 | 2579074.6634 | 1183827.1101 | 2579078.0329 | 1183825.9122
39 | 2579078.0329 | 1183825.9122 | 2579082.211 | 1183824.4267 | 2579087.2504 | 1183822.6415 | 2579090.0928 | 1183821.4886

## bus_geodata
| x | y | coords
0 | 2579050.7954 | 1183906.5918
1 | 2579062.2605 | 1183899.2245
2 | 2579036.7401 | 1183915.8561
3 | 2579058.0121 | 1183884.9431
4 | 2579026.8634 | 1183922.5721
5 | 2579072.3449 | 1183883.0515
6 | 2579054.8814 | 1183873.003
7 | 2579013.1077 | 1183931.9775
8 | 2579026.8331 | 1183892.2342
9 | 2579024.5215 | 1183890.4414
10 | 2579039.2052 | 1183888.6414
11 | 2579077.8689 | 1183882.3225
12 | 2579054.7619 | 1183872.4247
13 | 2579021.9509 | 1183880.4748
14 | 2579050.8642 | 1183853.5739
15 | 2579050.8109 | 1183853.3159
16 | 2579050.81 | 1183853.3115
17 | 2579050.7055 | 1183852.8058
18 | 2579050.7029 | 1183852.7934
19 | 2579017.1182 | 1183861.7375
20 | 2579021.709 | 1183879.5369
21 | 2579016.8067 | 1183860.5297
22 | 2579016.6109 | 1183859.7705
23 | 2579012.9597 | 1183845.6143
24 | 2579004.1293 | 1183847.4354
25 | 2579015.1831 | 1183845.1388
26 | 2578995.1352 | 1183849.2904
27 | 2579050.6816 | 1183852.6902
28 | 2579047.688 | 1183838.1883
29 | 2579041.3892 | 1183839.5352
30 | 2579053.1182 | 1183836.7589
31 | 2579025.5629 | 1183842.9193
32 | 2579059.2266 | 1183835.1509
33 | 2579064.2523 | 1183833.8279
34 | 2579081.8616 | 1183827.9613
35 | 2579077.5749 | 1183829.8197
36 | 2579071.7642 | 1183831.5679
37 | 2579066.2326 | 1183833.2321
38 | 2579068.6088 | 1183828.8879
39 | 2579078.0329 | 1183825.9122
40 | 2579090.0928 | 1183821.4886
41 | 2579047.688 | 1183838.1883

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9942 | -0.11143 | 0.021962 | 0.0055041
1 | 0.99528 | -0.090544 | 0 | 0
2 | 0.9932 | -0.13077 | 0.051369 | 0.012874
3 | 0.99647 | -0.06776 | 0 | 0
4 | 0.99305 | -0.13365 | 0 | 0
5 | 0.99624 | -0.072166 | 0.0089145 | 0.0022342
6 | 0.99764 | -0.045134 | 0.015661 | 0.003925
7 | 0.99284 | -0.13768 | 0.013681 | 0.0034287
8 | 0.99387 | -0.11797 | 0 | 0
9 | 0.99393 | -0.11678 | 0 | 0
10 | 0.99368 | -0.12158 | 0.015854 | 0.0039734
11 | 0.9962 | -0.072993 | 0.008447 | 0.002117
12 | 0.99771 | -0.043893 | 0.010488 | 0.0026285
13 | 0.99408 | -0.1139 | 0.0083977 | 0.0021047
14 | 1 | 0 | -0.44972 | -0.11295
15 | 0.99997 | -0.00048336 | 0.006958 | 0.0017438
16 | 0.99997 | -0.00049157 | 0.006886 | 0.0017258
17 | 0.99993 | -0.0013977 | 0.0079948 | 0.0020037
18 | 0.99993 | -0.0014194 | 0.0047502 | 0.0011905
19 | 0.99463 | -0.10319 | 0.024967 | 0.0062572
20 | 0.9941 | -0.11349 | 0.0075191 | 0.0018845
21 | 0.9947 | -0.10195 | 0.0085719 | 0.0021483
22 | 0.99475 | -0.10104 | 0.011682 | 0.0029278
23 | 0.99577 | -0.081239 | 0 | 0
24 | 0.99549 | -0.086644 | 0.020277 | 0.005082
25 | 0.996 | -0.0768 | 0.016435 | 0.0041189
26 | 0.99538 | -0.088875 | 0.013814 | 0.0034621
27 | 0.99992 | -0.0015964 | 0.0059127 | 0.0014819
28 | 0.99864 | -0.02601 | 0 | 0
29 | 0.99831 | -0.032448 | 0.026101 | 0.0065415
30 | 0.99807 | -0.036994 | 0.0060341 | 0.0015123
31 | 0.99724 | -0.053048 | 0.017887 | 0.004483
32 | 0.99746 | -0.048698 | 0.010691 | 0.0026795
33 | 0.99701 | -0.057363 | 0 | 0
34 | 0.99664 | -0.064647 | 0.010784 | 0.0027028
35 | 0.99668 | -0.063762 | 0.0096421 | 0.0024165
36 | 0.99679 | -0.061588 | 0.0081344 | 0.0020387
37 | 0.99694 | -0.058694 | 0.0081438 | 0.002041
38 | 0.99666 | -0.064114 | 0.020659 | 0.0051776
39 | 0.99632 | -0.070669 | 0.012603 | 0.0031587
40 | 0.99603 | -0.076349 | 0.02517 | 0.0063083
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.087076 | -0.021848 | 0.087163 | 0.021903 | 8.6814e-05 | 5.5384e-05 | 0.13034 | 0.13034 | 0.13034 | 0.9942 | -0.11143 | 0.99528 | -0.090544 | 35.8063
1 | 0.065114 | 0.016344 | -0.065054 | -0.016306 | 5.9981e-05 | 3.8169e-05 | 0.097465 | 0.097465 | 0.097465 | 0.9942 | -0.11143 | 0.9932 | -0.13077 | 26.7761
2 | -0.087163 | -0.021903 | 0.087258 | 0.021964 | 9.4916e-05 | 6.0552e-05 | 0.13034 | 0.13033 | 0.13034 | 0.99528 | -0.090544 | 0.99647 | -0.06776 | 35.8063
3 | 0.013685 | 0.0034312 | -0.013683 | -0.0034301 | 1.8793e-06 | 1.0485e-06 | 0.020504 | 0.020504 | 0.020504 | 0.9932 | -0.13077 | 0.99305 | -0.13365 | 5.6329
4 | 0.017365 | 0.0043535 | -0.017362 | -0.0043513 | 3.6458e-06 | 2.145e-06 | 0.025932 | 0.025932 | 0.025932 | 0.99647 | -0.06776 | 0.99624 | -0.072166 | 7.1242
5 | -0.10462 | -0.026317 | 0.10474 | 0.02639 | 0.00011322 | 7.2298e-05 | 0.15627 | 0.15627 | 0.15627 | 0.99647 | -0.06776 | 0.99764 | -0.045134 | 42.9305
6 | 0.013683 | 0.0034301 | -0.013681 | -0.0034287 | 2.6271e-06 | 1.4658e-06 | 0.020504 | 0.020504 | 0.020504 | 0.99305 | -0.13365 | 0.99284 | -0.13768 | 5.6329
7 | 0.0084473 | 0.0021172 | -0.008447 | -0.002117 | 3.3263e-07 | 1.4034e-07 | 0.012617 | 0.012617 | 0.012617 | 0.99624 | -0.072166 | 0.9962 | -0.072993 | 3.4663
8 | -0.1204 | -0.030315 | 0.1204 | 0.030319 | 7.1451e-06 | 4.5652e-06 | 0.17963 | 0.17963 | 0.17963 | 0.99764 | -0.045134 | 0.99771 | -0.043893 | 49.3478
9 | -0.015857 | -0.003975 | 0.015858 | 0.0039755 | 9.0062e-07 | 5.2117e-07 | 0.023741 | 0.023741 | 0.023741 | 0.99387 | -0.11797 | 0.99393 | -0.11678 | 6.5223
10 | 0.015857 | 0.003975 | -0.015854 | -0.0039734 | 2.7235e-06 | 1.5761e-06 | 0.023741 | 0.023741 | 0.023741 | 0.99387 | -0.11797 | 0.99368 | -0.12158 | 6.5223
11 | -0.015858 | -0.0039755 | 0.01586 | 0.0039768 | 2.1755e-06 | 1.2589e-06 | 0.023741 | 0.023741 | 0.023741 | 0.99393 | -0.11678 | 0.99408 | -0.1139 | 6.5223
12 | -0.13089 | -0.032948 | 0.13117 | 0.033124 | 0.00027524 | 0.0001759 | 0.19527 | 0.19527 | 0.19527 | 0.99771 | -0.043893 | 1 | 0 | 53.645
13 | -0.024258 | -0.0060814 | 0.024258 | 0.0060817 | 4.7893e-07 | 2.9396e-07 | 0.036311 | 0.036311 | 0.036311 | 0.99408 | -0.1139 | 0.9941 | -0.11349 | 9.9756
14 | 0.3169 | 0.079823 | -0.3169 | -0.079818 | 7.3252e-06 | 4.6778e-06 | 0.4717 | 0.4717 | 0.4717 | 1 | 0 | 0.99997 | -0.00048336 | 43.1959
15 | 0.30994 | 0.078075 | -0.30994 | -0.078075 | 1.2162e-07 | 7.7606e-08 | 0.46135 | 0.46135 | 0.46135 | 0.99997 | -0.00048336 | 0.99997 | -0.00049157 | 42.2478
16 | 0.30305 | 0.076349 | -0.30304 | -0.07634 | 1.3133e-05 | 8.3847e-06 | 0.4511 | 0.4511 | 0.4511 | 0.99997 | -0.00049157 | 0.99993 | -0.0013977 | 41.3094
17 | 0.29505 | 0.074337 | -0.29504 | -0.074336 | 3.0655e-07 | 1.9567e-07 | 0.4392 | 0.4392 | 0.4392 | 0.99993 | -0.0013977 | 0.99993 | -0.0014194 | 40.2199
18 | 0.29029 | 0.073146 | -0.29029 | -0.073144 | 2.4584e-06 | 1.5692e-06 | 0.43213 | 0.43213 | 0.43213 | 0.99993 | -0.0014194 | 0.99992 | -0.0015964 | 39.5726
19 | 0.031793 | 0.0079759 | -0.031777 | -0.0079662 | 1.5596e-05 | 9.7431e-06 | 0.047566 | 0.047566 | 0.047566 | 0.99463 | -0.10319 | 0.9941 | -0.11349 | 13.0676
20 | -0.056759 | -0.014233 | 0.056763 | 0.014235 | 3.3728e-06 | 2.1424e-06 | 0.084917 | 0.084917 | 0.084917 | 0.99463 | -0.10319 | 0.9947 | -0.10195 | 23.3289
21 | -0.065335 | -0.016384 | 0.065337 | 0.016385 | 2.8091e-06 | 1.7876e-06 | 0.09774 | 0.09774 | 0.09774 | 0.9947 | -0.10195 | 0.99475 | -0.10104 | 26.8518
22 | -0.07702 | -0.019313 | 0.077092 | 0.01936 | 7.2776e-05 | 4.6386e-05 | 0.11522 | 0.11522 | 0.11522 | 0.99475 | -0.10104 | 0.99577 | -0.081239 | 31.6526
23 | 0.034102 | 0.0085504 | -0.034093 | -0.0085449 | 8.7807e-06 | 5.5024e-06 | 0.050961 | 0.050961 | 0.050961 | 0.99577 | -0.081239 | 0.99549 | -0.086644 | 14.0002
24 | -0.11119 | -0.02791 | 0.11122 | 0.027925 | 2.3545e-05 | 1.5039e-05 | 0.16618 | 0.16618 | 0.16618 | 0.99577 | -0.081239 | 0.996 | -0.0768 | 45.6528
25 | 0.013815 | 0.0034629 | -0.013814 | -0.0034621 | 1.4686e-06 | 8.2053e-07 | 0.020651 | 0.020651 | 0.020651 | 0.99549 | -0.086644 | 0.99538 | -0.088875 | 5.6733
26 | -0.12765 | -0.032044 | 0.1278 | 0.032137 | 0.0001448 | 9.2532e-05 | 0.19073 | 0.19073 | 0.19073 | 0.996 | -0.0768 | 0.99724 | -0.053048 | 52.3982
27 | 0.28438 | 0.071663 | -0.28405 | -0.071451 | 0.00033171 | 0.00021171 | 0.42333 | 0.42333 | 0.42333 | 0.99992 | -0.0015964 | 0.99864 | -0.02601 | 38.7669
28 | 0.17198 | 0.043286 | -0.17193 | -0.043252 | 5.29e-05 | 3.3603e-05 | 0.25632 | 0.25632 | 0.25632 | 0.99864 | -0.02601 | 0.99831 | -0.032448 | 23.4729
29 | 0.11207 | 0.028165 | -0.11201 | -0.028127 | 5.8733e-05 | 3.7516e-05 | 0.16701 | 0.16701 | 0.16701 | 0.99864 | -0.02601 | 0.99807 | -0.036994 | 45.882
30 | 0.14583 | 0.036711 | -0.14568 | -0.03662 | 0.00014345 | 9.1382e-05 | 0.21742 | 0.21742 | 0.21742 | 0.99831 | -0.032448 | 0.99724 | -0.053048 | 29.8654
31 | 0.10597 | 0.026615 | -0.10591 | -0.026577 | 5.9142e-05 | 3.7769e-05 | 0.15801 | 0.15801 | 0.15801 | 0.99807 | -0.036994 | 0.99746 | -0.048698 | 43.4105
32 | 0.095223 | 0.023898 | -0.095183 | -0.023873 | 3.9332e-05 | 2.5105e-05 | 0.14206 | 0.14206 | 0.14206 | 0.99746 | -0.048698 | 0.99701 | -0.057363 | 39.0288
33 | 0.05847 | 0.014668 | -0.058451 | -0.014656 | 1.8812e-05 | 1.1954e-05 | 0.08727 | 0.08727 | 0.08727 | 0.99701 | -0.057363 | 0.99666 | -0.064114 | 23.9752
34 | 0.036713 | 0.0092045 | -0.036711 | -0.009203 | 2.3285e-06 | 1.4633e-06 | 0.054795 | 0.054795 | 0.054795 | 0.99701 | -0.057363 | 0.99694 | -0.058694 | 15.0536
35 | -0.010784 | -0.0027028 | 0.010785 | 0.002703 | 4.5466e-07 | 2.3004e-07 | 0.016101 | 0.016101 | 0.016101 | 0.99664 | -0.064647 | 0.99668 | -0.063762 | 4.4235
36 | -0.020427 | -0.0051196 | 0.020429 | 0.0051208 | 2.1163e-06 | 1.2753e-06 | 0.030497 | 0.030497 | 0.030497 | 0.99668 | -0.063762 | 0.99679 | -0.061588 | 8.3782
37 | -0.028563 | -0.0071595 | 0.028567 | 0.007162 | 3.9385e-06 | 2.4453e-06 | 0.04264 | 0.04264 | 0.04264 | 0.99679 | -0.061588 | 0.99694 | -0.058694 | 11.7142
38 | 0.037792 | 0.0094786 | -0.037781 | -0.0094712 | 1.1804e-05 | 7.4257e-06 | 0.056426 | 0.056426 | 0.056426 | 0.99666 | -0.064114 | 0.99632 | -0.070669 | 15.5017
39 | 0.025177 | 0.0063125 | -0.02517 | -0.0063083 | 6.8126e-06 | 4.1928e-06 | 0.037603 | 0.037603 | 0.037603 | 0.99632 | -0.070669 | 0.99603 | -0.076349 | 10.3306

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45901 | 0.11527

## res_load
| p_mw | q_mvar
0 | 0.021962 | 0.0055041
1 | 0.051369 | 0.012874
2 | 0.0089145 | 0.0022342
3 | 0.015661 | 0.003925
4 | 0.013681 | 0.0034287
5 | 0.015854 | 0.0039734
6 | 0.008447 | 0.002117
7 | 0.010488 | 0.0026285
8 | 0.0083977 | 0.0021047
9 | 0.0092851 | 0.0023271
10 | 0.006958 | 0.0017438
11 | 0.006886 | 0.0017258
12 | 0.0079948 | 0.0020037
13 | 0.0047502 | 0.0011905
14 | 0.024967 | 0.0062572
15 | 0.0075191 | 0.0018845
16 | 0.0085719 | 0.0021483
17 | 0.011682 | 0.0029278
18 | 0.020277 | 0.005082
19 | 0.016435 | 0.0041189
20 | 0.013814 | 0.0034621
21 | 0.0059127 | 0.0014819
22 | 0.026101 | 0.0065415
23 | 0.0060341 | 0.0015123
24 | 0.017887 | 0.004483
25 | 0.010691 | 0.0026795
26 | 0.010784 | 0.0027028
27 | 0.0096421 | 0.0024165
28 | 0.0081344 | 0.0020387
29 | 0.0081438 | 0.002041
30 | 0.020659 | 0.0051776
31 | 0.012603 | 0.0031587
32 | 0.02517 | 0.0063083

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1