## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2196-91_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2196-91_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2196-91_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2196-91_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2196-91_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2196-91_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2196-91_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2196-91_0_4_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2196-91_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_2196-91_0_4_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_2196-91_0_4_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_2196-91_0_4_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_2196-91_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2196-91_0_4_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_2196-91_0_4_node_45 | 0.4 | n |  | TRUE
15 | bus_LV_2196-91_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2196-91_0_4_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_2196-91_0_4_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_2196-91_0_4_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_2196-91_0_4_node_44 | 0.4 | n |  | TRUE
20 | bus_LV_2196-91_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2196-91_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2196-91_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2196-91_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2196-91_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2196-91_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2196-91_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2196-91_0_4_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_2196-91_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2196-91_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_2196-91_0_4_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_2196-91_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2196-91_0_4_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2196-91_0_4_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_2196-91_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_2196-91_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_2196-91_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_2196-91_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_2196-91_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_2196-91_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_2196-91_0_4_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_2196-91_0_4_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_2196-91_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_MV_507_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2196-91_0_4_load_0 | 0 | 0.018333 | 0.0045947 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2196-91_0_4_load_1 | 1 | 0.062124 | 0.01557 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2196-91_0_4_load_3 | 3 | 0.014003 | 0.0035095 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2196-91_0_4_load_12 | 7 | 0.016846 | 0.004222 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2196-91_0_4_load_19 | 8 | 0.0076403 | 0.0019148 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2196-91_0_4_load_42 | 10 | 0.0098214 | 0.0024615 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2196-91_0_4_load_37 | 11 | 0.049577 | 0.012425 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2196-91_0_4_load_46 | 13 | 0.019225 | 0.0048181 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2196-91_0_4_load_45 | 14 | 0.020226 | 0.0050692 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2196-91_0_4_load_13 | 15 | 0.024289 | 0.0060874 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2196-91_0_4_load_38 | 16 | 0.016706 | 0.0041868 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2196-91_0_4_load_40 | 17 | 0.0079806 | 0.0020001 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2196-91_0_4_load_47 | 18 | 0.013343 | 0.003344 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2196-91_0_4_load_44 | 19 | 0.012425 | 0.003114 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2196-91_0_4_load_14 | 20 | 0.013801 | 0.0034589 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2196-91_0_4_load_15 | 23 | 0.021038 | 0.0052726 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2196-91_0_4_load_20 | 25 | 0.026588 | 0.0066637 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2196-91_0_4_load_21 | 26 | 0.013814 | 0.003462 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2196-91_0_4_load_28 | 27 | 0.0061767 | 0.001548 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2196-91_0_4_load_29 | 29 | 0.006362 | 0.0015945 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2196-91_0_4_load_48 | 33 | 0.0031965 | 0.00080112 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2196-91_0_4_load_33 | 34 | 0.031183 | 0.0078153 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2196-91_0_4_load_26 | 35 | 0.013458 | 0.0033729 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2196-91_0_4_load_27 | 36 | 0.030488 | 0.007641 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2196-91_0_4_load_34 | 37 | 0.0051714 | 0.0012961 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2196-91_0_4_load_31 | 38 | 0.004837 | 0.0012123 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2196-91_0_4_load_30 | 39 | 0.01059 | 0.002654 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2196-91_0_4_load_36 | 40 | 0.014291 | 0.0035817 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2196-91_0_4_load_41 | 41 | 0.014058 | 0.0035232 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2196-91_0_4_load_43 | 42 | 0.012247 | 0.0030694 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2196-91_0_4_line_0 |  | 0 | 1 | 0.039251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2196-91_0_4_line_1 |  | 0 | 2 | 0.0095151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2196-91_0_4_line_2 |  | 1 | 3 | 0.018089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2196-91_0_4_line_3 |  | 2 | 4 | 0.003537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2196-91_0_4_line_4 |  | 2 | 5 | 0.074225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2196-91_0_4_line_5 |  | 2 | 6 | 0.078799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2196-91_0_4_line_6 |  | 3 | 7 | 0.0219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2196-91_0_4_line_7 |  | 4 | 8 | 0.014057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2196-91_0_4_line_8 |  | 5 | 9 | 0.011282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2196-91_0_4_line_9 |  | 5 | 10 | 0.01723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2196-91_0_4_line_10 |  | 6 | 11 | 0.018201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2196-91_0_4_line_11 |  | 7 | 15 | 0.014345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2196-91_0_4_line_12 |  | 9 | 16 | 0.0036611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2196-91_0_4_line_13 |  | 10 | 17 | 0.00063613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2196-91_0_4_line_14 |  | 12 | 13 | 0.0063659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2196-91_0_4_line_15 |  | 12 | 14 | 0.0090904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2196-91_0_4_line_16 |  | 13 | 18 | 0.0072015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2196-91_0_4_line_17 |  | 14 | 19 | 0.0057349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2196-91_0_4_line_18 |  | 15 | 20 | 0.034396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2196-91_0_4_line_19 |  | 17 | 41 | 0.0055548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2196-91_0_4_line_20 |  | 19 | 42 | 0.0011941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2196-91_0_4_line_21 |  | 20 | 21 | 0.01482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2196-91_0_4_line_22 |  | 21 | 22 | 0.012808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2196-91_0_4_line_23 |  | 22 | 23 | 0.018756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2196-91_0_4_line_24 |  | 23 | 24 | 0.0093081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2196-91_0_4_line_25 |  | 24 | 25 | 0.012945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2196-91_0_4_line_26 |  | 24 | 26 | 0.012774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2196-91_0_4_line_27 |  | 26 | 27 | 0.012032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2196-91_0_4_line_28 |  | 27 | 35 | 0.031446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2196-91_0_4_line_29 |  | 28 | 29 | 0.0072726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2196-91_0_4_line_30 |  | 28 | 30 | 0.002736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2196-91_0_4_line_31 |  | 29 | 36 | 0.029152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2196-91_0_4_line_32 |  | 30 | 37 | 0.034839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2196-91_0_4_line_33 |  | 30 | 32 | 0.03005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2196-91_0_4_line_34 |  | 31 | 32 | 0.030778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2196-91_0_4_line_35 |  | 31 | 33 | 0.034916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2196-91_0_4_line_36 |  | 32 | 34 | 0.028391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2196-91_0_4_line_37 |  | 34 | 38 | 0.041305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2196-91_0_4_line_38 |  | 35 | 36 | 0.0084349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2196-91_0_4_line_39 |  | 37 | 40 | 0.0029099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2196-91_0_4_line_40 |  | 38 | 39 | 0.020718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2196-91_0_4_line_41 |  | 41 | 42 | 0.0065509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2196-91_0_4_trafo_21 | 0.63 MVA 20/0.4 kV | 43 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2578772.9647 | 1183848.6532 | 2578765.8731 | 1183833.6599 | 2578755.5832 | 1183818.5998 | 2578751.7671 | 1183816.3585
1 | 2578777.033 | 1183857.2547 | 2578772.9647 | 1183848.6532
2 | 2578751.7671 | 1183816.3585 | 2578736.1692 | 1183807.1972
3 | 2578780.0799 | 1183855.4429 | 2578777.033 | 1183857.2547
4 | 2578777.033 | 1183857.2547 | 2578783.5887 | 1183867.6257 | 2578792.6804 | 1183874.1968 | 2578803.1886 | 1183879.8624 | 2578806.9962 | 1183881.5942 | 2578808.931 | 1183882.6212 | 2578809.6652 | 1183883.0077 | 2578812.3342 | 1183884.4212 | 2578813.1514 | 1183882.395 | 2578815.4012 | 1183877.5289 | 2578817.6698 | 1183873.6744 | 2578821.1555 | 1183868.5928 | 2578828.9628 | 1183861.7282
5 | 2578723.3992 | 1183892.9865 | 2578741.0306 | 1183866.899 | 2578760.0498 | 1183876.7809 | 2578761.6387 | 1183874.9743 | 2578769.8257 | 1183865.4068 | 2578777.033 | 1183857.2547
6 | 2578736.1692 | 1183807.1972 | 2578734.0044 | 1183805.9256 | 2578716.7824 | 1183797.0183
7 | 2578780.0799 | 1183855.4429 | 2578779.7953 | 1183854.8548 | 2578779.1187 | 1183853.4787 | 2578773.9584 | 1183842.7891
8 | 2578822.2362 | 1183852.6584 | 2578828.9628 | 1183861.7282
9 | 2578828.9628 | 1183861.7282 | 2578845.7259 | 1183857.5443
10 | 2578723.3992 | 1183892.9865 | 2578716.1984 | 1183887.954 | 2578708.1582 | 1183883.0532
11 | 2578704.983 | 1183788.9981 | 2578711.2914 | 1183794.1783 | 2578716.7824 | 1183797.0183
12 | 2578822.2362 | 1183852.6584 | 2578822.7424 | 1183849.0325
13 | 2578846.3612 | 1183857.5766 | 2578845.7259 | 1183857.5443
14 | 2578873.2974 | 1183864.0278 | 2578879.6439 | 1183864.5241
15 | 2578873.2974 | 1183864.0278 | 2578864.9255 | 1183860.4856
16 | 2578879.6439 | 1183864.5241 | 2578886.8235 | 1183865.0855
17 | 2578859.6439 | 1183858.2509 | 2578864.9255 | 1183860.4856
18 | 2578704.983 | 1183788.9981 | 2578714.65 | 1183774.9229 | 2578717.9852 | 1183772.5987 | 2578720.59 | 1183773.1119 | 2578725.0444 | 1183776.42 | 2578728.2254 | 1183780.3454
19 | 2578846.3612 | 1183857.5766 | 2578851.9089 | 1183857.8582
20 | 2578858.4514 | 1183858.1904 | 2578859.6439 | 1183858.2509 | 2578859.6439 | 1183858.2509
21 | 2578740.1414 | 1183788.7393 | 2578736.8261 | 1183785.9385 | 2578730.2274 | 1183782.816 | 2578728.2254 | 1183780.3454
22 | 2578740.1414 | 1183788.7393 | 2578748.8921 | 1183798.113
23 | 2578748.8921 | 1183798.113 | 2578765.5673 | 1183789.5266
24 | 2578772.6728 | 1183783.8987 | 2578770.3712 | 1183787.053 | 2578765.5673 | 1183789.5266
25 | 2578772.6728 | 1183783.8987 | 2578760.2679 | 1183787.599
26 | 2578772.6728 | 1183783.8987 | 2578779.9009 | 1183781.5384 | 2578784.7987 | 1183779.8822
27 | 2578796.1971 | 1183776.0278 | 2578784.7987 | 1183779.8822
28 | 2578796.1971 | 1183776.0278 | 2578809.4371 | 1183771.5505 | 2578823.4072 | 1183761.0621 | 2578823.4072 | 1183761.0621
29 | 2578850.7384 | 1183725.4911 | 2578846.3723 | 1183731.3073
30 | 2578850.7384 | 1183725.4911 | 2578852.1422 | 1183723.1405
31 | 2578846.3723 | 1183731.3073 | 2578843.969 | 1183734.5087 | 2578828.5714 | 1183754.393
32 | 2578852.1422 | 1183723.1405 | 2578873.3233 | 1183735.5608 | 2578872.2528 | 1183745.7895
33 | 2578867.6002 | 1183697.3501 | 2578852.1422 | 1183723.1405
34 | 2578885.1261 | 1183675.6101 | 2578877.7318 | 1183676.3366 | 2578869.6491 | 1183693.9299 | 2578867.6002 | 1183697.3501
35 | 2578885.1261 | 1183675.6101 | 2578915.1596 | 1183693.4172
36 | 2578867.6002 | 1183697.3501 | 2578892.6128 | 1183710.7825
37 | 2578905.9201 | 1183739.0201 | 2578904.5619 | 1183738.4629 | 2578902.9489 | 1183735.6449 | 2578903.722 | 1183731.9292 | 2578909.7178 | 1183719.9684 | 2578892.6128 | 1183710.7825
38 | 2578823.4072 | 1183761.0621 | 2578828.5714 | 1183754.393
39 | 2578871.9499 | 1183748.6836 | 2578872.2528 | 1183745.7895
40 | 2578905.9201 | 1183739.0201 | 2578925.0875 | 1183746.8837
41 | 2578851.9089 | 1183857.8582 | 2578858.4514 | 1183858.1904

## bus_geodata
| x | y | coords
0 | 2578772.9647 | 1183848.6532
1 | 2578751.7671 | 1183816.3585
2 | 2578777.033 | 1183857.2547
3 | 2578736.1692 | 1183807.1972
4 | 2578780.0799 | 1183855.4429
5 | 2578828.9628 | 1183861.7282
6 | 2578723.3992 | 1183892.9865
7 | 2578716.7824 | 1183797.0183
8 | 2578773.9584 | 1183842.7891
9 | 2578822.2362 | 1183852.6584
10 | 2578845.7259 | 1183857.5443
11 | 2578708.1582 | 1183883.0532
12 | 2578873.2974 | 1183864.0278
13 | 2578879.6439 | 1183864.5241
14 | 2578864.9255 | 1183860.4856
15 | 2578704.983 | 1183788.9981
16 | 2578822.7424 | 1183849.0325
17 | 2578846.3612 | 1183857.5766
18 | 2578886.8235 | 1183865.0855
19 | 2578859.6439 | 1183858.2509
20 | 2578728.2254 | 1183780.3454
21 | 2578740.1414 | 1183788.7393
22 | 2578748.8921 | 1183798.113
23 | 2578765.5673 | 1183789.5266
24 | 2578772.6728 | 1183783.8987
25 | 2578760.2679 | 1183787.599
26 | 2578784.7987 | 1183779.8822
27 | 2578796.1971 | 1183776.0278
28 | 2578850.7384 | 1183725.4911
29 | 2578846.3723 | 1183731.3073
30 | 2578852.1422 | 1183723.1405
31 | 2578885.1261 | 1183675.6101
32 | 2578867.6002 | 1183697.3501
33 | 2578915.1596 | 1183693.4172
34 | 2578892.6128 | 1183710.7825
35 | 2578823.4072 | 1183761.0621
36 | 2578828.5714 | 1183754.393
37 | 2578872.2528 | 1183745.7895
38 | 2578905.9201 | 1183739.0201
39 | 2578925.0875 | 1183746.8837
40 | 2578871.9499 | 1183748.6836
41 | 2578851.9089 | 1183857.8582
42 | 2578858.4514 | 1183858.1904
43 | 2578772.6728 | 1183783.8987

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98222 | -0.34034 | 0.018333 | 0.0045947
1 | 0.98468 | -0.29281 | 0.062124 | 0.01557
2 | 0.98141 | -0.3561 | 0 | 0
3 | 0.98615 | -0.26427 | 0.014003 | 0.0035095
4 | 0.98139 | -0.35659 | 0 | 0
5 | 0.97706 | -0.44112 | 0 | 0
6 | 0.97779 | -0.42706 | 0 | 0
7 | 0.98803 | -0.228 | 0.016846 | 0.004222
8 | 0.98129 | -0.35854 | 0.0076403 | 0.0019148
9 | 0.97689 | -0.44457 | 0 | 0
10 | 0.97531 | -0.47558 | 0.0098214 | 0.0024615
11 | 0.97695 | -0.44353 | 0.049577 | 0.012425
12 | 0.97367 | -0.50781 | 0 | 0
13 | 0.97348 | -0.51162 | 0.019225 | 0.0048181
14 | 0.97395 | -0.50236 | 0.020226 | 0.0050692
15 | 0.98934 | -0.20288 | 0.024289 | 0.0060874
16 | 0.97683 | -0.44568 | 0.016706 | 0.0041868
17 | 0.97525 | -0.47674 | 0.0079806 | 0.0020001
18 | 0.97339 | -0.51339 | 0.013343 | 0.003344
19 | 0.97423 | -0.4968 | 0.012425 | 0.003114
20 | 0.99272 | -0.138 | 0.013801 | 0.0034589
21 | 0.99425 | -0.10898 | 0 | 0
22 | 0.99556 | -0.083975 | 0 | 0
23 | 0.99749 | -0.047471 | 0.021038 | 0.0052726
24 | 0.9985 | -0.028266 | 0 | 0
25 | 0.99819 | -0.034285 | 0.026588 | 0.0066637
26 | 1 | 0 | -0.51481 | -0.13137
27 | 0.99862 | -0.026412 | 0.0061767 | 0.001548
28 | 0.99188 | -0.156 | 0 | 0
29 | 0.99234 | -0.14708 | 0.006362 | 0.0015945
30 | 0.9917 | -0.15936 | 0 | 0
31 | 0.99024 | -0.18767 | 0 | 0
32 | 0.99033 | -0.18592 | 0 | 0
33 | 0.99014 | -0.18966 | 0.0031965 | 0.00080112
34 | 0.98912 | -0.20947 | 0.031183 | 0.0078153
35 | 0.99518 | -0.092363 | 0.013458 | 0.0033729
36 | 0.99436 | -0.10813 | 0.030488 | 0.007641
37 | 0.99108 | -0.17138 | 0.0051714 | 0.0012961
38 | 0.98853 | -0.22083 | 0.004837 | 0.0012123
39 | 0.98833 | -0.22475 | 0.01059 | 0.002654
40 | 0.99104 | -0.17212 | 0.014291 | 0.0035817
41 | 0.97478 | -0.48606 | 0.014058 | 0.0035232
42 | 0.9743 | -0.49537 | 0.012247 | 0.0030694
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.20274 | -0.05126 | 0.20321 | 0.051555 | 0.00046334 | 0.00029504 | 0.3073 | 0.3073 | 0.3073 | 0.98222 | -0.34034 | 0.98468 | -0.29281 | 28.1414
1 | 0.18441 | 0.046665 | -0.18427 | -0.046576 | 0.0001394 | 8.8978e-05 | 0.27953 | 0.27953 | 0.27953 | 0.98222 | -0.34034 | 0.98141 | -0.3561 | 38.3971
2 | -0.26533 | -0.067125 | 0.26569 | 0.067357 | 0.00036393 | 0.00023222 | 0.40118 | 0.40118 | 0.40118 | 0.98468 | -0.29281 | 0.98615 | -0.26427 | 36.7385
3 | 0.0076412 | 0.0019152 | -0.007641 | -0.0019151 | 1.7803e-07 | 6.9249e-08 | 0.011586 | 0.011586 | 0.011586 | 0.98141 | -0.3561 | 0.98139 | -0.35659 | 3.1829
4 | 0.12685 | 0.032104 | -0.12633 | -0.031776 | 0.00051537 | 0.00032797 | 0.19243 | 0.19244 | 0.19244 | 0.98141 | -0.3561 | 0.97706 | -0.44112 | 26.4334
5 | 0.049784 | 0.012557 | -0.049615 | -0.01245 | 0.00016849 | 0.00010684 | 0.075511 | 0.075511 | 0.075511 | 0.98141 | -0.3561 | 0.97779 | -0.42706 | 20.7448
6 | -0.2797 | -0.070867 | 0.28019 | 0.071178 | 0.00048822 | 0.00031162 | 0.42231 | 0.42231 | 0.42231 | 0.98615 | -0.26427 | 0.98803 | -0.228 | 38.6734
7 | 0.007641 | 0.0019151 | -0.0076403 | -0.0019148 | 7.0755e-07 | 2.7524e-07 | 0.011586 | 0.011586 | 0.011586 | 0.98139 | -0.35659 | 0.98129 | -0.35854 | 3.1829
8 | 0.016709 | 0.004189 | -0.016707 | -0.0041874 | 2.7398e-06 | 1.6122e-06 | 0.025448 | 0.025448 | 0.025448 | 0.97706 | -0.44112 | 0.97689 | -0.44457 | 6.9912
9 | 0.10962 | 0.027587 | -0.10944 | -0.027472 | 0.00018017 | 0.00011509 | 0.16699 | 0.16699 | 0.16699 | 0.97706 | -0.44112 | 0.97531 | -0.47558 | 45.8757
10 | 0.049615 | 0.01245 | -0.049577 | -0.012425 | 3.8918e-05 | 2.468e-05 | 0.075511 | 0.075511 | 0.075511 | 0.97779 | -0.42706 | 0.97695 | -0.44353 | 20.7448
11 | -0.29703 | -0.0754 | 0.29739 | 0.07563 | 0.00035937 | 0.00022945 | 0.44768 | 0.44768 | 0.44768 | 0.98803 | -0.228 | 0.98934 | -0.20288 | 40.9967
12 | 0.016707 | 0.0041874 | -0.016706 | -0.0041868 | 8.8909e-07 | 5.2318e-07 | 0.025448 | 0.025448 | 0.025448 | 0.97689 | -0.44457 | 0.97683 | -0.44568 | 6.9912
13 | 0.099619 | 0.025011 | -0.099613 | -0.025007 | 5.5116e-06 | 3.5195e-06 | 0.152 | 0.152 | 0.152 | 0.97531 | -0.47558 | 0.97525 | -0.47674 | 41.7591
14 | 0.032574 | 0.0081664 | -0.032568 | -0.0081627 | 5.9162e-06 | 3.7072e-06 | 0.049782 | 0.049783 | 0.049783 | 0.97367 | -0.50781 | 0.97348 | -0.51162 | 13.6765
15 | -0.032574 | -0.0081664 | 0.032583 | 0.0081717 | 8.4483e-06 | 5.2938e-06 | 0.049782 | 0.049782 | 0.049782 | 0.97367 | -0.50781 | 0.97395 | -0.50236 | 13.6765
16 | 0.013344 | 0.0033446 | -0.013343 | -0.003344 | 1.1235e-06 | 6.2952e-07 | 0.020397 | 0.020397 | 0.020397 | 0.97348 | -0.51162 | 0.97339 | -0.51339 | 5.6035
17 | -0.052809 | -0.013241 | 0.052823 | 0.01325 | 1.4e-05 | 8.8889e-06 | 0.080685 | 0.080685 | 0.080685 | 0.97395 | -0.50236 | 0.97423 | -0.4968 | 22.1662
18 | -0.32168 | -0.081717 | 0.32269 | 0.082361 | 0.0010081 | 0.00064384 | 0.48422 | 0.48422 | 0.48422 | 0.98934 | -0.20288 | 0.99272 | -0.138 | 44.3421
19 | 0.091633 | 0.023007 | -0.091592 | -0.022981 | 4.0727e-05 | 2.5996e-05 | 0.13983 | 0.13983 | 0.13983 | 0.97525 | -0.47674 | 0.97478 | -0.48606 | 38.4139
20 | -0.065248 | -0.016364 | 0.065253 | 0.016367 | 4.4475e-06 | 2.8316e-06 | 0.099663 | 0.099663 | 0.099663 | 0.97423 | -0.4968 | 0.9743 | -0.49537 | 27.3799
21 | -0.33649 | -0.08582 | 0.33696 | 0.086121 | 0.00047225 | 0.00030167 | 0.5049 | 0.5049 | 0.5049 | 0.99272 | -0.138 | 0.99425 | -0.10898 | 46.2365
22 | -0.33696 | -0.086121 | 0.33737 | 0.086382 | 0.00040814 | 0.00026071 | 0.5049 | 0.5049 | 0.5049 | 0.99425 | -0.10898 | 0.99556 | -0.083975 | 46.2364
23 | -0.33737 | -0.086382 | 0.33797 | 0.086764 | 0.00059767 | 0.00038178 | 0.5049 | 0.5049 | 0.5049 | 0.99556 | -0.083975 | 0.99749 | -0.047471 | 46.2364
24 | -0.35901 | -0.092037 | 0.35934 | 0.09225 | 0.00033463 | 0.0002138 | 0.53628 | 0.53628 | 0.53628 | 0.99749 | -0.047471 | 0.9985 | -0.028266 | 49.1103
25 | 0.026596 | 0.0066684 | -0.026588 | -0.0066637 | 7.6262e-06 | 4.7115e-06 | 0.039636 | 0.039636 | 0.039636 | 0.9985 | -0.028266 | 0.99819 | -0.034285 | 10.8889
26 | -0.38594 | -0.098919 | 0.38647 | 0.099257 | 0.00052961 | 0.00033845 | 0.57592 | 0.57592 | 0.57592 | 0.9985 | -0.028266 | 1 | 0 | 52.7399
27 | 0.12669 | 0.032115 | -0.12653 | -0.032012 | 0.00016059 | 0.00010262 | 0.18865 | 0.18865 | 0.18865 | 1 | 0 | 0.99862 | -0.026412 | 51.8274
28 | 0.12036 | 0.030464 | -0.11998 | -0.030222 | 0.00037972 | 0.00024261 | 0.17945 | 0.17945 | 0.17945 | 0.99862 | -0.026412 | 0.99518 | -0.092363 | 49.2989
29 | -0.069419 | -0.017453 | 0.069448 | 0.017472 | 2.9589e-05 | 1.8843e-05 | 0.10416 | 0.10416 | 0.10416 | 0.99188 | -0.156 | 0.99234 | -0.14708 | 28.6159
30 | 0.069419 | 0.017453 | -0.069407 | -0.017446 | 1.1132e-05 | 7.089e-06 | 0.10416 | 0.10416 | 0.10416 | 0.99188 | -0.156 | 0.9917 | -0.15936 | 28.6159
31 | -0.07581 | -0.019066 | 0.075952 | 0.019157 | 0.00014133 | 9.0074e-05 | 0.1137 | 0.1137 | 0.1137 | 0.99234 | -0.14708 | 0.99436 | -0.10813 | 31.2367
32 | 0.019474 | 0.0048848 | -0.019463 | -0.0048781 | 1.1156e-05 | 6.6908e-06 | 0.029222 | 0.029222 | 0.029222 | 0.9917 | -0.15936 | 0.99108 | -0.17138 | 8.0281
33 | 0.049933 | 0.012561 | -0.04987 | -0.012521 | 6.3285e-05 | 4.0115e-05 | 0.07494 | 0.07494 | 0.07494 | 0.9917 | -0.15936 | 0.99033 | -0.18592 | 20.5879
34 | -0.0031968 | -0.00080086 | 0.0031971 | 0.00080064 | 2.6632e-07 | -2.2553e-07 | 0.0048037 | 0.0048035 | 0.0048037 | 0.99024 | -0.18767 | 0.99033 | -0.18592 | 1.3197
35 | 0.0031968 | 0.00080086 | -0.0031965 | -0.00080112 | 3.0214e-07 | -2.5575e-07 | 0.0048037 | 0.0048038 | 0.0048038 | 0.99024 | -0.18767 | 0.99014 | -0.18966 | 1.3197
36 | 0.046673 | 0.011721 | -0.04662 | -0.011687 | 5.2372e-05 | 3.3153e-05 | 0.070136 | 0.070136 | 0.070136 | 0.99033 | -0.18592 | 0.98912 | -0.20947 | 19.2682
37 | 0.015437 | 0.0038721 | -0.015429 | -0.0038673 | 8.3546e-06 | 4.8171e-06 | 0.023224 | 0.023224 | 0.023224 | 0.98912 | -0.20947 | 0.98853 | -0.22083 | 6.3804
38 | 0.10652 | 0.026849 | -0.10644 | -0.026798 | 8.0293e-05 | 5.1278e-05 | 0.15933 | 0.15933 | 0.15933 | 0.99518 | -0.092363 | 0.99436 | -0.10813 | 43.7707
39 | 0.014292 | 0.003582 | -0.014291 | -0.0035817 | 5.0244e-07 | 2.8406e-07 | 0.021458 | 0.021458 | 0.021458 | 0.99108 | -0.17138 | 0.99104 | -0.17212 | 5.895
40 | 0.010592 | 0.002655 | -0.01059 | -0.002654 | 1.9749e-06 | 9.9836e-07 | 0.015943 | 0.015943 | 0.015943 | 0.98853 | -0.22083 | 0.98833 | -0.22475 | 4.3801
41 | 0.077534 | 0.019458 | -0.0775 | -0.019436 | 3.4419e-05 | 2.1946e-05 | 0.11837 | 0.11837 | 0.11837 | 0.97478 | -0.48606 | 0.9743 | -0.49537 | 32.5184

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52862 | 0.13483

## res_load
| p_mw | q_mvar
0 | 0.018333 | 0.0045947
1 | 0.062124 | 0.01557
2 | 0.014003 | 0.0035095
3 | 0.016846 | 0.004222
4 | 0.0076403 | 0.0019148
5 | 0.0098214 | 0.0024615
6 | 0.049577 | 0.012425
7 | 0.019225 | 0.0048181
8 | 0.020226 | 0.0050692
9 | 0.024289 | 0.0060874
10 | 0.016706 | 0.0041868
11 | 0.0079806 | 0.0020001
12 | 0.013343 | 0.003344
13 | 0.012425 | 0.003114
14 | 0.013801 | 0.0034589
15 | 0.021038 | 0.0052726
16 | 0.026588 | 0.0066637
17 | 0.013814 | 0.003462
18 | 0.0061767 | 0.001548
19 | 0.006362 | 0.0015945
20 | 0.0031965 | 0.00080112
21 | 0.031183 | 0.0078153
22 | 0.013458 | 0.0033729
23 | 0.030488 | 0.007641
24 | 0.0051714 | 0.0012961
25 | 0.004837 | 0.0012123
26 | 0.01059 | 0.002654
27 | 0.014291 | 0.0035817
28 | 0.014058 | 0.0035232
29 | 0.012247 | 0.0030694

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1