## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2197-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2197-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2197-1_0_4_node_13 | 0.4 | n |  | TRUE
3 | bus_LV_2197-1_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2197-1_0_4_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_2197-1_0_4_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_2197-1_0_4_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_2197-1_0_4_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_2197-1_0_4_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_2197-1_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_2197-1_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2197-1_0_4_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_2197-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2197-1_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2197-1_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2197-1_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2197-1_0_4_node_3 | 0.4 | n |  | TRUE
17 | bus_LV_2197-1_0_4_node_5 | 0.4 | n |  | TRUE
18 | bus_LV_2197-1_0_4_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_2197-1_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2197-1_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2197-1_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2197-1_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_2197-1_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_2197-1_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_MV_506_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2197-1_0_4_load_0 | 0 | 0.094862 | 0.023775 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2197-1_0_4_load_12 | 4 | 0.043385 | 0.010873 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2197-1_0_4_load_21 | 7 | 0.09244 | 0.023168 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2197-1_0_4_load_20 | 8 | 0.0034692 | 0.00086947 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2197-1_0_4_load_26 | 9 | 0.041629 | 0.010433 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2197-1_0_4_load_8 | 12 | 0.059661 | 0.014952 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2197-1_0_4_load_9 | 14 | 0.0053055 | 0.0013297 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2197-1_0_4_load_15 | 15 | 0.028695 | 0.0071917 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2197-1_0_4_load_3 | 16 | 0.033826 | 0.0084775 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2197-1_0_4_load_7 | 18 | 0.09271 | 0.023235 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2197-1_0_4_load_19 | 21 | 0.0084635 | 0.0021211 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2197-1_0_4_load_23 | 22 | 0.026668 | 0.0066837 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2197-1_0_4_load_24 | 23 | 0.0043889 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2197-1_0_4_load_22 | 24 | 0.001244 | 0.00031178 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2197-1_0_4_line_0 |  | 0 | 1 | 0.0080239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_2197-1_0_4_line_1 |  | 0 | 2 | 0.10772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2197-1_0_4_line_2 |  | 1 | 3 | 0.13699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2197-1_0_4_line_3 |  | 2 | 6 | 0.13058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2197-1_0_4_line_4 |  | 2 | 4 | 0.037804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2197-1_0_4_line_5 |  | 3 | 10 | 0.057863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2197-1_0_4_line_6 |  | 3 | 11 | 0.02976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2197-1_0_4_line_7 |  | 3 | 12 | 0.069465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2197-1_0_4_line_8 |  | 4 | 5 | 0.17514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2197-1_0_4_line_9 |  | 5 | 9 | 0.066677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2197-1_0_4_line_10 |  | 6 | 7 | 0.014884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2197-1_0_4_line_11 |  | 6 | 8 | 0.045103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2197-1_0_4_line_12 |  | 10 | 13 | 0.039825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2197-1_0_4_line_13 |  | 10 | 14 | 0.018308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2197-1_0_4_line_14 |  | 11 | 16 | 0.031354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2197-1_0_4_line_15 |  | 13 | 15 | 0.037306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2197-1_0_4_line_16 |  | 15 | 19 | 0.11977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2197-1_0_4_line_17 |  | 16 | 17 | 0.017541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2197-1_0_4_line_18 |  | 17 | 18 | 0.049194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2197-1_0_4_line_19 |  | 19 | 20 | 0.028469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2197-1_0_4_line_20 |  | 19 | 21 | 0.056052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2197-1_0_4_line_21 |  | 20 | 22 | 0.024246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2197-1_0_4_line_22 |  | 22 | 23 | 0.051791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2197-1_0_4_line_23 |  | 23 | 24 | 0.05858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2197-1_0_4_trafo_1 | 0.63 MVA 20/0.4 kV | 25 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2575403.4654 | 1184634.921 | 2575401.2491 | 1184642.6327
1 | 2575401.2491 | 1184642.6327 | 2575347.6943 | 1184736.093
2 | 2575403.4654 | 1184634.921 | 2575408.509 | 1184616.057 | 2575424.6909 | 1184564.4967 | 2575457.1061 | 1184573.8572 | 2575465.9424 | 1184545.5171
3 | 2575249.9954 | 1184756.5524 | 2575258.3504 | 1184752.3266 | 2575269.0454 | 1184714.2179 | 2575317.6652 | 1184727.7349 | 2575332.1754 | 1184731.777 | 2575347.6943 | 1184736.093
4 | 2575347.6943 | 1184736.093 | 2575349.1995 | 1184736.5092 | 2575339.3347 | 1184771.383
5 | 2575465.9424 | 1184545.5171 | 2575474.8119 | 1184536.387 | 2575483.3192 | 1184505.9695 | 2575496.7889 | 1184507.4371
6 | 2575465.9424 | 1184545.5171 | 2575459.8773 | 1184540.6061 | 2575442.9843 | 1184536.3178 | 2575438.4146 | 1184536.848
7 | 2575465.9424 | 1184545.5171 | 2575477.8878 | 1184549.3923 | 2575477.5469 | 1184566.7361 | 2575508.7014 | 1184575.7907 | 2575515.5301 | 1184577.7918
8 | 2575339.3347 | 1184771.383 | 2575459.9217 | 1184898.3933
9 | 2575524.2576 | 1184916.572 | 2575459.9217 | 1184898.3933
10 | 2575235.2231 | 1184755.5576 | 2575244.7544 | 1184757.1077 | 2575249.9954 | 1184756.5524
11 | 2575249.9954 | 1184756.5524 | 2575246.3357 | 1184768.4738 | 2575237.5739 | 1184799.9075
12 | 2575486.1826 | 1184480.2665 | 2575487.1855 | 1184492.1352 | 2575483.3192 | 1184505.9695 | 2575496.7889 | 1184507.4371
13 | 2575496.7889 | 1184507.4371 | 2575504.7837 | 1184508.3159 | 2575514.6386 | 1184511.1889
14 | 2575438.4146 | 1184536.848 | 2575439.8966 | 1184505.5287
15 | 2575486.1826 | 1184480.2665 | 2575480.9393 | 1184474.7407 | 2575470.1039 | 1184469.8604 | 2575452.8022 | 1184465.6598
16 | 2575336.2004 | 1184438.8737 | 2575338.5995 | 1184439.4752 | 2575408.8843 | 1184457.1167 | 2575424.133 | 1184458.6992 | 2575452.8022 | 1184465.6598
17 | 2575438.6816 | 1184488.5994 | 2575440.5703 | 1184491.293 | 2575439.8966 | 1184505.5287
18 | 2575438.6816 | 1184488.5994 | 2575434.708 | 1184485.6031 | 2575391.9866 | 1184474.199
19 | 2575344.5601 | 1184411.6582 | 2575336.2004 | 1184438.8737
20 | 2575336.2004 | 1184438.8737 | 2575281.8154 | 1184425.3052
21 | 2575344.5601 | 1184411.6582 | 2575321.117 | 1184405.4697
22 | 2575321.117 | 1184405.4697 | 2575271.0413 | 1184392.2505
23 | 2575271.0413 | 1184392.2505 | 2575265.7962 | 1184333.9062

## bus_geodata
| x | y | coords
0 | 2575401.2491 | 1184642.6327
1 | 2575403.4654 | 1184634.921
2 | 2575347.6943 | 1184736.093
3 | 2575465.9424 | 1184545.5171
4 | 2575339.3347 | 1184771.383
5 | 2575459.9217 | 1184898.3933
6 | 2575249.9954 | 1184756.5524
7 | 2575235.2231 | 1184755.5576
8 | 2575237.5739 | 1184799.9075
9 | 2575524.2576 | 1184916.572
10 | 2575496.7889 | 1184507.4371
11 | 2575438.4146 | 1184536.848
12 | 2575515.5301 | 1184577.7918
13 | 2575486.1826 | 1184480.2665
14 | 2575514.6386 | 1184511.1889
15 | 2575452.8022 | 1184465.6598
16 | 2575439.8966 | 1184505.5287
17 | 2575438.6816 | 1184488.5994
18 | 2575391.9866 | 1184474.199
19 | 2575336.2004 | 1184438.8737
20 | 2575344.5601 | 1184411.6582
21 | 2575281.8154 | 1184425.3052
22 | 2575321.117 | 1184405.4697
23 | 2575271.0413 | 1184392.2505
24 | 2575265.7962 | 1184333.9062
25 | 2575408.509 | 1184616.057

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99898 | -0.019306 | 0.094862 | 0.023775
1 | 1 | 0 | -0.54821 | -0.14078
2 | 0.98995 | -0.19106 | 0 | 0
3 | 0.98334 | -0.31686 | 0 | 0
4 | 0.98698 | -0.2484 | 0.043385 | 0.010873
5 | 0.98022 | -0.37976 | 0 | 0
6 | 0.97832 | -0.41645 | 0 | 0
7 | 0.97704 | -0.44154 | 0.09244 | 0.023168
8 | 0.97817 | -0.4193 | 0.0034692 | 0.00086947
9 | 0.97764 | -0.43025 | 0.041629 | 0.010433
10 | 0.98132 | -0.35594 | 0 | 0
11 | 0.97982 | -0.38499 | 0 | 0
12 | 0.9795 | -0.39186 | 0.059661 | 0.014952
13 | 0.98004 | -0.38101 | 0 | 0
14 | 0.98123 | -0.3577 | 0.0053055 | 0.0013297
15 | 0.97762 | -0.42816 | 0.028695 | 0.0071917
16 | 0.97612 | -0.45729 | 0.033826 | 0.0084775
17 | 0.9746 | -0.48709 | 0 | 0
18 | 0.97034 | -0.57114 | 0.09271 | 0.023235
19 | 0.97307 | -0.51764 | 0 | 0
20 | 0.97221 | -0.53458 | 0 | 0
21 | 0.97262 | -0.52637 | 0.0084635 | 0.0021211
22 | 0.97148 | -0.54903 | 0.026668 | 0.0066837
23 | 0.9712 | -0.55443 | 0.0043889 | 0.0011
24 | 0.97114 | -0.55577 | 0.001244 | 0.00031178
25 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.27907 | -0.071209 | 0.27933 | 0.071376 | 0.00026052 | 0.00016652 | 0.41613 | 0.41613 | 0.41613 | 0.99898 | -0.019306 | 1 | 0 | 57.1604
1 | 0.1842 | 0.047434 | -0.18268 | -0.046461 | 0.0015255 | 0.00097352 | 0.27483 | 0.27483 | 0.27483 | 0.99898 | -0.019306 | 0.98995 | -0.19106 | 37.7514
2 | 0.26723 | 0.069403 | -0.26315 | -0.066796 | 0.0040793 | 0.0026072 | 0.39851 | 0.39852 | 0.39852 | 1 | 0 | 0.98334 | -0.31686 | 54.7412
3 | 0.097065 | 0.024774 | -0.096021 | -0.024108 | 0.0010447 | 0.00066692 | 0.14606 | 0.14606 | 0.14606 | 0.98995 | -0.19106 | 0.97832 | -0.41645 | 40.1269
4 | 0.085613 | 0.021686 | -0.085378 | -0.021536 | 0.00023507 | 0.00014996 | 0.12877 | 0.12877 | 0.12877 | 0.98995 | -0.19106 | 0.98698 | -0.2484 | 35.3761
5 | 0.075377 | 0.019122 | -0.075236 | -0.019033 | 0.00014136 | 8.9006e-05 | 0.11415 | 0.11415 | 0.11415 | 0.98334 | -0.31686 | 0.98132 | -0.35594 | 15.6795
6 | 0.1279 | 0.032586 | -0.12748 | -0.032318 | 0.00041887 | 0.0002677 | 0.19374 | 0.19374 | 0.19374 | 0.98334 | -0.31686 | 0.97982 | -0.38499 | 53.2241
7 | 0.059875 | 0.015089 | -0.059661 | -0.014952 | 0.00021398 | 0.00013607 | 0.090634 | 0.090634 | 0.090634 | 0.98334 | -0.31686 | 0.9795 | -0.39186 | 24.8996
8 | 0.041993 | 0.010663 | -0.04173 | -0.010497 | 0.00026366 | 0.00016652 | 0.063361 | 0.063361 | 0.063361 | 0.98698 | -0.2484 | 0.98022 | -0.37976 | 17.407
9 | 0.04173 | 0.010497 | -0.041629 | -0.010433 | 0.00010038 | 6.3407e-05 | 0.063361 | 0.063362 | 0.063362 | 0.98022 | -0.37976 | 0.97764 | -0.43025 | 17.407
10 | 0.092551 | 0.023238 | -0.09244 | -0.023168 | 0.00011063 | 7.0615e-05 | 0.14078 | 0.14078 | 0.14078 | 0.97832 | -0.41645 | 0.97704 | -0.44154 | 38.6771
11 | 0.0034697 | 0.0008692 | -0.0034692 | -0.00086947 | 4.7104e-07 | -2.6478e-07 | 0.0052772 | 0.0052774 | 0.0052774 | 0.97832 | -0.41645 | 0.97817 | -0.4193 | 1.4498
12 | 0.06993 | 0.017703 | -0.069846 | -0.017651 | 8.4062e-05 | 5.2794e-05 | 0.1061 | 0.1061 | 0.1061 | 0.98132 | -0.35594 | 0.98004 | -0.38101 | 14.5744
13 | 0.005306 | 0.0013297 | -0.0053055 | -0.0013297 | 4.4442e-07 | 5.315e-08 | 0.0080456 | 0.0080457 | 0.0080457 | 0.98132 | -0.35594 | 0.98123 | -0.3577 | 2.2104
14 | 0.12748 | 0.032318 | -0.12704 | -0.032036 | 0.00044131 | 0.00028205 | 0.19374 | 0.19374 | 0.19374 | 0.97982 | -0.38499 | 0.97612 | -0.45729 | 53.2241
15 | 0.069846 | 0.017651 | -0.069689 | -0.01755 | 0.00015749 | 0.00010032 | 0.1061 | 0.1061 | 0.1061 | 0.98004 | -0.38101 | 0.97762 | -0.42816 | 29.1488
16 | 0.040993 | 0.010359 | -0.040818 | -0.010248 | 0.00017503 | 0.00011052 | 0.062425 | 0.062426 | 0.062426 | 0.97762 | -0.42816 | 0.97307 | -0.51764 | 17.1499
17 | 0.093216 | 0.023558 | -0.093083 | -0.023473 | 0.00013296 | 8.4875e-05 | 0.14217 | 0.14217 | 0.14217 | 0.97612 | -0.45729 | 0.9746 | -0.48709 | 39.058
18 | 0.093083 | 0.023473 | -0.09271 | -0.023235 | 0.00037288 | 0.00023803 | 0.14217 | 0.14217 | 0.14217 | 0.9746 | -0.48709 | 0.97034 | -0.57114 | 39.0581
19 | 0.032351 | 0.0081254 | -0.032325 | -0.008109 | 2.6135e-05 | 1.6373e-05 | 0.049478 | 0.049478 | 0.049478 | 0.97307 | -0.51764 | 0.97221 | -0.53458 | 13.5928
20 | 0.008467 | 0.0021227 | -0.0084635 | -0.0021211 | 3.524e-06 | 1.5594e-06 | 0.012948 | 0.012948 | 0.012948 | 0.97307 | -0.51764 | 0.97262 | -0.52637 | 3.5572
21 | 0.032325 | 0.008109 | -0.032303 | -0.0080951 | 2.2258e-05 | 1.3945e-05 | 0.049478 | 0.049478 | 0.049478 | 0.97221 | -0.53458 | 0.97148 | -0.54903 | 13.5928
22 | 0.0056344 | 0.0014113 | -0.005633 | -0.0014111 | 1.4465e-06 | 2.8469e-07 | 0.00863 | 0.0086302 | 0.0086302 | 0.97148 | -0.54903 | 0.9712 | -0.55443 | 2.3709
23 | 0.0012441 | 0.00031111 | -0.001244 | -0.00031178 | 7.9806e-08 | -6.7377e-07 | 0.0019059 | 0.0019062 | 0.0019062 | 0.9712 | -0.55443 | 0.97114 | -0.55577 | 0.52367

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54821 | 0.14078

## res_load
| p_mw | q_mvar
0 | 0.094862 | 0.023775
1 | 0.043385 | 0.010873
2 | 0.09244 | 0.023168
3 | 0.0034692 | 0.00086947
4 | 0.041629 | 0.010433
5 | 0.059661 | 0.014952
6 | 0.0053055 | 0.0013297
7 | 0.028695 | 0.0071917
8 | 0.033826 | 0.0084775
9 | 0.09271 | 0.023235
10 | 0.0084635 | 0.0021211
11 | 0.026668 | 0.0066837
12 | 0.0043889 | 0.0011
13 | 0.001244 | 0.00031178

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1