## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2197-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2197-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2197-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2197-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2197-6_0_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2197-6_0_3_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2197-6_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2197-6_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2197-6_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2197-6_0_3_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_2197-6_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2197-6_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2197-6_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_2197-6_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_2197-6_0_3_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2197-6_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2197-6_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2197-6_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2197-6_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2197-6_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2197-6_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2197-6_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2197-6_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2197-6_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2197-6_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_2197-6_0_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_2197-6_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_2197-6_0_3_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_2197-6_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_2197-6_0_3_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2197-6_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_MV_506_0_node_34 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2197-6_0_3_load_0 | 0 | 0.027928 | 0.0069994 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2197-6_0_3_load_2 | 2 | 0.051871 | 0.013 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2197-6_0_3_load_3 | 3 | 0.028032 | 0.0070254 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2197-6_0_3_load_6 | 4 | 0.001343 | 0.00033659 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2197-6_0_3_load_16 | 5 | 0.0020659 | 0.00051777 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2197-6_0_3_load_7 | 7 | 0.024441 | 0.0061255 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2197-6_0_3_load_20 | 9 | 0.063124 | 0.01582 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2197-6_0_3_load_9 | 10 | 0.060059 | 0.015052 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2197-6_0_3_load_8 | 11 | 0.018106 | 0.0045378 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2197-6_0_3_load_23 | 12 | 0.0038912 | 0.00097522 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2197-6_0_3_load_21 | 13 | 0.0021547 | 0.00054002 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2197-6_0_3_load_24 | 14 | 0.0016779 | 0.00042053 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2197-6_0_3_load_14 | 15 | 0.0038209 | 0.00095761 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2197-6_0_3_load_12 | 16 | 0.028805 | 0.0072191 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2197-6_0_3_load_11 | 18 | 0.011382 | 0.0028525 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2197-6_0_3_load_13 | 19 | 0.0042503 | 0.0010652 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2197-6_0_3_load_15 | 20 | 0.0025134 | 0.00062992 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2197-6_0_3_load_17 | 21 | 0.0022999 | 0.00057641 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2197-6_0_3_load_18 | 22 | 0.002865 | 0.00071804 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2197-6_0_3_load_19 | 23 | 0.0017454 | 0.00043745 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2197-6_0_3_load_25 | 24 | 0.0022132 | 0.00055469 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2197-6_0_3_load_29 | 26 | 0.0016454 | 0.00041238 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2197-6_0_3_load_26 | 27 | 0.0017547 | 0.00043978 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2197-6_0_3_load_30 | 29 | 0.002861 | 0.00071704 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2197-6_0_3_load_31 | 30 | 0.0024845 | 0.00062268 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2197-6_0_3_line_0 |  | 0 | 1 | 0.031264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2197-6_0_3_line_1 |  | 1 | 2 | 0.03718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2197-6_0_3_line_2 |  | 1 | 3 | 0.031314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2197-6_0_3_line_3 |  | 2 | 6 | 0.070608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2197-6_0_3_line_4 |  | 3 | 7 | 0.063067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2197-6_0_3_line_5 |  | 4 | 5 | 0.042543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2197-6_0_3_line_6 |  | 4 | 6 | 0.0174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2197-6_0_3_line_7 |  | 5 | 15 | 0.054204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2197-6_0_3_line_8 |  | 6 | 8 | 0.032961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2197-6_0_3_line_9 |  | 7 | 9 | 0.077863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2197-6_0_3_line_10 |  | 8 | 12 | 0.032217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2197-6_0_3_line_11 |  | 8 | 13 | 0.038447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2197-6_0_3_line_12 |  | 9 | 16 | 0.039851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2197-6_0_3_line_13 |  | 10 | 11 | 0.033918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2197-6_0_3_line_14 |  | 11 | 17 | 0.026159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2197-6_0_3_line_15 |  | 12 | 14 | 0.020632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2197-6_0_3_line_16 |  | 14 | 24 | 0.024906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2197-6_0_3_line_17 |  | 15 | 19 | 0.012853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2197-6_0_3_line_18 |  | 16 | 18 | 0.0079359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2197-6_0_3_line_19 |  | 17 | 18 | 0.033455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2197-6_0_3_line_20 |  | 19 | 20 | 0.016782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2197-6_0_3_line_21 |  | 20 | 21 | 0.02765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2197-6_0_3_line_22 |  | 21 | 22 | 0.0018126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2197-6_0_3_line_23 |  | 22 | 23 | 0.00061617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2197-6_0_3_line_24 |  | 24 | 25 | 0.0082129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2197-6_0_3_line_25 |  | 25 | 26 | 0.037431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2197-6_0_3_line_26 |  | 25 | 27 | 0.016676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2197-6_0_3_line_27 |  | 26 | 30 | 0.02497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2197-6_0_3_line_28 |  | 27 | 28 | 0.018441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2197-6_0_3_line_29 |  | 28 | 29 | 0.022109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2197-6_0_3_trafo_3 | 0.63 MVA 20/0.4 kV | 31 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2576705.3484 | 1185522.196 | 2576732.5098 | 1185537.6788
1 | 2576705.3484 | 1185522.196 | 2576715.5465 | 1185515.108 | 2576732.0368 | 1185509.0516 | 2576739.215 | 1185508.5798
2 | 2576705.3484 | 1185522.196 | 2576678.1813 | 1185506.6231
3 | 2576809.641 | 1185513.6519 | 2576739.215 | 1185508.5798
4 | 2576678.1813 | 1185506.6231 | 2576623.4661 | 1185475.2589
5 | 2576810.2922 | 1185531.0398 | 2576810.5181 | 1185537.0719 | 2576812.3999 | 1185573.5296
6 | 2576809.641 | 1185513.6519 | 2576810.2922 | 1185531.0398
7 | 2576812.3999 | 1185573.5296 | 2576813.4561 | 1185593.9903 | 2576814.1302 | 1185600.5578 | 2576815.9047 | 1185605.5202 | 2576818.7451 | 1185609.867 | 2576821.8467 | 1185612.712 | 2576824.6488 | 1185615.0579 | 2576831.7079 | 1185620.2917
8 | 2576833.0999 | 1185492.1829 | 2576825.756 | 1185495.4242 | 2576821.483 | 1185497.5197 | 2576818.3026 | 1185499.9556 | 2576815.7674 | 1185503.4673 | 2576813.2054 | 1185507.9129 | 2576809.641 | 1185513.6519
9 | 2576581.9393 | 1185409.3941 | 2576623.4661 | 1185475.2589
10 | 2576833.0999 | 1185492.1829 | 2576836.76 | 1185499.3169 | 2576840.5792 | 1185506.1279 | 2576848.8362 | 1185515.9788 | 2576851.6705 | 1185518.0942
11 | 2576833.0999 | 1185492.1829 | 2576841.249 | 1185487.9824 | 2576850.5723 | 1185481.5651 | 2576858.8865 | 1185474.6737 | 2576863.8723 | 1185469.5326
12 | 2576595.7592 | 1185372.0161 | 2576581.9393 | 1185409.3941
13 | 2576659.4802 | 1185394.4328 | 2576691.5134 | 1185405.5825
14 | 2576634.7753 | 1185385.8338 | 2576659.4802 | 1185394.4328
15 | 2576851.6705 | 1185518.0942 | 2576858.1121 | 1185522.902 | 2576868.4382 | 1185530.1122
16 | 2576868.4382 | 1185530.1122 | 2576868.6411 | 1185530.2539 | 2576876.7978 | 1185535.903 | 2576881.3172 | 1185540.2878 | 2576887.4674 | 1185546.067
17 | 2576831.7079 | 1185620.2917 | 2576842.0324 | 1185627.9467
18 | 2576595.7592 | 1185372.0161 | 2576603.2398 | 1185374.6654
19 | 2576634.7753 | 1185385.8338 | 2576603.2398 | 1185374.6654
20 | 2576855.5135 | 1185637.942 | 2576842.0324 | 1185627.9467
21 | 2576855.5135 | 1185637.942 | 2576876.4064 | 1185653.4328 | 2576877.7517 | 1185654.373
22 | 2576879.2374 | 1185655.4114 | 2576877.7517 | 1185654.373
23 | 2576879.7425 | 1185655.7644 | 2576879.2374 | 1185655.4114
24 | 2576894.5727 | 1185550.1861 | 2576887.4674 | 1185546.067
25 | 2576894.5727 | 1185550.1861 | 2576900.1414 | 1185553.5885 | 2576905.1101 | 1185557.7604 | 2576910.052 | 1185562.8773 | 2576915.6056 | 1185570.2708 | 2576919.4445 | 1185577.3534
26 | 2576894.5727 | 1185550.1861 | 2576904.3336 | 1185536.6656
27 | 2576919.4445 | 1185577.3534 | 2576922.3462 | 1185582.7067 | 2576931.2986 | 1185599.3308
28 | 2576915.1276 | 1185521.7138 | 2576904.3336 | 1185536.6656
29 | 2576898.0859 | 1185507.5724 | 2576915.1276 | 1185521.7138

## bus_geodata
| x | y | coords
0 | 2576732.5098 | 1185537.6788
1 | 2576705.3484 | 1185522.196
2 | 2576739.215 | 1185508.5798
3 | 2576678.1813 | 1185506.6231
4 | 2576810.2922 | 1185531.0398
5 | 2576812.3999 | 1185573.5296
6 | 2576809.641 | 1185513.6519
7 | 2576623.4661 | 1185475.2589
8 | 2576833.0999 | 1185492.1829
9 | 2576581.9393 | 1185409.3941
10 | 2576691.5134 | 1185405.5825
11 | 2576659.4802 | 1185394.4328
12 | 2576851.6705 | 1185518.0942
13 | 2576863.8723 | 1185469.5326
14 | 2576868.4382 | 1185530.1122
15 | 2576831.7079 | 1185620.2917
16 | 2576595.7592 | 1185372.0161
17 | 2576634.7753 | 1185385.8338
18 | 2576603.2398 | 1185374.6654
19 | 2576842.0324 | 1185627.9467
20 | 2576855.5135 | 1185637.942
21 | 2576877.7517 | 1185654.373
22 | 2576879.2374 | 1185655.4114
23 | 2576879.7425 | 1185655.7644
24 | 2576887.4674 | 1185546.067
25 | 2576894.5727 | 1185550.1861
26 | 2576919.4445 | 1185577.3534
27 | 2576904.3336 | 1185536.6656
28 | 2576915.1276 | 1185521.7138
29 | 2576898.0859 | 1185507.5724
30 | 2576931.2986 | 1185599.3308
31 | 2576705.3484 | 1185522.196

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99579 | -0.080729 | 0.027928 | 0.0069994
1 | 0.99658 | -0.065393 | 0 | 0
2 | 0.99347 | -0.12527 | 0.051871 | 0.013
3 | 1 | 0 | -0.33098 | -0.084095
4 | 0.99058 | -0.18123 | 0.001343 | 0.00033659
5 | 0.98981 | -0.19603 | 0.0020659 | 0.00051777
6 | 0.99091 | -0.17477 | 0 | 0
7 | 0.994 | -0.11386 | 0.024441 | 0.0061255
8 | 0.99035 | -0.18572 | 0 | 0
9 | 0.98747 | -0.23932 | 0.063124 | 0.01582
10 | 0.97622 | -0.45853 | 0.060059 | 0.015052
11 | 0.97812 | -0.42135 | 0.018106 | 0.0045378
12 | 0.98986 | -0.19519 | 0.0038912 | 0.00097522
13 | 0.99027 | -0.18719 | 0.0021547 | 0.00054002
14 | 0.98962 | -0.19983 | 0.0016779 | 0.00042053
15 | 0.98895 | -0.21292 | 0.0038209 | 0.00095761
16 | 0.9831 | -0.324 | 0.028805 | 0.0072191
17 | 0.98001 | -0.38417 | 0 | 0
18 | 0.98244 | -0.33683 | 0.011382 | 0.0028525
19 | 0.98878 | -0.21605 | 0.0042503 | 0.0010652
20 | 0.98864 | -0.21887 | 0.0025134 | 0.00062992
21 | 0.98846 | -0.22228 | 0.0022999 | 0.00057641
22 | 0.98846 | -0.22243 | 0.002865 | 0.00071804
23 | 0.98846 | -0.22245 | 0.0017454 | 0.00043745
24 | 0.98937 | -0.20469 | 0.0022132 | 0.00055469
25 | 0.9893 | -0.20597 | 0 | 0
26 | 0.98916 | -0.20872 | 0.0016454 | 0.00041238
27 | 0.98923 | -0.20734 | 0.0017547 | 0.00043978
28 | 0.98919 | -0.20828 | 0 | 0
29 | 0.98913 | -0.20941 | 0.002861 | 0.00071704
30 | 0.98911 | -0.20983 | 0.0024845 | 0.00062268
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.027928 | -0.0069994 | 0.027948 | 0.007012 | 2.0419e-05 | 1.2661e-05 | 0.041733 | 0.041733 | 0.041733 | 0.99579 | -0.080729 | 0.99658 | -0.065393 | 11.465
1 | 0.091878 | 0.023183 | -0.091615 | -0.023015 | 0.00026261 | 0.00016758 | 0.13724 | 0.13724 | 0.13724 | 0.99658 | -0.065393 | 0.99347 | -0.12527 | 37.7032
2 | -0.11983 | -0.030195 | 0.1202 | 0.030435 | 0.00037613 | 0.00024032 | 0.17897 | 0.17897 | 0.17897 | 0.99658 | -0.065393 | 1 | 0 | 49.1682
3 | 0.039744 | 0.010015 | -0.03965 | -0.0099561 | 9.3889e-05 | 5.9177e-05 | 0.059547 | 0.059548 | 0.059548 | 0.99347 | -0.12527 | 0.99091 | -0.17477 | 16.3592
4 | 0.20913 | 0.05366 | -0.20798 | -0.052927 | 0.0011484 | 0.00073333 | 0.31163 | 0.31163 | 0.31163 | 1 | 0 | 0.994 | -0.11386 | 42.8068
5 | 0.019593 | 0.0049211 | -0.019579 | -0.0049128 | 1.3824e-05 | 8.2998e-06 | 0.029436 | 0.029436 | 0.029436 | 0.99058 | -0.18123 | 0.98981 | -0.19603 | 8.0869
6 | -0.020936 | -0.0052577 | 0.020943 | 0.0052616 | 6.4553e-06 | 3.9074e-06 | 0.031454 | 0.031453 | 0.031454 | 0.99058 | -0.18123 | 0.99091 | -0.17477 | 8.6411
7 | 0.017513 | 0.0043951 | -0.017499 | -0.0043867 | 1.4092e-05 | 8.323e-06 | 0.026331 | 0.026331 | 0.026331 | 0.98981 | -0.19603 | 0.98895 | -0.21292 | 7.2337
8 | 0.018707 | 0.0046944 | -0.018697 | -0.0046886 | 9.7558e-06 | 5.8194e-06 | 0.028094 | 0.028094 | 0.028094 | 0.99091 | -0.17477 | 0.99035 | -0.18572 | 7.7182
9 | 0.18354 | 0.046801 | -0.18244 | -0.046096 | 0.0011044 | 0.00070484 | 0.27505 | 0.27505 | 0.27505 | 0.994 | -0.11386 | 0.98747 | -0.23932 | 37.7811
10 | 0.016543 | 0.004149 | -0.016535 | -0.0041446 | 7.4646e-06 | 4.363e-06 | 0.024857 | 0.024857 | 0.024857 | 0.99035 | -0.18572 | 0.98986 | -0.19519 | 6.8288
11 | 0.0021548 | 0.00053962 | -0.0021547 | -0.00054002 | 1.5113e-07 | -3.9795e-07 | 0.0032375 | 0.0032377 | 0.0032377 | 0.99035 | -0.18572 | 0.99027 | -0.18719 | 0.88948
12 | 0.11931 | 0.030276 | -0.11883 | -0.029967 | 0.00048379 | 0.00030912 | 0.17993 | 0.17993 | 0.17993 | 0.98747 | -0.23932 | 0.9831 | -0.324 | 49.4304
13 | -0.060059 | -0.015052 | 0.060165 | 0.01512 | 0.00010659 | 6.7795e-05 | 0.091545 | 0.091545 | 0.091545 | 0.97622 | -0.45853 | 0.97812 | -0.42135 | 25.1497
14 | -0.078272 | -0.019658 | 0.078411 | 0.019746 | 0.00013912 | 8.8709e-05 | 0.11909 | 0.11909 | 0.11909 | 0.97812 | -0.42135 | 0.98001 | -0.38417 | 32.717
15 | 0.012644 | 0.0031694 | -0.012641 | -0.0031679 | 2.7953e-06 | 1.5238e-06 | 0.019007 | 0.019007 | 0.019007 | 0.98986 | -0.19519 | 0.98962 | -0.19983 | 5.2218
16 | 0.010963 | 0.0027474 | -0.010961 | -0.0027461 | 2.538e-06 | 1.3044e-06 | 0.016485 | 0.016485 | 0.016485 | 0.98962 | -0.19983 | 0.98937 | -0.20469 | 4.5287
17 | 0.013678 | 0.0034291 | -0.013676 | -0.003428 | 2.0417e-06 | 1.1418e-06 | 0.020582 | 0.020582 | 0.020582 | 0.98895 | -0.21292 | 0.98878 | -0.21605 | 5.6543
18 | 0.090026 | 0.022748 | -0.08997 | -0.022712 | 5.531e-05 | 3.5298e-05 | 0.13633 | 0.13633 | 0.13633 | 0.9831 | -0.324 | 0.98244 | -0.33683 | 37.4529
19 | -0.078411 | -0.019746 | 0.078589 | 0.01986 | 0.00017793 | 0.00011345 | 0.11909 | 0.11909 | 0.11909 | 0.98001 | -0.38417 | 0.98244 | -0.33683 | 32.717
20 | 0.0094262 | 0.0023628 | -0.0094249 | -0.0023622 | 1.2664e-06 | 5.9528e-07 | 0.014185 | 0.014186 | 0.014186 | 0.98878 | -0.21605 | 0.98864 | -0.21887 | 3.8971
21 | 0.0069115 | 0.0017322 | -0.0069104 | -0.0017319 | 1.1221e-06 | 3.6364e-07 | 0.010403 | 0.010403 | 0.010403 | 0.98864 | -0.21887 | 0.98846 | -0.22228 | 2.8579
22 | 0.0046105 | 0.0011555 | -0.0046104 | -0.0011555 | 3.2743e-08 | -2.2789e-09 | 0.0069405 | 0.0069405 | 0.0069405 | 0.98846 | -0.22228 | 0.98846 | -0.22243 | 1.9067
23 | 0.0017454 | 0.00043744 | -0.0017454 | -0.00043745 | 1.5954e-09 | -6.8774e-09 | 0.0026276 | 0.0026276 | 0.0026276 | 0.98846 | -0.22243 | 0.98846 | -0.22245 | 0.72186
24 | 0.0087475 | 0.0021914 | -0.008747 | -0.0021911 | 5.3306e-07 | 2.3569e-07 | 0.013156 | 0.013156 | 0.013156 | 0.98937 | -0.20469 | 0.9893 | -0.20597 | 3.6143
25 | 0.0041306 | 0.0010347 | -0.0041301 | -0.0010348 | 5.4179e-07 | -1.338e-07 | 0.0062127 | 0.0062129 | 0.0062129 | 0.9893 | -0.20597 | 0.98916 | -0.20872 | 1.7068
26 | 0.0046163 | 0.0011565 | -0.004616 | -0.0011565 | 3.0147e-07 | -2.1161e-08 | 0.0069433 | 0.0069433 | 0.0069433 | 0.9893 | -0.20597 | 0.98923 | -0.20734 | 1.9075
27 | 0.0024846 | 0.00062244 | -0.0024845 | -0.00062268 | 1.3081e-07 | -2.3679e-07 | 0.0037376 | 0.0037377 | 0.0037377 | 0.98916 | -0.20872 | 0.98911 | -0.20983 | 1.0268
28 | 0.0028613 | 0.00071669 | -0.0028612 | -0.00071685 | 1.281e-07 | -1.5476e-07 | 0.0043038 | 0.0043039 | 0.0043039 | 0.98923 | -0.20734 | 0.98919 | -0.20828 | 1.1824
29 | 0.0028612 | 0.00071685 | -0.002861 | -0.00071704 | 1.5358e-07 | -1.8551e-07 | 0.0043039 | 0.004304 | 0.004304 | 0.98919 | -0.20828 | 0.98913 | -0.20941 | 1.1824

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35901 | 0.091121

## res_load
| p_mw | q_mvar
0 | 0.027928 | 0.0069994
1 | 0.051871 | 0.013
2 | 0.028032 | 0.0070254
3 | 0.001343 | 0.00033659
4 | 0.0020659 | 0.00051777
5 | 0.024441 | 0.0061255
6 | 0.063124 | 0.01582
7 | 0.060059 | 0.015052
8 | 0.018106 | 0.0045378
9 | 0.0038912 | 0.00097522
10 | 0.0021547 | 0.00054002
11 | 0.0016779 | 0.00042053
12 | 0.0038209 | 0.00095761
13 | 0.028805 | 0.0072191
14 | 0.011382 | 0.0028525
15 | 0.0042503 | 0.0010652
16 | 0.0025134 | 0.00062992
17 | 0.0022999 | 0.00057641
18 | 0.002865 | 0.00071804
19 | 0.0017454 | 0.00043745
20 | 0.0022132 | 0.00055469
21 | 0.0016454 | 0.00041238
22 | 0.0017547 | 0.00043978
23 | 0.002861 | 0.00071704
24 | 0.0024845 | 0.00062268

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1