## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2198-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2198-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2198-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2198-11_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2198-11_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2198-11_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2198-11_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2198-11_0_4_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_2198-11_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_2198-11_0_4_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_2198-11_0_4_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_2198-11_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_2198-11_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2198-11_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_2198-11_0_4_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_2198-11_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2198-11_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_2198-11_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_2198-11_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2198-11_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2198-11_0_4_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_2198-11_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2198-11_0_4_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_2198-11_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2198-11_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2198-11_0_4_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_2198-11_0_4_node_37 | 0.4 | n |  | TRUE
27 | bus_LV_2198-11_0_4_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_2198-11_0_4_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_2198-11_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_2198-11_0_4_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2198-11_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2198-11_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2198-11_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_2198-11_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_2198-11_0_4_node_33 | 0.4 | n |  | TRUE
36 | bus_MV_506_0_node_53 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2198-11_0_4_load_0 | 0 | 0.021556 | 0.0054025 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2198-11_0_4_load_1 | 1 | 0.033564 | 0.0084119 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2198-11_0_4_load_4 | 4 | 0.022714 | 0.0056926 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2198-11_0_4_load_5 | 5 | 0.011403 | 0.0028579 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2198-11_0_4_load_17 | 7 | 0.017618 | 0.0044155 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2198-11_0_4_load_38 | 9 | 0.013282 | 0.0033287 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2198-11_0_4_load_28 | 10 | 0.0081989 | 0.0020548 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2198-11_0_4_load_27 | 13 | 0.010025 | 0.0025125 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2198-11_0_4_load_26 | 14 | 0.0077183 | 0.0019344 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2198-11_0_4_load_16 | 15 | 0.02995 | 0.0075061 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2198-11_0_4_load_7 | 16 | 0.021368 | 0.0053554 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2198-11_0_4_load_8 | 17 | 0.0019302 | 0.00048375 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2198-11_0_4_load_9 | 18 | 0.0090736 | 0.0022741 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2198-11_0_4_load_21 | 20 | 0.0038973 | 0.00097676 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2198-11_0_4_load_18 | 21 | 0.0026278 | 0.0006586 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2198-11_0_4_load_29 | 22 | 0.024642 | 0.006176 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2198-11_0_4_load_19 | 24 | 0.0044217 | 0.0011082 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2198-11_0_4_load_36 | 25 | 0.0036117 | 0.00090518 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2198-11_0_4_load_37 | 26 | 0.0032127 | 0.00080517 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2198-11_0_4_load_34 | 27 | 0.0042164 | 0.0010567 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2198-11_0_4_load_12 | 28 | 0.0090348 | 0.0022643 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2198-11_0_4_load_13 | 29 | 0.0037745 | 0.00094599 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2198-11_0_4_load_32 | 30 | 0.035318 | 0.0088515 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2198-11_0_4_load_22 | 31 | 0.03706 | 0.0092881 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2198-11_0_4_load_23 | 32 | 0.02727 | 0.0068345 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2198-11_0_4_load_31 | 33 | 0.029598 | 0.007418 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2198-11_0_4_load_30 | 34 | 0.026531 | 0.0066493 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2198-11_0_4_load_33 | 35 | 0.026715 | 0.0066955 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2198-11_0_4_line_0 |  | 0 | 1 | 0.036022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2198-11_0_4_line_1 |  | 0 | 2 | 0.0082848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2198-11_0_4_line_2 |  | 1 | 3 | 0.027942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2198-11_0_4_line_3 |  | 2 | 4 | 0.022374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2198-11_0_4_line_4 |  | 3 | 6 | 0.002723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2198-11_0_4_line_5 |  | 4 | 5 | 0.0027417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2198-11_0_4_line_6 |  | 5 | 12 | 0.035702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2198-11_0_4_line_7 |  | 6 | 9 | 0.018969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2198-11_0_4_line_8 |  | 7 | 8 | 0.017029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2198-11_0_4_line_9 |  | 8 | 15 | 0.013266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2198-11_0_4_line_10 |  | 8 | 28 | 0.014467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2198-11_0_4_line_11 |  | 10 | 11 | 0.012705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2198-11_0_4_line_12 |  | 11 | 22 | 0.025591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2198-11_0_4_line_13 |  | 11 | 18 | 0.011007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2198-11_0_4_line_14 |  | 12 | 13 | 0.012699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2198-11_0_4_line_15 |  | 12 | 14 | 0.030911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2198-11_0_4_line_16 |  | 14 | 15 | 0.02861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2198-11_0_4_line_17 |  | 16 | 17 | 0.0037697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2198-11_0_4_line_18 |  | 16 | 18 | 0.020098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2198-11_0_4_line_19 |  | 17 | 19 | 0.013978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2198-11_0_4_line_20 |  | 19 | 20 | 0.017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2198-11_0_4_line_21 |  | 19 | 21 | 0.021366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2198-11_0_4_line_22 |  | 20 | 23 | 0.013917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2198-11_0_4_line_23 |  | 21 | 24 | 0.0011201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2198-11_0_4_line_24 |  | 23 | 29 | 0.01678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2198-11_0_4_line_25 |  | 24 | 26 | 0.058606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2198-11_0_4_line_26 |  | 25 | 26 | 0.026864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2198-11_0_4_line_27 |  | 25 | 27 | 0.039595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2198-11_0_4_line_28 |  | 27 | 30 | 0.030715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2198-11_0_4_line_29 |  | 28 | 29 | 0.0017401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2198-11_0_4_line_30 |  | 30 | 34 | 0.018757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2198-11_0_4_line_31 |  | 31 | 32 | 0.0027361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2198-11_0_4_line_32 |  | 31 | 33 | 0.046281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2198-11_0_4_line_33 |  | 33 | 35 | 0.01887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2198-11_0_4_line_34 |  | 33 | 34 | 0.019178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2198-11_0_4_trafo_16 | 0.63 MVA 20/0.4 kV | 36 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2577135.3112 | 1184664.2943 | 2577135.0586 | 1184673.7457 | 2577131.596 | 1184700.0862
1 | 2577135.5326 | 1184656.0124 | 2577135.3112 | 1184664.2943
2 | 2577127.9542 | 1184727.7901 | 2577131.596 | 1184700.0862
3 | 2577154.0926 | 1184643.5167 | 2577135.5326 | 1184656.0124
4 | 2577127.9542 | 1184727.7901 | 2577130.6276 | 1184728.3468
5 | 2577154.0926 | 1184643.5167 | 2577153.6048 | 1184640.8187
6 | 2577178.7326 | 1184628.4438 | 2577155.6869 | 1184631.4446 | 2577152.0492 | 1184632.2145 | 2577153.6048 | 1184640.8187
7 | 2577130.6276 | 1184728.3468 | 2577133.9039 | 1184728.8901 | 2577139.3657 | 1184728.1577 | 2577144.6819 | 1184725.2803 | 2577147.7842 | 1184722.6117
8 | 2577199.0499 | 1184698.336 | 2577182.7351 | 1184703.2166
9 | 2577199.0499 | 1184698.336 | 2577195.2957 | 1184685.6122
10 | 2577199.0499 | 1184698.336 | 2577202.7218 | 1184712.3294
11 | 2577169.67 | 1184775.1885 | 2577167.0682 | 1184762.7523
12 | 2577169.67 | 1184775.1885 | 2577144.8059 | 1184781.5314
13 | 2577169.67 | 1184775.1885 | 2577174.8254 | 1184772.1894 | 2577179.6756 | 1184770.8102
14 | 2577178.7326 | 1184628.4438 | 2577177.9954 | 1184615.766
15 | 2577178.7326 | 1184628.4438 | 2577186.2063 | 1184654.8068 | 2577187.1993 | 1184658.1721
16 | 2577187.1993 | 1184658.1721 | 2577195.2957 | 1184685.6122
17 | 2577199.0072 | 1184765.3132 | 2577202.6331 | 1184764.2821
18 | 2577199.0072 | 1184765.3132 | 2577179.6756 | 1184770.8102
19 | 2577216.0781 | 1184760.459 | 2577202.6331 | 1184764.2821
20 | 2577216.0781 | 1184760.459 | 2577211.2548 | 1184743.6216
21 | 2577216.0781 | 1184760.459 | 2577224.228 | 1184780.2099
22 | 2577207.4223 | 1184730.2429 | 2577211.2548 | 1184743.6216
23 | 2577224.6553 | 1184781.2453 | 2577224.228 | 1184780.2099
24 | 2577207.4223 | 1184730.2429 | 2577203.1634 | 1184714.0125
25 | 2577224.6553 | 1184781.2453 | 2577281.4974 | 1184766.9733
26 | 2577276.8664 | 1184740.5121 | 2577280.7322 | 1184763.0472 | 2577281.4974 | 1184766.9733
27 | 2577276.8664 | 1184740.5121 | 2577273.3872 | 1184720.2306 | 2577270.0007 | 1184701.5172
28 | 2577264.5312 | 1184671.293 | 2577270.0007 | 1184701.5172
29 | 2577203.1634 | 1184714.0125 | 2577202.7218 | 1184712.3294
30 | 2577261.1911 | 1184652.8362 | 2577264.5312 | 1184671.293
31 | 2577211.395 | 1184649.6095 | 2577214.1155 | 1184649.318
32 | 2577214.1155 | 1184649.318 | 2577257.7759 | 1184633.9646
33 | 2577254.4157 | 1184615.3967 | 2577257.7759 | 1184633.9646
34 | 2577261.1911 | 1184652.8362 | 2577257.7759 | 1184633.9646

## bus_geodata
| x | y | coords
0 | 2577135.3112 | 1184664.2943
1 | 2577131.596 | 1184700.0862
2 | 2577135.5326 | 1184656.0124
3 | 2577127.9542 | 1184727.7901
4 | 2577154.0926 | 1184643.5167
5 | 2577153.6048 | 1184640.8187
6 | 2577130.6276 | 1184728.3468
7 | 2577182.7351 | 1184703.2166
8 | 2577199.0499 | 1184698.336
9 | 2577147.7842 | 1184722.6117
10 | 2577167.0682 | 1184762.7523
11 | 2577169.67 | 1184775.1885
12 | 2577178.7326 | 1184628.4438
13 | 2577177.9954 | 1184615.766
14 | 2577187.1993 | 1184658.1721
15 | 2577195.2957 | 1184685.6122
16 | 2577199.0072 | 1184765.3132
17 | 2577202.6331 | 1184764.2821
18 | 2577179.6756 | 1184770.8102
19 | 2577216.0781 | 1184760.459
20 | 2577211.2548 | 1184743.6216
21 | 2577224.228 | 1184780.2099
22 | 2577144.8059 | 1184781.5314
23 | 2577207.4223 | 1184730.2429
24 | 2577224.6553 | 1184781.2453
25 | 2577276.8664 | 1184740.5121
26 | 2577281.4974 | 1184766.9733
27 | 2577270.0007 | 1184701.5172
28 | 2577202.7218 | 1184712.3294
29 | 2577203.1634 | 1184714.0125
30 | 2577264.5312 | 1184671.293
31 | 2577214.1155 | 1184649.318
32 | 2577211.395 | 1184649.6095
33 | 2577257.7759 | 1184633.9646
34 | 2577261.1911 | 1184652.8362
35 | 2577254.4157 | 1184615.3967
36 | 2577199.0499 | 1184698.336

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98813 | -0.22802 | 0.021556 | 0.0054025
1 | 0.98658 | -0.25819 | 0.033564 | 0.0084119
2 | 0.98865 | -0.21791 | 0 | 0
3 | 0.98624 | -0.26484 | 0 | 0
4 | 0.99006 | -0.19065 | 0.022714 | 0.0056926
5 | 0.99029 | -0.18621 | 0.011403 | 0.0028579
6 | 0.98621 | -0.26549 | 0 | 0
7 | 0.9985 | -0.028406 | 0.017618 | 0.0044155
8 | 0.99878 | -0.023162 | 0 | 0
9 | 0.98598 | -0.27 | 0.013282 | 0.0033287
10 | 0.99114 | -0.16914 | 0.0081989 | 0.0020548
11 | 0.99124 | -0.1673 | 0 | 0
12 | 0.99365 | -0.12138 | 0 | 0
13 | 0.99353 | -0.12363 | 0.010025 | 0.0025125
14 | 0.99684 | -0.060162 | 0.0077183 | 0.0019344
15 | 1 | 0 | -0.42754 | -0.10887
16 | 0.99234 | -0.14596 | 0.021368 | 0.0053554
17 | 0.99256 | -0.14174 | 0.0019302 | 0.00048375
18 | 0.99157 | -0.16089 | 0.0090736 | 0.0022741
19 | 0.99339 | -0.12563 | 0 | 0
20 | 0.99482 | -0.098257 | 0.0038973 | 0.00097676
21 | 0.99207 | -0.1509 | 0.0026278 | 0.0006586
22 | 0.99066 | -0.17849 | 0.024642 | 0.006176
23 | 0.99598 | -0.076247 | 0 | 0
24 | 0.992 | -0.1522 | 0.0044217 | 0.0011082
25 | 0.98692 | -0.24986 | 0.0036117 | 0.00090518
26 | 0.9885 | -0.21941 | 0.0032127 | 0.00080517
27 | 0.98464 | -0.29406 | 0.0042164 | 0.0010567
28 | 0.99752 | -0.046998 | 0.0090348 | 0.0022643
29 | 0.99737 | -0.049777 | 0.0037745 | 0.00094599
30 | 0.98291 | -0.32771 | 0.035318 | 0.0088515
31 | 0.97672 | -0.44883 | 0.03706 | 0.0092881
32 | 0.97665 | -0.4502 | 0.02727 | 0.0068345
33 | 0.97948 | -0.39459 | 0.029598 | 0.007418
34 | 0.98163 | -0.35265 | 0.026531 | 0.0066493
35 | 0.97901 | -0.40375 | 0.026715 | 0.0066955
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.04692 | 0.011787 | -0.046853 | -0.011745 | 6.7457e-05 | 4.2712e-05 | 0.070667 | 0.070667 | 0.070667 | 0.98813 | -0.22802 | 0.98658 | -0.25819 | 19.4139
1 | -0.068477 | -0.01719 | 0.06851 | 0.017211 | 3.3042e-05 | 2.1041e-05 | 0.10313 | 0.10313 | 0.10313 | 0.98813 | -0.22802 | 0.98865 | -0.21791 | 28.3319
2 | 0.013289 | 0.0033329 | -0.013285 | -0.0033305 | 4.2099e-06 | 2.3377e-06 | 0.020044 | 0.020044 | 0.020044 | 0.98658 | -0.25819 | 0.98624 | -0.26484 | 5.5067
3 | -0.06851 | -0.017211 | 0.068599 | 0.017268 | 8.9235e-05 | 5.6823e-05 | 0.10313 | 0.10313 | 0.10313 | 0.98865 | -0.21791 | 0.99006 | -0.19065 | 28.3318
4 | 0.013285 | 0.0033305 | -0.013285 | -0.0033303 | 4.1026e-07 | 2.2782e-07 | 0.020044 | 0.020044 | 0.020044 | 0.98624 | -0.26484 | 0.98621 | -0.26549 | 5.5067
5 | -0.091313 | -0.02296 | 0.091332 | 0.022973 | 1.9372e-05 | 1.2363e-05 | 0.13727 | 0.13727 | 0.13727 | 0.99006 | -0.19065 | 0.99029 | -0.18621 | 37.7103
6 | -0.10274 | -0.025831 | 0.10305 | 0.026035 | 0.00031917 | 0.00020381 | 0.1544 | 0.1544 | 0.1544 | 0.99029 | -0.18621 | 0.99365 | -0.12138 | 42.4176
7 | 0.013285 | 0.0033303 | -0.013282 | -0.0033287 | 2.858e-06 | 1.5871e-06 | 0.020044 | 0.020044 | 0.020044 | 0.98621 | -0.26549 | 0.98598 | -0.27 | 5.5067
8 | -0.017618 | -0.0044155 | 0.017623 | 0.0044181 | 4.4021e-06 | 2.5945e-06 | 0.026255 | 0.026255 | 0.026255 | 0.9985 | -0.028406 | 0.99878 | -0.023162 | 7.213
9 | -0.30407 | -0.077732 | 0.30441 | 0.07795 | 0.00034112 | 0.0002178 | 0.45355 | 0.45355 | 0.45355 | 0.99878 | -0.023162 | 1 | 0 | 41.5343
10 | 0.28645 | 0.073314 | -0.28612 | -0.073103 | 0.00033019 | 0.00021075 | 0.4273 | 0.4273 | 0.4273 | 0.99878 | -0.023162 | 0.99752 | -0.046998 | 39.13
11 | -0.0081989 | -0.0020548 | 0.0081996 | 0.0020551 | 7.219e-07 | 2.9825e-07 | 0.012309 | 0.012309 | 0.012309 | 0.99114 | -0.16914 | 0.99124 | -0.1673 | 3.3816
12 | 0.024656 | 0.006184 | -0.024642 | -0.006176 | 1.3148e-05 | 8.0848e-06 | 0.037014 | 0.037014 | 0.037014 | 0.99124 | -0.1673 | 0.99066 | -0.17849 | 10.1687
13 | -0.032855 | -0.0082392 | 0.032865 | 0.0082455 | 1.0041e-05 | 6.2845e-06 | 0.049323 | 0.049323 | 0.049323 | 0.99124 | -0.1673 | 0.99157 | -0.16089 | 13.5502
14 | 0.010026 | 0.002513 | -0.010025 | -0.0025125 | 1.0736e-06 | 5.226e-07 | 0.015014 | 0.015014 | 0.015014 | 0.99365 | -0.12138 | 0.99353 | -0.12363 | 4.1248
15 | -0.11308 | -0.028548 | 0.11341 | 0.02876 | 0.00033269 | 0.00021252 | 0.16941 | 0.16941 | 0.16941 | 0.99365 | -0.12138 | 0.99684 | -0.060162 | 46.5424
16 | -0.12113 | -0.030694 | 0.12148 | 0.030919 | 0.00035123 | 0.00022441 | 0.18094 | 0.18094 | 0.18094 | 0.99684 | -0.060162 | 1 | 0 | 49.7075
17 | -0.063337 | -0.015894 | 0.06335 | 0.015902 | 1.2753e-05 | 8.1132e-06 | 0.094981 | 0.094981 | 0.094981 | 0.99234 | -0.14596 | 0.99256 | -0.14174 | 26.0937
18 | 0.041969 | 0.010538 | -0.041939 | -0.01052 | 2.9856e-05 | 1.8848e-05 | 0.062939 | 0.062939 | 0.062939 | 0.99234 | -0.14596 | 0.99157 | -0.16089 | 17.291
19 | -0.06528 | -0.016386 | 0.06533 | 0.016418 | 5.0213e-05 | 3.1956e-05 | 0.097875 | 0.097875 | 0.097875 | 0.99256 | -0.14174 | 0.99339 | -0.12563 | 26.8887
20 | -0.26838 | -0.068258 | 0.26873 | 0.068484 | 0.00035444 | 0.00022616 | 0.40236 | 0.40236 | 0.40236 | 0.99339 | -0.12563 | 0.99482 | -0.098257 | 36.8464
21 | 0.20305 | 0.05184 | -0.2028 | -0.051683 | 0.00024762 | 0.00015765 | 0.30449 | 0.30449 | 0.30449 | 0.99339 | -0.12563 | 0.99207 | -0.1509 | 27.8836
22 | -0.27263 | -0.069461 | 0.27292 | 0.069646 | 0.00028985 | 0.00018496 | 0.40819 | 0.40819 | 0.40819 | 0.99482 | -0.098257 | 0.99598 | -0.076247 | 37.3802
23 | 0.20017 | 0.051024 | -0.20016 | -0.051016 | 1.2647e-05 | 8.0509e-06 | 0.30055 | 0.30055 | 0.30055 | 0.99207 | -0.1509 | 0.992 | -0.1522 | 27.5227
24 | -0.27292 | -0.069646 | 0.27327 | 0.069869 | 0.00034948 | 0.00022301 | 0.40819 | 0.40819 | 0.40819 | 0.99598 | -0.076247 | 0.99737 | -0.049777 | 37.3802
25 | 0.19574 | 0.049908 | -0.19511 | -0.049505 | 0.00063285 | 0.00040276 | 0.29391 | 0.29392 | 0.29392 | 0.992 | -0.1522 | 0.9885 | -0.21941 | 26.9154
26 | -0.19161 | -0.048521 | 0.19189 | 0.0487 | 0.00028062 | 0.00017857 | 0.28908 | 0.28908 | 0.28908 | 0.98692 | -0.24986 | 0.9885 | -0.21941 | 26.4725
27 | 0.188 | 0.047616 | -0.1876 | -0.047363 | 0.00039817 | 0.00025331 | 0.28363 | 0.28364 | 0.28364 | 0.98692 | -0.24986 | 0.98464 | -0.29406 | 25.9739
28 | 0.18339 | 0.046306 | -0.18309 | -0.046118 | 0.00029515 | 0.00018773 | 0.27726 | 0.27726 | 0.27726 | 0.98464 | -0.29406 | 0.98291 | -0.32771 | 25.3904
29 | 0.27708 | 0.070839 | -0.27704 | -0.070815 | 3.7249e-05 | 2.3771e-05 | 0.41382 | 0.41382 | 0.41382 | 0.99752 | -0.046998 | 0.99737 | -0.049777 | 37.8959
30 | 0.14777 | 0.037267 | -0.1476 | -0.037155 | 0.00017614 | 0.00011226 | 0.2238 | 0.2238 | 0.2238 | 0.98291 | -0.32771 | 0.98163 | -0.35265 | 30.7412
31 | 0.027272 | 0.0068356 | -0.02727 | -0.0068345 | 1.7713e-06 | 1.0994e-06 | 0.041549 | 0.041549 | 0.041549 | 0.97672 | -0.44883 | 0.97665 | -0.4502 | 11.4145
32 | -0.064332 | -0.016124 | 0.064499 | 0.01623 | 0.00016671 | 0.00010611 | 0.098009 | 0.098009 | 0.098009 | 0.97672 | -0.44883 | 0.97948 | -0.39459 | 26.9255
33 | 0.026727 | 0.0067027 | -0.026715 | -0.0066955 | 1.1667e-05 | 7.2293e-06 | 0.040605 | 0.040605 | 0.040605 | 0.97948 | -0.39459 | 0.97901 | -0.40375 | 11.1552
34 | -0.12082 | -0.030351 | 0.12107 | 0.030505 | 0.00024237 | 0.00015488 | 0.18358 | 0.18358 | 0.18358 | 0.97948 | -0.39459 | 0.98163 | -0.35265 | 50.4337

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45749 | 0.11637

## res_load
| p_mw | q_mvar
0 | 0.021556 | 0.0054025
1 | 0.033564 | 0.0084119
2 | 0.022714 | 0.0056926
3 | 0.011403 | 0.0028579
4 | 0.017618 | 0.0044155
5 | 0.013282 | 0.0033287
6 | 0.0081989 | 0.0020548
7 | 0.010025 | 0.0025125
8 | 0.0077183 | 0.0019344
9 | 0.02995 | 0.0075061
10 | 0.021368 | 0.0053554
11 | 0.0019302 | 0.00048375
12 | 0.0090736 | 0.0022741
13 | 0.0038973 | 0.00097676
14 | 0.0026278 | 0.0006586
15 | 0.024642 | 0.006176
16 | 0.0044217 | 0.0011082
17 | 0.0036117 | 0.00090518
18 | 0.0032127 | 0.00080517
19 | 0.0042164 | 0.0010567
20 | 0.0090348 | 0.0022643
21 | 0.0037745 | 0.00094599
22 | 0.035318 | 0.0088515
23 | 0.03706 | 0.0092881
24 | 0.02727 | 0.0068345
25 | 0.029598 | 0.007418
26 | 0.026531 | 0.0066493
27 | 0.026715 | 0.0066955

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1