## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2198-8_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2198-8_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2198-8_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2198-8_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2198-8_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2198-8_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2198-8_0_5_node_65 | 0.4 | n |  | TRUE
7 | bus_LV_2198-8_0_5_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_2198-8_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2198-8_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2198-8_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2198-8_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_2198-8_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_2198-8_0_5_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_2198-8_0_5_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_2198-8_0_5_node_70 | 0.4 | n |  | TRUE
16 | bus_LV_2198-8_0_5_node_71 | 0.4 | n |  | TRUE
17 | bus_LV_2198-8_0_5_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_2198-8_0_5_node_56 | 0.4 | n |  | TRUE
19 | bus_LV_2198-8_0_5_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2198-8_0_5_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2198-8_0_5_node_72 | 0.4 | n |  | TRUE
22 | bus_LV_2198-8_0_5_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_2198-8_0_5_node_57 | 0.4 | n |  | TRUE
24 | bus_LV_2198-8_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2198-8_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2198-8_0_5_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2198-8_0_5_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2198-8_0_5_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2198-8_0_5_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2198-8_0_5_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2198-8_0_5_node_61 | 0.4 | n |  | TRUE
32 | bus_LV_2198-8_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_2198-8_0_5_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2198-8_0_5_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_2198-8_0_5_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_2198-8_0_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_2198-8_0_5_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_2198-8_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_2198-8_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2198-8_0_5_node_59 | 0.4 | n |  | TRUE
41 | bus_LV_2198-8_0_5_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_2198-8_0_5_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2198-8_0_5_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_2198-8_0_5_node_77 | 0.4 | n |  | TRUE
45 | bus_LV_2198-8_0_5_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_2198-8_0_5_node_76 | 0.4 | n |  | TRUE
47 | bus_LV_2198-8_0_5_node_75 | 0.4 | n |  | TRUE
48 | bus_LV_2198-8_0_5_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2198-8_0_5_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_2198-8_0_5_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2198-8_0_5_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2198-8_0_5_node_68 | 0.4 | n |  | TRUE
53 | bus_LV_2198-8_0_5_node_74 | 0.4 | n |  | TRUE
54 | bus_LV_2198-8_0_5_node_54 | 0.4 | n |  | TRUE
55 | bus_LV_2198-8_0_5_node_69 | 0.4 | n |  | TRUE
56 | bus_LV_2198-8_0_5_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_2198-8_0_5_node_73 | 0.4 | n |  | TRUE
58 | bus_LV_2198-8_0_5_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_2198-8_0_5_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_2198-8_0_5_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_2198-8_0_5_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_2198-8_0_5_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_2198-8_0_5_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2198-8_0_5_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_2198-8_0_5_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_2198-8_0_5_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_2198-8_0_5_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_2198-8_0_5_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_2198-8_0_5_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_2198-8_0_5_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_2198-8_0_5_node_66 | 0.4 | n |  | TRUE
72 | bus_MV_506_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2198-8_0_5_load_0 | 0 | 0.0048159 | 0.001207 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2198-8_0_5_load_1 | 1 | 0.0070041 | 0.0017554 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2198-8_0_5_load_2 | 2 | 0.030698 | 0.0076936 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2198-8_0_5_load_3 | 3 | 0.0021547 | 0.00054001 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2198-8_0_5_load_5 | 5 | 0.0053858 | 0.0013498 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2198-8_0_5_load_65 | 6 | 0.0064021 | 0.0016045 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2198-8_0_5_load_7 | 8 | 0.0047912 | 0.0012008 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2198-8_0_5_load_8 | 9 | 0.0068142 | 0.0017078 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2198-8_0_5_load_12 | 13 | 0.011051 | 0.0027697 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2198-8_0_5_load_13 | 14 | 0.0092321 | 0.0023138 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2198-8_0_5_load_70 | 15 | 0.013954 | 0.0034971 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2198-8_0_5_load_56 | 18 | 0.0011858 | 0.00029718 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2198-8_0_5_load_24 | 20 | 0.0021493 | 0.00053867 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2198-8_0_5_load_72 | 21 | 0.04778 | 0.011975 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2198-8_0_5_load_57 | 23 | 0.0050229 | 0.0012589 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2198-8_0_5_load_19 | 24 | 0.0038237 | 0.00095832 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2198-8_0_5_load_16 | 25 | 0.0021825 | 0.00054698 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2198-8_0_5_load_23 | 26 | 0.0014406 | 0.00036106 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2198-8_0_5_load_14 | 27 | 0.0096361 | 0.002415 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2198-8_0_5_load_15 | 28 | 0.0020253 | 0.0005076 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2198-8_0_5_load_61 | 31 | 0.004747 | 0.0011897 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2198-8_0_5_load_22 | 33 | 0.0018038 | 0.00045206 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2198-8_0_5_load_20 | 34 | 0.0047895 | 0.0012004 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2198-8_0_5_load_21 | 35 | 0.0027153 | 0.00068053 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2198-8_0_5_load_26 | 37 | 0.013325 | 0.0033396 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2198-8_0_5_load_59 | 40 | 0.015079 | 0.0037791 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2198-8_0_5_load_35 | 43 | 0.020298 | 0.0050871 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2198-8_0_5_load_77 | 44 | 0.01282 | 0.0032131 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2198-8_0_5_load_48 | 45 | 0.0030721 | 0.00076995 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2198-8_0_5_load_76 | 46 | 0.01013 | 0.0025389 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2198-8_0_5_load_75 | 47 | 0.010902 | 0.0027322 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2198-8_0_5_load_46 | 49 | 0.0082448 | 0.0020663 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2198-8_0_5_load_74 | 53 | 0.013842 | 0.0034692 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2198-8_0_5_load_54 | 54 | 0.042345 | 0.010613 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2198-8_0_5_load_69 | 55 | 0.014198 | 0.0035584 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2198-8_0_5_load_45 | 56 | 0.020347 | 0.0050994 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2198-8_0_5_load_73 | 57 | 0.013842 | 0.003469 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2198-8_0_5_load_41 | 58 | 0.036357 | 0.0091118 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2198-8_0_5_load_42 | 59 | 0.0022216 | 0.00055678 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2198-8_0_5_load_44 | 61 | 0.020702 | 0.0051883 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2198-8_0_5_load_50 | 63 | 0.016611 | 0.004163 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2198-8_0_5_load_47 | 64 | 0.0012695 | 0.00031818 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2198-8_0_5_load_49 | 65 | 0.0014621 | 0.00036643 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2198-8_0_5_load_63 | 66 | 0.0013112 | 0.00032862 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2198-8_0_5_load_64 | 67 | 0.014198 | 0.0035584 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2198-8_0_5_load_53 | 69 | 0.04643 | 0.011637 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2198-8_0_5_load_62 | 70 | 0.0028566 | 0.00071593 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2198-8_0_5_load_66 | 71 | 0.0053768 | 0.0013476 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 55 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2198-8_0_5_line_0 |  | 0 | 1 | 0.0040982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2198-8_0_5_line_1 |  | 0 | 2 | 0.017009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2198-8_0_5_line_2 |  | 1 | 3 | 0.032366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2198-8_0_5_line_3 |  | 3 | 4 | 0.027584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2198-8_0_5_line_4 |  | 4 | 5 | 0.30003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2198-8_0_5_line_5 |  | 5 | 6 | 0.016711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_2198-8_0_5_line_6 |  | 6 | 7 | 0.064632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_2198-8_0_5_line_7 |  | 7 | 45 | 0.034332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2198-8_0_5_line_8 |  | 7 | 30 | 0.15286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_2198-8_0_5_line_9 |  | 8 | 9 | 0.035629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_2198-8_0_5_line_10 |  | 8 | 10 | 0.07877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_2198-8_0_5_line_11 |  | 9 | 11 | 0.035905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_2198-8_0_5_line_12 |  | 10 | 12 | 0.042171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2198-8_0_5_line_13 |  | 10 | 13 | 0.025037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_2198-8_0_5_line_14 |  | 10 | 14 | 0.02359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2198-8_0_5_line_15 |  | 11 | 15 | 0.0075025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2198-8_0_5_line_16 |  | 11 | 16 | 0.014566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_2198-8_0_5_line_17 |  | 12 | 17 | 0.008675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2198-8_0_5_line_18 |  | 12 | 18 | 0.030732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2198-8_0_5_line_19 |  | 13 | 19 | 0.049934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_2198-8_0_5_line_20 |  | 14 | 20 | 0.034388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2198-8_0_5_line_21 |  | 16 | 21 | 0.026654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_2198-8_0_5_line_22 |  | 17 | 22 | 0.014762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2198-8_0_5_line_23 |  | 18 | 23 | 0.0066754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2198-8_0_5_line_24 |  | 19 | 24 | 0.014049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2198-8_0_5_line_25 |  | 19 | 25 | 0.010568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_2198-8_0_5_line_26 |  | 20 | 26 | 0.0003183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2198-8_0_5_line_27 |  | 21 | 57 | 0.022971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_2198-8_0_5_line_28 |  | 22 | 71 | 0.017223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2198-8_0_5_line_29 |  | 24 | 33 | 0.027643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2198-8_0_5_line_30 |  | 25 | 27 | 0.021744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_2198-8_0_5_line_31 |  | 26 | 36 | 0.04452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2198-8_0_5_line_32 |  | 27 | 28 | 0.0014878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_2198-8_0_5_line_33 |  | 28 | 29 | 0.026521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_2198-8_0_5_line_34 |  | 29 | 30 | 0.056872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_2198-8_0_5_line_35 |  | 30 | 31 | 0.040891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2198-8_0_5_line_36 |  | 30 | 32 | 0.050583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2198-8_0_5_line_37 |  | 31 | 38 | 0.018587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2198-8_0_5_line_38 |  | 32 | 44 | 0.007472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2198-8_0_5_line_39 |  | 33 | 34 | 0.011549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2198-8_0_5_line_40 |  | 34 | 35 | 0.023337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2198-8_0_5_line_41 |  | 36 | 37 | 0.0077445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2198-8_0_5_line_42 |  | 38 | 39 | 0.043197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2198-8_0_5_line_43 |  | 39 | 40 | 0.059174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2198-8_0_5_line_44 |  | 41 | 42 | 0.13493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2198-8_0_5_line_45 |  | 41 | 43 | 0.048248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2198-8_0_5_line_46 |  | 42 | 46 | 0.022276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2198-8_0_5_line_47 |  | 42 | 47 | 0.013191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2198-8_0_5_line_48 |  | 43 | 48 | 0.038287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2198-8_0_5_line_49 |  | 45 | 49 | 0.0072387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2198-8_0_5_line_50 |  | 48 | 50 | 0.26589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2198-8_0_5_line_51 |  | 48 | 51 | 0.22964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2198-8_0_5_line_52 |  | 49 | 64 | 0.018648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2198-8_0_5_line_53 |  | 50 | 52 | 0.037208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_2198-8_0_5_line_54 |  | 50 | 53 | 0.038203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_2198-8_0_5_line_55 |  | 51 | 54 | 0.055943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2198-8_0_5_line_56 |  | 52 | 55 | 0.011634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_2198-8_0_5_line_57 |  | 52 | 56 | 0.029598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_2198-8_0_5_line_58 |  | 53 | 57 | 0.020551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_2198-8_0_5_line_59 |  | 56 | 60 | 0.014772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2198-8_0_5_line_60 |  | 58 | 59 | 0.012889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2198-8_0_5_line_61 |  | 58 | 60 | 0.048806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2198-8_0_5_line_62 |  | 59 | 61 | 0.053359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2198-8_0_5_line_63 |  | 61 | 62 | 0.0046231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2198-8_0_5_line_64 |  | 62 | 63 | 0.039056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2198-8_0_5_line_65 |  | 63 | 68 | 0.024108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2198-8_0_5_line_66 |  | 64 | 65 | 0.0045342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2198-8_0_5_line_67 |  | 65 | 66 | 0.002797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2198-8_0_5_line_68 |  | 66 | 67 | 0.022871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2198-8_0_5_line_69 |  | 68 | 69 | 0.035306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2198-8_0_5_line_70 |  | 69 | 70 | 0.21122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2198-8_0_5_trafo_69 | 0.63 MVA 20/0.4 kV | 72 | 55 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2577544.4857 | 1185198.7418 | 2577541.8523 | 1185197.2191 | 2577541.0458 | 1185196.537
1 | 2577560.0066 | 1185205.0104 | 2577553.5617 | 1185203.9897 | 2577544.4857 | 1185198.7418
2 | 2577541.0458 | 1185196.537 | 2577530.9119 | 1185187.9665 | 2577517.5905 | 1185174.2874
3 | 2577498.0702 | 1185154.8285 | 2577500.7418 | 1185156.9862 | 2577517.5905 | 1185174.2874
4 | 2577498.0702 | 1185154.8285 | 2577487.9471 | 1185147.8075 | 2577467.4755 | 1185130.7202 | 2577407.6084 | 1185083.2662 | 2577368.5607 | 1185062.1587 | 2577333.4111 | 1185048.7073 | 2577284.0471 | 1185028.2399 | 2577236.8739 | 1185014.2875
5 | 2577236.8739 | 1185014.2875 | 2577235.8437 | 1185013.9828 | 2577221.1758 | 1185008.565
6 | 2577175.2599 | 1184965.4999 | 2577176.7374 | 1184968.6959 | 2577183.5138 | 1184978.4863 | 2577195.5586 | 1184992.9033 | 2577209.5989 | 1185004.289 | 2577221.1758 | 1185008.565
7 | 2577175.2599 | 1184965.4999 | 2577173.1933 | 1184975.9133 | 2577170.9787 | 1184985.5157 | 2577171.7893 | 1184999.3533
8 | 2577084.9365 | 1185035.0158 | 2577090.8068 | 1185011.5587 | 2577091.488 | 1185008.0987 | 2577091.9894 | 1185001.5378 | 2577091.3938 | 1184999.4613 | 2577093.9706 | 1184994.7822 | 2577097.2609 | 1184981.1069 | 2577100.6246 | 1184966.6976 | 2577101.3172 | 1184964.2158 | 2577106.7255 | 1184965.4847 | 2577108.5928 | 1184958.874 | 2577166.6699 | 1184966.4333 | 2577175.2599 | 1184965.4999
9 | 2577220.0811 | 1185242.0173 | 2577192.8861 | 1185218.9986
10 | 2577132.4985 | 1185168.5587 | 2577143.7077 | 1185176.0975 | 2577190.4932 | 1185216.9732 | 2577192.8861 | 1185218.9986
11 | 2577247.4866 | 1185265.2142 | 2577220.0811 | 1185242.0173
12 | 2577113.5488 | 1185206.2511 | 2577132.4985 | 1185168.5587
13 | 2577132.4985 | 1185168.5587 | 2577146.9296 | 1185148.0991
14 | 2577132.4985 | 1185168.5587 | 2577112.9338 | 1185155.3786
15 | 2577247.4866 | 1185265.2142 | 2577253.2231 | 1185270.0495
16 | 2577247.4866 | 1185265.2142 | 2577238.2268 | 1185276.4776
17 | 2577113.5488 | 1185206.2511 | 2577109.6483 | 1185214.0034
18 | 2577113.5488 | 1185206.2511 | 2577084.3853 | 1185196.5571
19 | 2577175.7109 | 1185107.2946 | 2577146.9296 | 1185148.0991
20 | 2577112.9338 | 1185155.3786 | 2577084.4135 | 1185136.1655
21 | 2577238.2268 | 1185276.4776 | 2577224.011 | 1185299.0241
22 | 2577109.6483 | 1185214.0034 | 2577122.7778 | 1185220.8233
23 | 2577084.3853 | 1185196.5571 | 2577078.0507 | 1185194.4514
24 | 2577175.7109 | 1185107.2946 | 2577187.0604 | 1185115.5743
25 | 2577175.7109 | 1185107.2946 | 2577167.1966 | 1185101.0343
26 | 2577084.1495 | 1185135.9876 | 2577084.4135 | 1185136.1655
27 | 2577224.011 | 1185299.0241 | 2577219.9305 | 1185305.496 | 2577232.9407 | 1185313.586
28 | 2577122.7778 | 1185220.8233 | 2577138.1385 | 1185228.6127
29 | 2577187.0604 | 1185115.5743 | 2577209.3924 | 1185131.8662
30 | 2577149.6779 | 1185088.1535 | 2577167.1966 | 1185101.0343
31 | 2577047.1547 | 1185111.223 | 2577051.3088 | 1185113.864 | 2577084.1495 | 1185135.9876
32 | 2577149.6779 | 1185088.1535 | 2577148.4793 | 1185087.2722
33 | 2577127.1125 | 1185071.562 | 2577148.4793 | 1185087.2722
34 | 2577127.1125 | 1185071.562 | 2577089.8866 | 1185044.1904 | 2577085.477 | 1185038.6489 | 2577084.9365 | 1185035.0158
35 | 2577084.9365 | 1185035.0158 | 2577075.0288 | 1185032.6192 | 2577060.4025 | 1185021.7253 | 2577063.2519 | 1185009.5958
36 | 2577084.9365 | 1185035.0158 | 2577090.8068 | 1185011.5587 | 2577096.8628 | 1185012.5805 | 2577098.467 | 1185007.0158 | 2577103.2258 | 1185008.1093 | 2577111.5096 | 1185012.9356
37 | 2577056.2631 | 1184997.1506 | 2577063.8959 | 1184999.3779 | 2577065.0055 | 1185002.1307 | 2577063.2519 | 1185009.5958
38 | 2577111.5096 | 1185012.9356 | 2577114.2303 | 1185019.8954
39 | 2577218.7226 | 1185138.6728 | 2577209.3924 | 1185131.8662
40 | 2577218.7226 | 1185138.6728 | 2577237.5756 | 1185152.4266
41 | 2577047.1547 | 1185111.223 | 2577051.1205 | 1185104.571
42 | 2577056.2631 | 1184997.1506 | 2577051.7035 | 1185016.1002 | 2577049.4935 | 1185026.8477 | 2577054.9392 | 1185027.9607 | 2577061.0743 | 1185031.6835
43 | 2577061.0743 | 1185031.6835 | 2577058.7661 | 1185032.804 | 2577056.9157 | 1185035.8572 | 2577057.9273 | 1185046.8702 | 2577057.1105 | 1185048.8077 | 2577054.0625 | 1185052.0099 | 2577053.0999 | 1185053.7256 | 2577053.7795 | 1185055.813 | 2577057.7974 | 1185058.7324 | 2577079.5334 | 1185073.5861
44 | 2576992.4994 | 1185424.5864 | 2577001.6927 | 1185410.11 | 2577002.3943 | 1185382.2594 | 2577010.0681 | 1185381.3961 | 2577061.5063 | 1185374.1944 | 2577065.2663 | 1185373.624 | 2577068.7803 | 1185372.5544 | 2577074.8835 | 1185370.0741 | 2577076.4792 | 1185372.258 | 2577078.645 | 1185373.8617 | 2577081.1821 | 1185374.7746 | 2577083.8842 | 1185374.9087 | 2577086.4992 | 1185374.2428 | 2577088.8061 | 1185372.8443
45 | 2577088.8061 | 1185372.8443 | 2577095.0775 | 1185380.3686 | 2577119.9351 | 1185404.8416 | 2577122.7333 | 1185407.059
46 | 2576992.4994 | 1185424.5864 | 2576979.9281 | 1185442.9759
47 | 2576992.4994 | 1185424.5864 | 2576998.2061 | 1185428.1329 | 2577003.3833 | 1185432.0173
48 | 2577154.6247 | 1185428.132 | 2577131.8303 | 1185414.2676 | 2577122.7333 | 1185407.059
49 | 2577172.2127 | 1185006.5797 | 2577171.7893 | 1184999.3533
50 | 2577154.6247 | 1185428.132 | 2577166.6076 | 1185434.5673 | 2577174.9554 | 1185438.3374 | 2577193.7711 | 1185445.5247 | 2577202.3077 | 1185448.7827 | 2577203.4131 | 1185446.4995 | 2577210.1897 | 1185432.5107 | 2577216.8973 | 1185418.4444 | 2577221.7804 | 1185408.2316 | 2577232.252 | 1185384.6126 | 2577231.9174 | 1185380.923 | 2577225.7833 | 1185377.3223 | 2577227.7679 | 1185371.4339 | 2577211.5683 | 1185355.921 | 2577212.2494 | 1185354.4176 | 2577235.4106 | 1185358.409 | 2577236.4544 | 1185355.9704 | 2577238.2925 | 1185353.6845 | 2577242.9544 | 1185355.4565 | 2577243.8943 | 1185353.7742 | 2577238.39 | 1185351.2495 | 2577246.3889 | 1185333.5542 | 2577278.5088 | 1185347.3834 | 2577281.2304 | 1185342.6373
51 | 2577154.6247 | 1185428.132 | 2577166.6076 | 1185434.5673 | 2577174.9554 | 1185438.3374 | 2577193.7711 | 1185445.5247 | 2577202.3077 | 1185448.7827 | 2577211.186 | 1185451.6058 | 2577219.5906 | 1185454.2862 | 2577237.4812 | 1185459.0427 | 2577243.8514 | 1185460.5525 | 2577261.7765 | 1185464.364 | 2577278.8137 | 1185467.4785 | 2577299.624 | 1185469.467 | 2577368.1469 | 1185476.0101 | 2577377.1391 | 1185476.6875
52 | 2577172.2127 | 1185006.5797 | 2577172.2933 | 1185007.9557 | 2577173.1505 | 1185018.558 | 2577176.8577 | 1185024.0578 | 2577176.8577 | 1185024.0578
53 | 2577300.164 | 1185310.5818 | 2577281.2304 | 1185342.6373
54 | 2577281.2304 | 1185342.6373 | 2577277.0536 | 1185340.0073 | 2577277.4513 | 1185336.2261 | 2577267.8063 | 1185330.5154 | 2577251.1966 | 1185322.9397
55 | 2577377.1391 | 1185476.6875 | 2577415.3443 | 1185479.5665 | 2577432.7642 | 1185482.2797
56 | 2577300.164 | 1185310.5818 | 2577291.5135 | 1185302.8023
57 | 2577300.164 | 1185310.5818 | 2577322.1692 | 1185330.3764
58 | 2577251.1966 | 1185322.9397 | 2577239.1386 | 1185317.44 | 2577232.9407 | 1185313.586
59 | 2577333.2518 | 1185340.1381 | 2577331.1391 | 1185338.4453 | 2577322.1692 | 1185330.3764
60 | 2577371.8403 | 1185369.8524 | 2577383.4856 | 1185375.3771 | 2577383.4856 | 1185375.3771
61 | 2577333.2518 | 1185340.1381 | 2577368.096 | 1185368.076 | 2577371.8403 | 1185369.8524
62 | 2577383.4856 | 1185375.3771 | 2577433.3219 | 1185394.4422
63 | 2577437.6398 | 1185396.094 | 2577433.3219 | 1185394.4422
64 | 2577437.6398 | 1185396.094 | 2577474.1189 | 1185410.0463
65 | 2577496.8537 | 1185416.9591 | 2577493.2457 | 1185417.3618 | 2577474.1189 | 1185410.0463
66 | 2577180.5849 | 1185026.6398 | 2577176.8577 | 1185024.0578
67 | 2577180.5849 | 1185026.6398 | 2577180.9592 | 1185026.8991 | 2577183.1703 | 1185027.6701
68 | 2577203.3172 | 1185038.0417 | 2577193.6678 | 1185031.3306 | 2577183.1703 | 1185027.6701
69 | 2577496.8537 | 1185416.9591 | 2577500.5687 | 1185416.556 | 2577530.0218 | 1185427.9195
70 | 2577675.9045 | 1185508.012 | 2577685.3159 | 1185500.4283 | 2577690.8955 | 1185494.6155 | 2577694.796 | 1185484.6735 | 2577695.3986 | 1185478.4792 | 2577692.6821 | 1185474.4539 | 2577650.5343 | 1185462.1051 | 2577599.7714 | 1185447.9214 | 2577568.0054 | 1185440.6036 | 2577548.5936 | 1185435.0848 | 2577530.0218 | 1185427.9195

## bus_geodata
| x | y | coords
0 | 2577544.4857 | 1185198.7418
1 | 2577541.0458 | 1185196.537
2 | 2577560.0066 | 1185205.0104
3 | 2577517.5905 | 1185174.2874
4 | 2577498.0702 | 1185154.8285
5 | 2577236.8739 | 1185014.2875
6 | 2577221.1758 | 1185008.565
7 | 2577175.2599 | 1184965.4999
8 | 2577192.8861 | 1185218.9986
9 | 2577220.0811 | 1185242.0173
10 | 2577132.4985 | 1185168.5587
11 | 2577247.4866 | 1185265.2142
12 | 2577113.5488 | 1185206.2511
13 | 2577146.9296 | 1185148.0991
14 | 2577112.9338 | 1185155.3786
15 | 2577253.2231 | 1185270.0495
16 | 2577238.2268 | 1185276.4776
17 | 2577109.6483 | 1185214.0034
18 | 2577084.3853 | 1185196.5571
19 | 2577175.7109 | 1185107.2946
20 | 2577084.4135 | 1185136.1655
21 | 2577224.011 | 1185299.0241
22 | 2577122.7778 | 1185220.8233
23 | 2577078.0507 | 1185194.4514
24 | 2577187.0604 | 1185115.5743
25 | 2577167.1966 | 1185101.0343
26 | 2577084.1495 | 1185135.9876
27 | 2577149.6779 | 1185088.1535
28 | 2577148.4793 | 1185087.2722
29 | 2577127.1125 | 1185071.562
30 | 2577084.9365 | 1185035.0158
31 | 2577063.2519 | 1185009.5958
32 | 2577111.5096 | 1185012.9356
33 | 2577209.3924 | 1185131.8662
34 | 2577218.7226 | 1185138.6728
35 | 2577237.5756 | 1185152.4266
36 | 2577047.1547 | 1185111.223
37 | 2577051.1205 | 1185104.571
38 | 2577056.2631 | 1184997.1506
39 | 2577061.0743 | 1185031.6835
40 | 2577079.5334 | 1185073.5861
41 | 2577088.8061 | 1185372.8443
42 | 2576992.4994 | 1185424.5864
43 | 2577122.7333 | 1185407.059
44 | 2577114.2303 | 1185019.8954
45 | 2577171.7893 | 1184999.3533
46 | 2576979.9281 | 1185442.9759
47 | 2577003.3833 | 1185432.0173
48 | 2577154.6247 | 1185428.132
49 | 2577172.2127 | 1185006.5797
50 | 2577281.2304 | 1185342.6373
51 | 2577377.1391 | 1185476.6875
52 | 2577300.164 | 1185310.5818
53 | 2577251.1966 | 1185322.9397
54 | 2577432.7642 | 1185482.2797
55 | 2577291.5135 | 1185302.8023
56 | 2577322.1692 | 1185330.3764
57 | 2577232.9407 | 1185313.586
58 | 2577371.8403 | 1185369.8524
59 | 2577383.4856 | 1185375.3771
60 | 2577333.2518 | 1185340.1381
61 | 2577433.3219 | 1185394.4422
62 | 2577437.6398 | 1185396.094
63 | 2577474.1189 | 1185410.0463
64 | 2577176.8577 | 1185024.0578
65 | 2577180.5849 | 1185026.6398
66 | 2577183.1703 | 1185027.6701
67 | 2577203.3172 | 1185038.0417
68 | 2577496.8537 | 1185416.9591
69 | 2577530.0218 | 1185427.9195
70 | 2577675.9045 | 1185508.012
71 | 2577138.1385 | 1185228.6127
72 | 2577300.164 | 1185310.5818

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97103 | -0.56024 | 0.0048159 | 0.001207
1 | 0.97116 | -0.55755 | 0.0070041 | 0.0017554
2 | 0.97054 | -0.5699 | 0.030698 | 0.0076936
3 | 0.97245 | -0.53216 | 0.0021547 | 0.00054001
4 | 0.9736 | -0.50947 | 0 | 0
5 | 0.97673 | -0.44803 | 0.0053858 | 0.0013498
6 | 0.97689 | -0.44497 | 0.0064021 | 0.0016045
7 | 0.97757 | -0.43163 | 0 | 0
8 | 0.9876 | -0.23663 | 0.0047912 | 0.0012008
9 | 0.98892 | -0.21127 | 0.0068142 | 0.0017078
10 | 0.98476 | -0.29156 | 0 | 0
11 | 0.99029 | -0.18492 | 0 | 0
12 | 0.98431 | -0.30034 | 0 | 0
13 | 0.98403 | -0.30568 | 0.011051 | 0.0027697
14 | 0.98419 | -0.30265 | 0.0092321 | 0.0023138
15 | 0.99019 | -0.18678 | 0.013954 | 0.0034971
16 | 0.99088 | -0.17353 | 0 | 0
17 | 0.98427 | -0.30118 | 0 | 0
18 | 0.98413 | -0.30378 | 0.0011858 | 0.00029718
19 | 0.98268 | -0.33192 | 0 | 0
20 | 0.98365 | -0.31312 | 0.0021493 | 0.00053867
21 | 0.99197 | -0.15272 | 0.04778 | 0.011975
22 | 0.98419 | -0.30261 | 0 | 0
23 | 0.9841 | -0.30438 | 0.0050229 | 0.0012589
24 | 0.98251 | -0.33525 | 0.0038237 | 0.00095832
25 | 0.98242 | -0.33698 | 0.0021825 | 0.00054698
26 | 0.98365 | -0.31321 | 0.0014406 | 0.00036106
27 | 0.98189 | -0.34723 | 0.0096361 | 0.002415
28 | 0.98186 | -0.34788 | 0.0020253 | 0.0005076
29 | 0.98127 | -0.35927 | 0 | 0
30 | 0.98002 | -0.38375 | 0 | 0
31 | 0.97927 | -0.39848 | 0.004747 | 0.0011897
32 | 0.97942 | -0.39553 | 0 | 0
33 | 0.98227 | -0.3399 | 0.0018038 | 0.00045206
34 | 0.98219 | -0.34146 | 0.0047895 | 0.0012004
35 | 0.98213 | -0.34261 | 0.0027153 | 0.00068053
36 | 0.9831 | -0.3239 | 0 | 0
37 | 0.98301 | -0.32576 | 0.013325 | 0.0033396
38 | 0.97901 | -0.40358 | 0 | 0
39 | 0.9784 | -0.41543 | 0 | 0
40 | 0.97757 | -0.43169 | 0.015079 | 0.0037791
41 | 0.98354 | -0.31489 | 0 | 0
42 | 0.98092 | -0.36617 | 0 | 0
43 | 0.98448 | -0.29662 | 0.020298 | 0.0050871
44 | 0.97933 | -0.39727 | 0.01282 | 0.0032131
45 | 0.97662 | -0.45016 | 0.0030721 | 0.00076995
46 | 0.98071 | -0.37026 | 0.01013 | 0.0025389
47 | 0.98079 | -0.36878 | 0.010902 | 0.0027322
48 | 0.98594 | -0.2682 | 0 | 0
49 | 0.97645 | -0.45367 | 0.0082448 | 0.0020663
50 | 0.99626 | -0.070752 | 0 | 0
51 | 0.97689 | -0.44419 | 0 | 0
52 | 0.99887 | -0.02131 | 0 | 0
53 | 0.99418 | -0.1105 | 0.013842 | 0.0034692
54 | 0.97469 | -0.48756 | 0.042345 | 0.010613
55 | 1 | 0 | -0.53473 | -0.1368
56 | 0.99689 | -0.059011 | 0.020347 | 0.0050994
57 | 0.99311 | -0.13094 | 0.013842 | 0.003469
58 | 0.98954 | -0.19964 | 0.036357 | 0.0091118
59 | 0.98848 | -0.22004 | 0.0022216 | 0.00055678
60 | 0.99518 | -0.091501 | 0 | 0
61 | 0.98421 | -0.30284 | 0.020702 | 0.0051883
62 | 0.98393 | -0.30832 | 0 | 0
63 | 0.98154 | -0.35478 | 0.016611 | 0.004163
64 | 0.97613 | -0.45989 | 0.0012695 | 0.00031818
65 | 0.97606 | -0.46129 | 0.0014621 | 0.00036643
66 | 0.97602 | -0.46209 | 0.0013112 | 0.00032862
67 | 0.97572 | -0.46803 | 0.014198 | 0.0035584
68 | 0.98044 | -0.3763 | 0 | 0
69 | 0.97883 | -0.40791 | 0.04643 | 0.011637
70 | 0.97827 | -0.41891 | 0.0028566 | 0.00071593
71 | 0.98411 | -0.30428 | 0.0053768 | 0.0013476
72 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.035528 | -0.0089094 | 0.035532 | 0.0089123 | 4.5556e-06 | 2.8649e-06 | 0.054445 | 0.054445 | 0.054445 | 0.97103 | -0.56024 | 0.97116 | -0.55755 | 14.9575
1 | 0.030712 | 0.0077024 | -0.030698 | -0.0076936 | 1.4129e-05 | 8.8324e-06 | 0.047065 | 0.047065 | 0.047065 | 0.97103 | -0.56024 | 0.97054 | -0.5699 | 12.93
2 | -0.042536 | -0.010668 | 0.042588 | 0.0107 | 5.1559e-05 | 3.2597e-05 | 0.065177 | 0.065177 | 0.065177 | 0.97116 | -0.55755 | 0.97245 | -0.53216 | 17.9058
3 | -0.044743 | -0.01124 | 0.044791 | 0.011271 | 4.8499e-05 | 3.0697e-05 | 0.068474 | 0.068474 | 0.068474 | 0.97245 | -0.53216 | 0.9736 | -0.50947 | 18.8115
4 | -0.044791 | -0.011271 | 0.044923 | 0.01134 | 0.00013187 | 6.9426e-05 | 0.068474 | 0.068468 | 0.068474 | 0.9736 | -0.50947 | 0.97673 | -0.44803 | 4.7029
5 | -0.050309 | -0.01269 | 0.050316 | 0.012694 | 7.3679e-06 | 3.6696e-06 | 0.076673 | 0.076673 | 0.076673 | 0.97673 | -0.44803 | 0.97689 | -0.44497 | 4.2128
6 | -0.056718 | -0.014298 | 0.056755 | 0.014318 | 3.6206e-05 | 1.9123e-05 | 0.086425 | 0.086423 | 0.086425 | 0.97689 | -0.44497 | 0.97757 | -0.43163 | 4.7486
7 | 0.0296 | 0.0074335 | -0.029573 | -0.0074172 | 2.6142e-05 | 1.6301e-05 | 0.045061 | 0.045061 | 0.045061 | 0.97757 | -0.43163 | 0.97662 | -0.45016 | 12.3794
8 | -0.086354 | -0.021751 | 0.086552 | 0.021868 | 0.00019819 | 0.00011724 | 0.13148 | 0.13148 | 0.13148 | 0.97757 | -0.43163 | 0.98002 | -0.38375 | 7.2244
9 | -0.20095 | -0.050984 | 0.2012 | 0.051139 | 0.00024532 | 0.00015472 | 0.303 | 0.303 | 0.303 | 0.9876 | -0.23663 | 0.98892 | -0.21127 | 16.6481
10 | 0.19616 | 0.049783 | -0.19564 | -0.049457 | 0.00051684 | 0.00032575 | 0.29578 | 0.29578 | 0.29578 | 0.9876 | -0.23663 | 0.98476 | -0.29156 | 16.2516
11 | -0.20801 | -0.052846 | 0.20828 | 0.053013 | 0.00026424 | 0.0001668 | 0.31325 | 0.31325 | 0.31325 | 0.98892 | -0.21127 | 0.99029 | -0.18492 | 17.2115
12 | 0.011593 | 0.0029066 | -0.011588 | -0.002904 | 4.8527e-06 | 2.5695e-06 | 0.017517 | 0.017518 | 0.017518 | 0.98476 | -0.29156 | 0.98431 | -0.30034 | 4.8125
13 | 0.15787 | 0.03998 | -0.15777 | -0.039913 | 0.00010699 | 6.6885e-05 | 0.2387 | 0.2387 | 0.2387 | 0.98476 | -0.29156 | 0.98403 | -0.30568 | 13.1156
14 | 0.026177 | 0.0065711 | -0.026164 | -0.0065625 | 1.3844e-05 | 8.56e-06 | 0.039559 | 0.039559 | 0.039559 | 0.98476 | -0.29156 | 0.98419 | -0.30265 | 10.8679
15 | 0.013955 | 0.0034978 | -0.013954 | -0.0034971 | 1.2371e-06 | 6.952e-07 | 0.020969 | 0.020969 | 0.020969 | 0.99029 | -0.18492 | 0.99019 | -0.18678 | 5.7607
16 | -0.22223 | -0.056511 | 0.22235 | 0.056588 | 0.00012203 | 7.716e-05 | 0.33422 | 0.33422 | 0.33422 | 0.99029 | -0.18492 | 0.99088 | -0.17353 | 18.3636
17 | 0.0053778 | 0.0013477 | -0.0053776 | -0.0013477 | 2.1501e-07 | 2.7347e-08 | 0.0081298 | 0.0081299 | 0.0081299 | 0.98431 | -0.30034 | 0.98427 | -0.30118 | 2.2335
18 | 0.0062099 | 0.0015563 | -0.0062089 | -0.0015561 | 1.0157e-06 | 2.5946e-07 | 0.0093877 | 0.0093878 | 0.0093878 | 0.98431 | -0.30034 | 0.98413 | -0.30378 | 2.5791
19 | 0.14672 | 0.037143 | -0.14653 | -0.037028 | 0.00018456 | 0.00011495 | 0.22199 | 0.22199 | 0.22199 | 0.98403 | -0.30568 | 0.98268 | -0.33192 | 12.1974
20 | 0.016932 | 0.0042488 | -0.016923 | -0.0042438 | 8.452e-06 | 4.9725e-06 | 0.025601 | 0.025601 | 0.025601 | 0.98419 | -0.30265 | 0.98365 | -0.31312 | 7.0333
21 | -0.22235 | -0.056588 | 0.22258 | 0.056729 | 0.00022329 | 0.00014119 | 0.33422 | 0.33422 | 0.33422 | 0.99088 | -0.17353 | 0.99197 | -0.15272 | 18.3635
22 | 0.0053776 | 0.0013477 | -0.0053773 | -0.0013476 | 3.6589e-07 | 4.6561e-08 | 0.0081299 | 0.0081299 | 0.0081299 | 0.98427 | -0.30118 | 0.98419 | -0.30261 | 2.2335
23 | 0.0050231 | 0.0012589 | -0.0050229 | -0.0012589 | 1.444e-07 | 7.5972e-09 | 0.0075949 | 0.007595 | 0.007595 | 0.98413 | -0.30378 | 0.9841 | -0.30438 | 2.0865
24 | 0.013137 | 0.0032934 | -0.013135 | -0.0032922 | 2.0849e-06 | 1.1564e-06 | 0.019893 | 0.019893 | 0.019893 | 0.98268 | -0.33192 | 0.98251 | -0.33525 | 5.4652
25 | 0.13339 | 0.033735 | -0.13336 | -0.033715 | 3.2374e-05 | 2.005e-05 | 0.2021 | 0.2021 | 0.2021 | 0.98268 | -0.33192 | 0.98242 | -0.33698 | 11.1044
26 | 0.014774 | 0.0037051 | -0.014774 | -0.0037051 | 5.9622e-08 | 3.4118e-08 | 0.02235 | 0.02235 | 0.02235 | 0.98365 | -0.31312 | 0.98365 | -0.31321 | 6.1401
27 | -0.27036 | -0.068704 | 0.27064 | 0.068884 | 0.00028383 | 0.00018017 | 0.40589 | 0.40589 | 0.40589 | 0.99197 | -0.15272 | 0.99311 | -0.13094 | 22.3015
28 | 0.0053773 | 0.0013476 | -0.0053768 | -0.0013476 | 4.2689e-07 | 5.4363e-08 | 0.0081299 | 0.00813 | 0.00813 | 0.98419 | -0.30261 | 0.98411 | -0.30428 | 2.2335
29 | 0.0093113 | 0.0023339 | -0.0093093 | -0.002333 | 2.0616e-06 | 9.694e-07 | 0.014102 | 0.014102 | 0.014102 | 0.98251 | -0.33525 | 0.98227 | -0.3399 | 3.8743
30 | 0.13118 | 0.033168 | -0.13111 | -0.033128 | 6.4449e-05 | 3.9872e-05 | 0.19879 | 0.1988 | 0.1988 | 0.98242 | -0.33698 | 0.98189 | -0.34723 | 10.9228
31 | 0.013333 | 0.003344 | -0.013326 | -0.0033402 | 6.7924e-06 | 3.7823e-06 | 0.02017 | 0.020171 | 0.020171 | 0.98365 | -0.31321 | 0.9831 | -0.3239 | 5.5414
32 | 0.12148 | 0.030713 | -0.12148 | -0.03071 | 3.7857e-06 | 2.3288e-06 | 0.18419 | 0.18419 | 0.18419 | 0.98189 | -0.34723 | 0.98186 | -0.34788 | 10.1204
33 | 0.11945 | 0.030203 | -0.11938 | -0.030163 | 6.5252e-05 | 4.0085e-05 | 0.18112 | 0.18112 | 0.18112 | 0.98186 | -0.34788 | 0.98127 | -0.35927 | 9.9518
34 | 0.11938 | 0.030163 | -0.11924 | -0.030077 | 0.00013993 | 8.5968e-05 | 0.18112 | 0.18112 | 0.18112 | 0.98127 | -0.35927 | 0.98002 | -0.38375 | 9.9519
35 | 0.019863 | 0.004991 | -0.01985 | -0.0049825 | 1.3952e-05 | 8.4146e-06 | 0.030164 | 0.030165 | 0.030165 | 0.98002 | -0.38375 | 0.97927 | -0.39848 | 8.287
36 | 0.012829 | 0.0032176 | -0.012821 | -0.0032137 | 7.1977e-06 | 3.9695e-06 | 0.019479 | 0.01948 | 0.01948 | 0.98002 | -0.38375 | 0.97942 | -0.39553 | 5.3515
37 | 0.015103 | 0.0037928 | -0.015099 | -0.0037907 | 3.6717e-06 | 2.1161e-06 | 0.022951 | 0.022951 | 0.022951 | 0.97927 | -0.39848 | 0.97901 | -0.40358 | 6.3054
38 | 0.012821 | 0.0032137 | -0.01282 | -0.0032131 | 1.0632e-06 | 5.8644e-07 | 0.01948 | 0.01948 | 0.01948 | 0.97942 | -0.39553 | 0.97933 | -0.39727 | 5.3515
39 | 0.0075055 | 0.0018809 | -0.007505 | -0.0018807 | 5.5988e-07 | 2.1214e-07 | 0.01137 | 0.01137 | 0.01137 | 0.98227 | -0.3399 | 0.98219 | -0.34146 | 3.1236
40 | 0.0027155 | 0.00068033 | -0.0027153 | -0.00068053 | 1.4811e-07 | -2.0055e-07 | 0.0041139 | 0.004114 | 0.004114 | 0.98219 | -0.34146 | 0.98213 | -0.34261 | 1.1302
41 | 0.013326 | 0.0033402 | -0.013325 | -0.0033396 | 1.1816e-06 | 6.5803e-07 | 0.020171 | 0.020171 | 0.020171 | 0.9831 | -0.3239 | 0.98301 | -0.32576 | 5.5414
42 | 0.015099 | 0.0037907 | -0.01509 | -0.0037858 | 8.5332e-06 | 4.9184e-06 | 0.022951 | 0.022952 | 0.022952 | 0.97901 | -0.40358 | 0.9784 | -0.41543 | 6.3054
43 | 0.01509 | 0.0037858 | -0.015079 | -0.0037791 | 1.169e-05 | 6.7388e-06 | 0.022952 | 0.022952 | 0.022952 | 0.9784 | -0.41543 | 0.97757 | -0.43169 | 6.3055
44 | 0.021087 | 0.0053041 | -0.021035 | -0.0052728 | 5.1522e-05 | 3.1266e-05 | 0.031909 | 0.03191 | 0.03191 | 0.98354 | -0.31489 | 0.98092 | -0.36617 | 8.7665
45 | -0.021087 | -0.0053041 | 0.021105 | 0.0053152 | 1.8422e-05 | 1.1177e-05 | 0.031909 | 0.031909 | 0.031909 | 0.98354 | -0.31489 | 0.98448 | -0.29662 | 8.7663
46 | 0.010132 | 0.0025399 | -0.01013 | -0.0025389 | 1.9735e-06 | 9.8191e-07 | 0.01537 | 0.015371 | 0.015371 | 0.98092 | -0.36617 | 0.98071 | -0.37026 | 4.2227
47 | 0.010903 | 0.0027329 | -0.010902 | -0.0027322 | 1.3532e-06 | 6.9957e-07 | 0.01654 | 0.01654 | 0.01654 | 0.98092 | -0.36617 | 0.98079 | -0.36878 | 4.5439
48 | -0.041403 | -0.010402 | 0.041459 | 0.010438 | 5.6243e-05 | 3.5508e-05 | 0.062589 | 0.062589 | 0.062589 | 0.98448 | -0.29662 | 0.98594 | -0.2682 | 17.1947
49 | 0.026501 | 0.0066472 | -0.026497 | -0.0066445 | 4.4262e-06 | 2.7422e-06 | 0.04038 | 0.04038 | 0.04038 | 0.97662 | -0.45016 | 0.97645 | -0.45367 | 11.0935
50 | -0.084252 | -0.021333 | 0.085059 | 0.021843 | 0.00080704 | 0.00050965 | 0.12723 | 0.12723 | 0.12723 | 0.98594 | -0.2682 | 0.99626 | -0.070752 | 17.4771
51 | 0.042792 | 0.010895 | -0.042432 | -0.010668 | 0.00035987 | 0.00022742 | 0.064645 | 0.064646 | 0.064646 | 0.98594 | -0.2682 | 0.97689 | -0.44419 | 17.7598
52 | 0.018252 | 0.0045781 | -0.018247 | -0.0045749 | 5.4106e-06 | 3.2296e-06 | 0.027816 | 0.027816 | 0.027816 | 0.97645 | -0.45367 | 0.97613 | -0.45989 | 7.6418
53 | -0.38424 | -0.098208 | 0.38516 | 0.098795 | 0.00092127 | 0.00058719 | 0.57457 | 0.57457 | 0.57457 | 0.99626 | -0.070752 | 0.99887 | -0.02131 | 31.57
54 | 0.29918 | 0.076365 | -0.2986 | -0.076001 | 0.00057337 | 0.00036448 | 0.44734 | 0.44734 | 0.44734 | 0.99626 | -0.070752 | 0.99418 | -0.1105 | 24.5794
55 | 0.042432 | 0.010668 | -0.042345 | -0.010613 | 8.7672e-05 | 5.5411e-05 | 0.064646 | 0.064646 | 0.064646 | 0.97689 | -0.44419 | 0.97469 | -0.48756 | 17.7598
56 | -0.53253 | -0.13644 | 0.53308 | 0.1368 | 0.00055059 | 0.00035162 | 0.79437 | 0.79437 | 0.79437 | 0.99887 | -0.02131 | 1 | 0 | 43.6465
57 | 0.14737 | 0.037648 | -0.1471 | -0.037477 | 0.0002681 | 0.00017081 | 0.21979 | 0.21979 | 0.21979 | 0.99887 | -0.02131 | 0.99689 | -0.059011 | 30.1913
58 | 0.28476 | 0.072532 | -0.28448 | -0.072353 | 0.00028054 | 0.00017822 | 0.42663 | 0.42663 | 0.42663 | 0.99418 | -0.1105 | 0.99311 | -0.13094 | 23.441
59 | 0.12676 | 0.032378 | -0.12656 | -0.032251 | 0.00019877 | 0.00012702 | 0.18942 | 0.18942 | 0.18942 | 0.99689 | -0.059011 | 0.99518 | -0.091501 | 52.039
60 | 0.089545 | 0.022719 | -0.089457 | -0.022663 | 8.7767e-05 | 5.6005e-05 | 0.13475 | 0.13475 | 0.13475 | 0.98954 | -0.19964 | 0.98848 | -0.22004 | 37.0196
61 | -0.1259 | -0.031831 | 0.12656 | 0.032251 | 0.00065669 | 0.00041965 | 0.18942 | 0.18942 | 0.18942 | 0.98954 | -0.19964 | 0.99518 | -0.091501 | 52.0391
62 | 0.087236 | 0.022106 | -0.08689 | -0.021886 | 0.00034552 | 0.00022045 | 0.13141 | 0.13141 | 0.13141 | 0.98848 | -0.22004 | 0.98421 | -0.30284 | 36.1009
63 | 0.066188 | 0.016698 | -0.066171 | -0.016687 | 1.7374e-05 | 1.1061e-05 | 0.10011 | 0.10011 | 0.10011 | 0.98421 | -0.30284 | 0.98393 | -0.30832 | 27.5024
64 | 0.066171 | 0.016687 | -0.066024 | -0.016593 | 0.00014678 | 9.3444e-05 | 0.10011 | 0.10011 | 0.10011 | 0.98393 | -0.30832 | 0.98154 | -0.35478 | 27.5024
65 | 0.049414 | 0.01243 | -0.049363 | -0.012398 | 5.0755e-05 | 3.2179e-05 | 0.074927 | 0.074927 | 0.074927 | 0.98154 | -0.35478 | 0.98044 | -0.3763 | 20.5844
66 | 0.016977 | 0.0042567 | -0.016976 | -0.0042561 | 1.1389e-06 | 6.7222e-07 | 0.025881 | 0.025881 | 0.025881 | 0.97613 | -0.45989 | 0.97606 | -0.46129 | 7.1101
67 | 0.015514 | 0.0038896 | -0.015513 | -0.0038893 | 5.8675e-07 | 3.4056e-07 | 0.023652 | 0.023652 | 0.023652 | 0.97606 | -0.46129 | 0.97602 | -0.46209 | 6.4977
68 | 0.014202 | 0.0035607 | -0.014198 | -0.0035584 | 4.0211e-06 | 2.2878e-06 | 0.021653 | 0.021653 | 0.021653 | 0.97602 | -0.46209 | 0.97572 | -0.46803 | 5.9486
69 | 0.049363 | 0.012398 | -0.049289 | -0.012351 | 7.433e-05 | 4.7126e-05 | 0.074927 | 0.074928 | 0.074928 | 0.98044 | -0.3763 | 0.97883 | -0.40791 | 20.5845
70 | 0.0028581 | 0.00071423 | -0.0028566 | -0.00071593 | 1.495e-06 | -1.6966e-06 | 0.0043441 | 0.0043451 | 0.0043451 | 0.97883 | -0.40791 | 0.97827 | -0.41891 | 1.1937

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54893 | 0.14035

## res_load
| p_mw | q_mvar
0 | 0.0048159 | 0.001207
1 | 0.0070041 | 0.0017554
2 | 0.030698 | 0.0076936
3 | 0.0021547 | 0.00054001
4 | 0.0053858 | 0.0013498
5 | 0.0064021 | 0.0016045
6 | 0.0047912 | 0.0012008
7 | 0.0068142 | 0.0017078
8 | 0.011051 | 0.0027697
9 | 0.0092321 | 0.0023138
10 | 0.013954 | 0.0034971
11 | 0.0011858 | 0.00029718
12 | 0.0021493 | 0.00053867
13 | 0.04778 | 0.011975
14 | 0.0050229 | 0.0012589
15 | 0.0038237 | 0.00095832
16 | 0.0021825 | 0.00054698
17 | 0.0014406 | 0.00036106
18 | 0.0096361 | 0.002415
19 | 0.0020253 | 0.0005076
20 | 0.004747 | 0.0011897
21 | 0.0018038 | 0.00045206
22 | 0.0047895 | 0.0012004
23 | 0.0027153 | 0.00068053
24 | 0.013325 | 0.0033396
25 | 0.015079 | 0.0037791
26 | 0.020298 | 0.0050871
27 | 0.01282 | 0.0032131
28 | 0.0030721 | 0.00076995
29 | 0.01013 | 0.0025389
30 | 0.010902 | 0.0027322
31 | 0.0082448 | 0.0020663
32 | 0.013842 | 0.0034692
33 | 0.042345 | 0.010613
34 | 0.014198 | 0.0035584
35 | 0.020347 | 0.0050994
36 | 0.013842 | 0.003469
37 | 0.036357 | 0.0091118
38 | 0.0022216 | 0.00055678
39 | 0.020702 | 0.0051883
40 | 0.016611 | 0.004163
41 | 0.0012695 | 0.00031818
42 | 0.0014621 | 0.00036643
43 | 0.0013112 | 0.00032862
44 | 0.014198 | 0.0035584
45 | 0.04643 | 0.011637
46 | 0.0028566 | 0.00071593
47 | 0.0053768 | 0.0013476

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1