## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2228-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2228-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2228-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2228-13_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2228-13_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2228-13_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2228-13_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_2228-13_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_2228-13_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_2228-13_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_2228-13_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2228-13_0_4_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_2228-13_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_2228-13_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2228-13_0_4_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_2228-13_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2228-13_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_2228-13_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_2228-13_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_MV_505_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2228-13_0_4_load_0 | 0 | 0.0052625 | 0.0013189 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2228-13_0_4_load_22 | 6 | 0.05586 | 0.014 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2228-13_0_4_load_19 | 9 | 0.071095 | 0.017818 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2228-13_0_4_load_21 | 11 | 0.070777 | 0.017738 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2228-13_0_4_load_14 | 12 | 0.073939 | 0.018531 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2228-13_0_4_load_15 | 15 | 0.0013547 | 0.00033951 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2228-13_0_4_load_18 | 16 | 0.024704 | 0.0061913 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2228-13_0_4_load_20 | 17 | 0.040449 | 0.010137 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2228-13_0_4_load_16 | 18 | 0.040116 | 0.010054 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2228-13_0_4_line_0 |  | 0 | 1 | 0.07094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2228-13_0_4_line_1 |  | 0 | 2 | 0.031572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2228-13_0_4_line_2 |  | 1 | 3 | 0.065388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2228-13_0_4_line_3 |  | 1 | 4 | 0.11177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2228-13_0_4_line_4 |  | 2 | 5 | 0.065903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2228-13_0_4_line_5 |  | 3 | 6 | 0.00918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2228-13_0_4_line_6 |  | 3 | 7 | 0.039998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2228-13_0_4_line_7 |  | 4 | 8 | 0.028839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2228-13_0_4_line_8 |  | 4 | 9 | 0.017378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2228-13_0_4_line_9 |  | 5 | 12 | 0.054983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2228-13_0_4_line_10 |  | 5 | 10 | 0.11864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2228-13_0_4_line_11 |  | 7 | 16 | 0.0049701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2228-13_0_4_line_12 |  | 8 | 17 | 0.032034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2228-13_0_4_line_13 |  | 10 | 11 | 0.018119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2228-13_0_4_line_14 |  | 11 | 14 | 0.0050623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2228-13_0_4_line_15 |  | 13 | 14 | 0.13239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2228-13_0_4_line_16 |  | 13 | 15 | 0.029833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2228-13_0_4_line_17 |  | 15 | 18 | 0.0074512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2228-13_0_4_trafo_14 | 0.63 MVA 20/0.4 kV | 19 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2575669.7039 | 1183008.1355 | 2575689.201 | 1183009.7124 | 2575708.3817 | 1183014.2256 | 2575709.9406 | 1183014.5972 | 2575723.0571 | 1183020.3691 | 2575738.5224 | 1183023.3059
1 | 2575769.5405 | 1183029.196 | 2575738.5224 | 1183023.3059
2 | 2575669.7039 | 1183008.1355 | 2575668.8871 | 1183011.8963 | 2575667.4517 | 1183017.4829 | 2575665.8343 | 1183025.2379 | 2575672.4064 | 1183030.5695 | 2575670.0325 | 1183034.4256 | 2575666.6926 | 1183046.6234 | 2575670.69 | 1183047.7521 | 2575669.2646 | 1183053.9278 | 2575669.5338 | 1183060.0299 | 2575670.6239 | 1183061.504 | 2575674.2921 | 1183062.4117
3 | 2575620.8006 | 1183094.7468 | 2575622.7633 | 1183089.3026 | 2575629.9348 | 1183069.4519 | 2575633.113 | 1183060.6676 | 2575638.3502 | 1183051.3303 | 2575651.6207 | 1183040.5928 | 2575647.7035 | 1183034.7835 | 2575649.1213 | 1183032.3765 | 2575650.5314 | 1183029.9695 | 2575652.5894 | 1183027.2819 | 2575653.8955 | 1183025.5757 | 2575655.679 | 1183024.8347 | 2575658.963 | 1183025.1326 | 2575665.8343 | 1183025.2379 | 2575667.4517 | 1183017.4829 | 2575668.8871 | 1183011.8963 | 2575669.7039 | 1183008.1355
4 | 2575769.5405 | 1183029.196 | 2575778.1358 | 1183030.8287 | 2575776.9728 | 1183035.8471 | 2575775.0474 | 1183042.992 | 2575774.2392 | 1183047.0085 | 2575788.347 | 1183050.6643 | 2575786.413 | 1183057.5646 | 2575785.5369 | 1183061.7815 | 2575780.6231 | 1183060.5674 | 2575778.3775 | 1183069.6924
5 | 2575674.2921 | 1183062.4117 | 2575683.2707 | 1183064.4429
6 | 2575674.2921 | 1183062.4117 | 2575670.6239 | 1183061.504 | 2575669.5338 | 1183060.0299 | 2575669.2646 | 1183053.9278 | 2575670.69 | 1183047.7521 | 2575673.2407 | 1183036.736 | 2575679.2043 | 1183033.2654 | 2575680.2434 | 1183033.4613 | 2575682.1976 | 1183035.2876
7 | 2575611.635 | 1183121.676 | 2575611.0627 | 1183119.8663 | 2575620.8006 | 1183094.7468
8 | 2575620.8006 | 1183094.7468 | 2575623.4843 | 1183095.7252 | 2575637.1656 | 1183100.593
9 | 2575778.3775 | 1183069.6924 | 2575771.9934 | 1183095.5874 | 2575764.3963 | 1183100.9766 | 2575745.9545 | 1183096.4115
10 | 2575778.3775 | 1183069.6924 | 2575780.6231 | 1183060.5674 | 2575785.5369 | 1183061.7815 | 2575786.413 | 1183057.5646 | 2575788.347 | 1183050.6643 | 2575799.9935 | 1183053.563 | 2575837.1567 | 1183062.784 | 2575866.0362 | 1183070.0598 | 2575862.8564 | 1183082.2902
11 | 2575682.1976 | 1183035.2876 | 2575686.9986 | 1183036.5728
12 | 2575611.635 | 1183121.676 | 2575612.3853 | 1183124.0742 | 2575640.2102 | 1183133.9378
13 | 2575862.8564 | 1183082.2902 | 2575858.2968 | 1183099.8261
14 | 2575857.0229 | 1183104.7255 | 2575858.2968 | 1183099.8261
15 | 2575804.5261 | 1183182.9343 | 2575819.215 | 1183186.8769 | 2575834.5764 | 1183191.0168 | 2575840.9359 | 1183166.5672 | 2575843.7318 | 1183168.8794 | 2575845.8452 | 1183170.4605 | 2575861.5741 | 1183108.7981 | 2575859.4132 | 1183106.8058 | 2575857.0229 | 1183104.7255
16 | 2575804.5261 | 1183182.9343 | 2575811.8796 | 1183154.0218
17 | 2575813.7163 | 1183146.8005 | 2575811.8796 | 1183154.0218

## bus_geodata
| x | y | coords
0 | 2575738.5224 | 1183023.3059
1 | 2575669.7039 | 1183008.1355
2 | 2575769.5405 | 1183029.196
3 | 2575674.2921 | 1183062.4117
4 | 2575620.8006 | 1183094.7468
5 | 2575778.3775 | 1183069.6924
6 | 2575683.2707 | 1183064.4429
7 | 2575682.1976 | 1183035.2876
8 | 2575611.635 | 1183121.676
9 | 2575637.1656 | 1183100.593
10 | 2575862.8564 | 1183082.2902
11 | 2575858.2968 | 1183099.8261
12 | 2575745.9545 | 1183096.4115
13 | 2575804.5261 | 1183182.9343
14 | 2575857.0229 | 1183104.7255
15 | 2575811.8796 | 1183154.0218
16 | 2575686.9986 | 1183036.5728
17 | 2575640.2102 | 1183133.9378
18 | 2575813.7163 | 1183146.8005
19 | 2575778.3775 | 1183069.6924

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98874 | -0.2131 | 0.0052625 | 0.0013189
1 | 0.98451 | -0.29444 | 0 | 0
2 | 0.99068 | -0.17614 | 0 | 0
3 | 0.97963 | -0.38965 | 0 | 0
4 | 0.97286 | -0.52133 | 0 | 0
5 | 0.99472 | -0.099443 | 0 | 0
6 | 0.97916 | -0.39896 | 0.05586 | 0.014
7 | 0.97872 | -0.40761 | 0 | 0
8 | 0.97177 | -0.54284 | 0 | 0
9 | 0.97171 | -0.54411 | 0.071095 | 0.017818
10 | 0.98236 | -0.337 | 0 | 0
11 | 0.98047 | -0.3738 | 0.070777 | 0.017738
12 | 1 | 0 | -0.31823 | -0.082038
13 | 0.97516 | -0.47773 | 0 | 0
14 | 0.98028 | -0.37761 | 0 | 0
15 | 0.97401 | -0.50043 | 0.0013547 | 0.00033951
16 | 0.9786 | -0.40984 | 0.024704 | 0.0061913
17 | 0.97056 | -0.56678 | 0.040449 | 0.010137
18 | 0.97373 | -0.50592 | 0.040116 | 0.010054
19 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.19468 | 0.049784 | -0.19391 | -0.049298 | 0.000763 | 0.0004856 | 0.29333 | 0.29333 | 0.29333 | 0.98874 | -0.2131 | 0.98451 | -0.29444 | 26.8622
1 | -0.19994 | -0.051103 | 0.2003 | 0.051331 | 0.00035816 | 0.00022801 | 0.30125 | 0.30125 | 0.30125 | 0.98874 | -0.2131 | 0.99068 | -0.17614 | 27.5873
2 | 0.08098 | 0.020456 | -0.080612 | -0.020222 | 0.00036768 | 0.00023449 | 0.12245 | 0.12245 | 0.12245 | 0.98451 | -0.29444 | 0.97963 | -0.38965 | 33.6408
3 | 0.11293 | 0.028842 | -0.11171 | -0.02806 | 0.001224 | 0.00078194 | 0.17088 | 0.17088 | 0.17088 | 0.98451 | -0.29444 | 0.97286 | -0.52133 | 46.946
4 | -0.2003 | -0.051331 | 0.20104 | 0.051806 | 0.00074761 | 0.00047592 | 0.30125 | 0.30125 | 0.30125 | 0.99068 | -0.17614 | 0.99472 | -0.099443 | 27.5873
5 | 0.055885 | 0.014016 | -0.05586 | -0.014 | 2.4808e-05 | 1.5761e-05 | 0.08489 | 0.08489 | 0.08489 | 0.97963 | -0.38965 | 0.97916 | -0.39896 | 23.3213
6 | 0.024727 | 0.006206 | -0.024706 | -0.0061929 | 2.1164e-05 | 1.3042e-05 | 0.037563 | 0.037563 | 0.037563 | 0.97963 | -0.38965 | 0.97872 | -0.40761 | 10.3196
7 | 0.040536 | 0.010193 | -0.040495 | -0.010167 | 4.1589e-05 | 2.626e-05 | 0.062013 | 0.062013 | 0.062013 | 0.97286 | -0.52133 | 0.97177 | -0.54284 | 17.0366
8 | 0.071172 | 0.017867 | -0.071095 | -0.017818 | 7.7241e-05 | 4.9218e-05 | 0.10887 | 0.10887 | 0.10887 | 0.97286 | -0.52133 | 0.97171 | -0.54411 | 29.9094
9 | -0.31505 | -0.08106 | 0.31658 | 0.082038 | 0.0015314 | 0.00097796 | 0.47204 | 0.47204 | 0.47204 | 0.99472 | -0.099443 | 1 | 0 | 43.2271
10 | 0.11401 | 0.029253 | -0.11271 | -0.028424 | 0.0012977 | 0.00082903 | 0.17079 | 0.17079 | 0.17079 | 0.99472 | -0.099443 | 0.98236 | -0.337 | 46.9197
11 | 0.024706 | 0.0061929 | -0.024704 | -0.0061913 | 2.6298e-06 | 1.6206e-06 | 0.037563 | 0.037563 | 0.037563 | 0.97872 | -0.40761 | 0.9786 | -0.40984 | 10.3196
12 | 0.040495 | 0.010167 | -0.040449 | -0.010137 | 4.6197e-05 | 2.917e-05 | 0.062013 | 0.062014 | 0.062014 | 0.97177 | -0.54284 | 0.97056 | -0.56678 | 17.0367
13 | 0.11271 | 0.028424 | -0.11251 | -0.028298 | 0.00019819 | 0.00012661 | 0.17079 | 0.17079 | 0.17079 | 0.98236 | -0.337 | 0.98047 | -0.3738 | 46.9197
14 | 0.041733 | 0.010559 | -0.041726 | -0.010555 | 7.624e-06 | 4.8155e-06 | 0.063373 | 0.063373 | 0.063373 | 0.98047 | -0.3738 | 0.98028 | -0.37761 | 17.4101
15 | -0.041526 | -0.010429 | 0.041726 | 0.010555 | 0.00019939 | 0.00012595 | 0.063374 | 0.063373 | 0.063374 | 0.97516 | -0.47773 | 0.98028 | -0.37761 | 17.4103
16 | 0.041526 | 0.010429 | -0.041481 | -0.0104 | 4.4931e-05 | 2.8384e-05 | 0.063374 | 0.063374 | 0.063374 | 0.97516 | -0.47773 | 0.97401 | -0.50043 | 17.4103
17 | 0.040127 | 0.010061 | -0.040116 | -0.010054 | 1.0501e-05 | 6.628e-06 | 0.061304 | 0.061304 | 0.061304 | 0.97401 | -0.50043 | 0.97373 | -0.50592 | 16.8418

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39217 | 0.10057

## res_load
| p_mw | q_mvar
0 | 0.0052625 | 0.0013189
1 | 0.05586 | 0.014
2 | 0.071095 | 0.017818
3 | 0.070777 | 0.017738
4 | 0.073939 | 0.018531
5 | 0.0013547 | 0.00033951
6 | 0.024704 | 0.0061913
7 | 0.040449 | 0.010137
8 | 0.040116 | 0.010054

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1