## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2228-19_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2228-19_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2228-19_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2228-19_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2228-19_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2228-19_0_6_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_2228-19_0_6_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_2228-19_0_6_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2228-19_0_6_node_49 | 0.4 | n |  | TRUE
9 | bus_LV_2228-19_0_6_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_2228-19_0_6_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_2228-19_0_6_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_2228-19_0_6_node_48 | 0.4 | n |  | TRUE
13 | bus_LV_2228-19_0_6_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_2228-19_0_6_node_50 | 0.4 | n |  | TRUE
15 | bus_LV_2228-19_0_6_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_2228-19_0_6_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_2228-19_0_6_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_2228-19_0_6_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2228-19_0_6_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_2228-19_0_6_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_2228-19_0_6_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_2228-19_0_6_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_2228-19_0_6_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_2228-19_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2228-19_0_6_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2228-19_0_6_node_8 | 0.4 | n |  | TRUE
27 | bus_LV_2228-19_0_6_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2228-19_0_6_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2228-19_0_6_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_2228-19_0_6_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2228-19_0_6_node_6 | 0.4 | n |  | TRUE
32 | bus_LV_2228-19_0_6_node_7 | 0.4 | n |  | TRUE
33 | bus_LV_2228-19_0_6_node_5 | 0.4 | n |  | TRUE
34 | bus_LV_2228-19_0_6_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_2228-19_0_6_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_2228-19_0_6_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_2228-19_0_6_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_2228-19_0_6_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_2228-19_0_6_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2228-19_0_6_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_2228-19_0_6_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_2228-19_0_6_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2228-19_0_6_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_2228-19_0_6_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_2228-19_0_6_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_2228-19_0_6_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_2228-19_0_6_node_46 | 0.4 | n |  | TRUE
48 | bus_MV_505_0_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2228-19_0_6_load_0 | 0 | 0.0017808 | 0.0004463 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2228-19_0_6_load_1 | 1 | 0.0065212 | 0.0016344 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2228-19_0_6_load_2 | 2 | 0.0018162 | 0.00045519 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2228-19_0_6_load_4 | 4 | 0.0014983 | 0.00037552 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2228-19_0_6_load_25 | 5 | 0.0069141 | 0.0017328 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2228-19_0_6_load_9 | 6 | 0.0026113 | 0.00065445 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2228-19_0_6_load_49 | 8 | 0.0025778 | 0.00064606 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2228-19_0_6_load_48 | 12 | 0.0012074 | 0.0003026 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2228-19_0_6_load_50 | 14 | 0.063454 | 0.015903 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2228-19_0_6_load_38 | 17 | 0.0074702 | 0.0018722 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2228-19_0_6_load_47 | 20 | 0.0069439 | 0.0017403 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2228-19_0_6_load_39 | 21 | 0.0071485 | 0.0017916 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2228-19_0_6_load_36 | 22 | 0.027438 | 0.0068767 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2228-19_0_6_load_44 | 23 | 0.0026058 | 0.00065308 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2228-19_0_6_load_26 | 25 | 0.017729 | 0.0044432 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2228-19_0_6_load_34 | 29 | 0.020632 | 0.0051709 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2228-19_0_6_load_32 | 30 | 0.020616 | 0.005167 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2228-19_0_6_load_6 | 31 | 0.0026075 | 0.0006535 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2228-19_0_6_load_7 | 32 | 0.0030367 | 0.00076107 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2228-19_0_6_load_5 | 33 | 0.0027407 | 0.00068688 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2228-19_0_6_load_37 | 34 | 0.0025766 | 0.00064574 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2228-19_0_6_load_35 | 35 | 0.0075627 | 0.0018954 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2228-19_0_6_load_41 | 36 | 0.0054586 | 0.001368 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2228-19_0_6_load_40 | 37 | 0.006415 | 0.0016077 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2228-19_0_6_load_30 | 41 | 0.085268 | 0.02137 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2228-19_0_6_load_27 | 42 | 0.0080687 | 0.0020222 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2228-19_0_6_load_33 | 43 | 0.041241 | 0.010336 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2228-19_0_6_load_42 | 45 | 0.006415 | 0.0016077 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2228-19_0_6_load_43 | 46 | 0.0087199 | 0.0021854 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2228-19_0_6_line_0 |  | 0 | 1 | 0.010172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2228-19_0_6_line_1 |  | 0 | 2 | 0.007808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_2228-19_0_6_line_2 |  | 1 | 3 | 0.017134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2228-19_0_6_line_3 |  | 2 | 4 | 0.01399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2228-19_0_6_line_4 |  | 3 | 5 | 0.013429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2228-19_0_6_line_5 |  | 4 | 6 | 0.0049596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2228-19_0_6_line_6 |  | 5 | 15 | 0.052145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2228-19_0_6_line_7 |  | 6 | 32 | 0.011833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2228-19_0_6_line_8 |  | 7 | 8 | 0.016592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2228-19_0_6_line_9 |  | 7 | 9 | 0.021587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2228-19_0_6_line_10 |  | 8 | 10 | 0.020052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2228-19_0_6_line_11 |  | 9 | 12 | 0.0020951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2228-19_0_6_line_12 |  | 10 | 11 | 0.027572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2228-19_0_6_line_13 |  | 11 | 19 | 0.017583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2228-19_0_6_line_14 |  | 11 | 20 | 0.038454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2228-19_0_6_line_15 |  | 11 | 18 | 0.055836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2228-19_0_6_line_16 |  | 13 | 14 | 0.01822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2228-19_0_6_line_17 |  | 13 | 15 | 0.029624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2228-19_0_6_line_18 |  | 15 | 19 | 0.05686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2228-19_0_6_line_19 |  | 16 | 17 | 0.044877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2228-19_0_6_line_20 |  | 16 | 18 | 0.004279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2228-19_0_6_line_21 |  | 18 | 23 | 0.019733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2228-19_0_6_line_22 |  | 19 | 21 | 0.069889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2228-19_0_6_line_23 |  | 19 | 22 | 0.042144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2228-19_0_6_line_24 |  | 22 | 35 | 0.030858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2228-19_0_6_line_25 |  | 23 | 38 | 0.078106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2228-19_0_6_line_26 |  | 24 | 25 | 0.060447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2228-19_0_6_line_27 |  | 24 | 26 | 0.064174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2228-19_0_6_line_28 |  | 25 | 42 | 0.028586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2228-19_0_6_line_29 |  | 26 | 31 | 0.039078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2228-19_0_6_line_30 |  | 27 | 28 | 0.016613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2228-19_0_6_line_31 |  | 27 | 29 | 0.061079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2228-19_0_6_line_32 |  | 28 | 30 | 0.034948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2228-19_0_6_line_33 |  | 29 | 40 | 0.048826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2228-19_0_6_line_34 |  | 30 | 43 | 0.06532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_2228-19_0_6_line_35 |  | 31 | 33 | 0.035419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2228-19_0_6_line_36 |  | 32 | 33 | 0.011283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2228-19_0_6_line_37 |  | 34 | 35 | 0.027586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2228-19_0_6_line_38 |  | 36 | 37 | 0.012351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2228-19_0_6_line_39 |  | 37 | 45 | 0.01235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2228-19_0_6_line_40 |  | 38 | 47 | 0.085867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2228-19_0_6_line_41 |  | 39 | 40 | 0.048186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2228-19_0_6_line_42 |  | 39 | 41 | 0.039625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2228-19_0_6_line_43 |  | 40 | 44 | 0.11987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2228-19_0_6_line_44 |  | 42 | 44 | 0.011427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2228-19_0_6_line_45 |  | 45 | 46 | 0.030517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2228-19_0_6_line_46 |  | 46 | 47 | 0.089371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2228-19_0_6_trafo_23 | 0.63 MVA 20/0.4 kV | 48 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2576589.6476 | 1183163.3618 | 2576594.9546 | 1183163.9512 | 2576599.6954 | 1183163.0171
1 | 2576589.6476 | 1183163.3618 | 2576581.8873 | 1183162.4998
2 | 2576605.6067 | 1183147.0451 | 2576599.9053 | 1183162.9758 | 2576599.6954 | 1183163.0171
3 | 2576567.983 | 1183160.9554 | 2576581.8873 | 1183162.4998
4 | 2576605.6067 | 1183147.0451 | 2576618.3466 | 1183151.2928
5 | 2576567.983 | 1183160.9554 | 2576563.0537 | 1183160.4078
6 | 2576653.0687 | 1183184.1453 | 2576651.961 | 1183174.1889 | 2576649.2658 | 1183168.263 | 2576644.4694 | 1183163.8239 | 2576632.9529 | 1183156.9209 | 2576619.909 | 1183151.8138 | 2576618.3466 | 1183151.2928
7 | 2576551.2929 | 1183159.1015 | 2576563.0537 | 1183160.4078
8 | 2576733.5949 | 1183176.5937 | 2576717.8707 | 1183171.2993
9 | 2576740.9591 | 1183156.2988 | 2576733.5949 | 1183176.5937
10 | 2576698.8672 | 1183164.9008 | 2576717.8707 | 1183171.2993
11 | 2576740.9591 | 1183156.2988 | 2576738.9663 | 1183155.6522
12 | 2576682.8198 | 1183156.9927 | 2576680.5212 | 1183158.7581 | 2576680.5973 | 1183160.6477 | 2576682.0933 | 1183162.5317 | 2576690.3593 | 1183165.979 | 2576693.9214 | 1183167.1546 | 2576697.69 | 1183168.4072 | 2576698.8672 | 1183164.9008
13 | 2576671.2178 | 1183149.6897 | 2576676.59 | 1183147.1563 | 2576679.6861 | 1183152.1468 | 2576682.8198 | 1183156.9927
14 | 2576682.8198 | 1183156.9927 | 2576691.3378 | 1183152.6349 | 2576719.6313 | 1183146.8155
15 | 2576682.8198 | 1183156.9927 | 2576679.6861 | 1183152.1468 | 2576704.8309 | 1183145.7008 | 2576728.4943 | 1183141.095
16 | 2576687.2756 | 1183205.1781 | 2576669.9464 | 1183199.3984
17 | 2576653.0687 | 1183184.1453 | 2576660.9066 | 1183185.4931 | 2576670.1196 | 1183187.0802 | 2576669.8774 | 1183195.4077 | 2576669.9464 | 1183199.3984
18 | 2576653.0687 | 1183184.1453 | 2576660.9066 | 1183185.4931 | 2576663.8822 | 1183175.2873 | 2576666.967 | 1183175.4309 | 2576669.9257 | 1183174.5855 | 2576672.461 | 1183172.8303 | 2576674.2836 | 1183170.3552 | 2576675.2187 | 1183167.4167 | 2576675.2082 | 1183164.7153 | 2576674.4346 | 1183162.1281 | 2576672.9447 | 1183159.8661 | 2576670.8767 | 1183158.1177 | 2576675.2319 | 1183155.1658 | 2576671.2178 | 1183149.6897
19 | 2576727.7984 | 1183136.8733 | 2576724.3894 | 1183116.2537 | 2576700.437 | 1183117.3401
20 | 2576728.4943 | 1183141.095 | 2576727.7984 | 1183136.8733
21 | 2576728.4943 | 1183141.095 | 2576747.8636 | 1183137.3234
22 | 2576671.2178 | 1183149.6897 | 2576666.3852 | 1183143.7944 | 2576652.6 | 1183142.4032 | 2576656.9688 | 1183121.4529 | 2576658.9665 | 1183114.9751 | 2576655.2845 | 1183108.5417 | 2576649.9749 | 1183101.7145 | 2576646.0145 | 1183100.2069
23 | 2576671.2178 | 1183149.6897 | 2576662.13 | 1183152.8047 | 2576658.2005 | 1183153.3314 | 2576652.1111 | 1183152.0768 | 2576631.0467 | 1183144.589
24 | 2576602.0431 | 1183134.0553 | 2576612.6407 | 1183138.0462 | 2576631.0467 | 1183144.589
25 | 2576824.919 | 1183124.5891 | 2576758.4969 | 1183135.2529 | 2576747.8636 | 1183137.3234
26 | 2576450.3878 | 1183174.1028 | 2576451.3772 | 1183173.3207 | 2576452.3708 | 1183173.6281 | 2576459.473 | 1183181.9711 | 2576503.4877 | 1183198.9851
27 | 2576450.3878 | 1183174.1028 | 2576449.2866 | 1183173.6291 | 2576449.7401 | 1183172.4601 | 2576453.3525 | 1183163.1521 | 2576459.7971 | 1183157.7016 | 2576460.656 | 1183156.7421 | 2576460.7858 | 1183152.8841 | 2576461.2157 | 1183138.008 | 2576461.2624 | 1183134.3503 | 2576480.8481 | 1183133.4171
28 | 2576530.1505 | 1183209.2917 | 2576503.4877 | 1183198.9851
29 | 2576480.8481 | 1183133.4171 | 2576480.2017 | 1183141.7907 | 2576481.2017 | 1183145.6332 | 2576483.5309 | 1183149.715 | 2576488.3346 | 1183152.1084 | 2576504.8757 | 1183153.9457
30 | 2576683.1847 | 1183324.6119 | 2576688.7505 | 1183322.8115 | 2576687.5693 | 1183317.4911 | 2576687.0677 | 1183312.2014
31 | 2576683.1847 | 1183324.6119 | 2576677.1995 | 1183324.5575 | 2576655.0337 | 1183319.5638 | 2576623.5851 | 1183311.8865
32 | 2576687.0677 | 1183312.2014 | 2576680.1232 | 1183312.8066 | 2576666.9349 | 1183309.7343 | 2576669.6405 | 1183295.5549
33 | 2576576.1525 | 1183300.3071 | 2576623.5851 | 1183311.8865
34 | 2576652.9765 | 1183240.5862 | 2576662.1595 | 1183242.329 | 2576674.1313 | 1183272.0199 | 2576669.6405 | 1183295.5549
35 | 2576540.0786 | 1183157.8559 | 2576504.8757 | 1183153.9457
36 | 2576540.0786 | 1183157.8559 | 2576551.2929 | 1183159.1015
37 | 2576602.0431 | 1183134.0553 | 2576583.366 | 1183127.0219 | 2576576.2892 | 1183124.1741
38 | 2576697.3177 | 1183068.2974 | 2576685.1475 | 1183070.4029
39 | 2576697.3177 | 1183068.2974 | 2576709.487 | 1183066.192
40 | 2576828.3002 | 1183051.638 | 2576832.3918 | 1183067.2858 | 2576839.3372 | 1183121.8651 | 2576824.919 | 1183124.5891
41 | 2576576.1525 | 1183300.3071 | 2576570.4062 | 1183298.9067 | 2576528.6197 | 1183291.6782
42 | 2576528.6197 | 1183291.6782 | 2576542.4399 | 1183254.5413
43 | 2576540.8089 | 1183213.4117 | 2576543.9679 | 1183218.8688 | 2576588.5393 | 1183235.3025 | 2576576.1525 | 1183300.3071
44 | 2576540.8089 | 1183213.4117 | 2576530.1505 | 1183209.2917
45 | 2576739.5577 | 1183060.9896 | 2576709.487 | 1183066.192
46 | 2576828.3002 | 1183051.638 | 2576814.4666 | 1183051.6028 | 2576765.0079 | 1183056.5866 | 2576739.5577 | 1183060.9896

## bus_geodata
| x | y | coords
0 | 2576589.6476 | 1183163.3618
1 | 2576599.6954 | 1183163.0171
2 | 2576581.8873 | 1183162.4998
3 | 2576605.6067 | 1183147.0451
4 | 2576567.983 | 1183160.9554
5 | 2576618.3466 | 1183151.2928
6 | 2576563.0537 | 1183160.4078
7 | 2576733.5949 | 1183176.5937
8 | 2576717.8707 | 1183171.2993
9 | 2576740.9591 | 1183156.2988
10 | 2576698.8672 | 1183164.9008
11 | 2576682.8198 | 1183156.9927
12 | 2576738.9663 | 1183155.6522
13 | 2576669.9464 | 1183199.3984
14 | 2576687.2756 | 1183205.1781
15 | 2576653.0687 | 1183184.1453
16 | 2576727.7984 | 1183136.8733
17 | 2576700.437 | 1183117.3401
18 | 2576728.4943 | 1183141.095
19 | 2576671.2178 | 1183149.6897
20 | 2576719.6313 | 1183146.8155
21 | 2576646.0145 | 1183100.2069
22 | 2576631.0467 | 1183144.589
23 | 2576747.8636 | 1183137.3234
24 | 2576450.3878 | 1183174.1028
25 | 2576503.4877 | 1183198.9851
26 | 2576480.8481 | 1183133.4171
27 | 2576683.1847 | 1183324.6119
28 | 2576687.0677 | 1183312.2014
29 | 2576623.5851 | 1183311.8865
30 | 2576669.6405 | 1183295.5549
31 | 2576504.8757 | 1183153.9457
32 | 2576551.2929 | 1183159.1015
33 | 2576540.0786 | 1183157.8559
34 | 2576576.2892 | 1183124.1741
35 | 2576602.0431 | 1183134.0553
36 | 2576685.1475 | 1183070.4029
37 | 2576697.3177 | 1183068.2974
38 | 2576824.919 | 1183124.5891
39 | 2576528.6197 | 1183291.6782
40 | 2576576.1525 | 1183300.3071
41 | 2576542.4399 | 1183254.5413
42 | 2576530.1505 | 1183209.2917
43 | 2576652.9765 | 1183240.5862
44 | 2576540.8089 | 1183213.4117
45 | 2576709.487 | 1183066.192
46 | 2576739.5577 | 1183060.9896
47 | 2576828.3002 | 1183051.638
48 | 2576660.9066 | 1183185.4931

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99527 | -0.089226 | 0.0017808 | 0.0004463
1 | 0.99576 | -0.079847 | 0.0065212 | 0.0016344
2 | 0.99489 | -0.096372 | 0.0018162 | 0.00045519
3 | 0.99662 | -0.063578 | 0 | 0
4 | 0.99422 | -0.10908 | 0.0014983 | 0.00037552
5 | 0.9973 | -0.050846 | 0.0069141 | 0.0017328
6 | 0.99398 | -0.11355 | 0.0026113 | 0.00065445
7 | 0.99423 | -0.11052 | 0 | 0
8 | 0.99425 | -0.11017 | 0.0025778 | 0.00064606
9 | 0.99421 | -0.11098 | 0 | 0
10 | 0.99432 | -0.10883 | 0 | 0
11 | 0.99441 | -0.10699 | 0 | 0
12 | 0.9942 | -0.11103 | 0.0012074 | 0.0003026
13 | 0.99829 | -0.03282 | 0 | 0
14 | 0.99724 | -0.053061 | 0.063454 | 0.015903
15 | 1 | 0 | -0.38627 | -0.098505
16 | 0.99248 | -0.14414 | 0 | 0
17 | 0.99217 | -0.15007 | 0.0074702 | 0.0018722
18 | 0.99251 | -0.14357 | 0 | 0
19 | 0.99518 | -0.092179 | 0 | 0
20 | 0.99417 | -0.1117 | 0.0069439 | 0.0017403
21 | 0.99473 | -0.10098 | 0.0071485 | 0.0017916
22 | 0.99374 | -0.12009 | 0.027438 | 0.0068767
23 | 0.99197 | -0.15392 | 0.0026058 | 0.00065308
24 | 0.98664 | -0.25385 | 0 | 0
25 | 0.98391 | -0.30638 | 0.017729 | 0.0044432
26 | 0.98953 | -0.1984 | 0 | 0
27 | 0.9758 | -0.46462 | 0 | 0
28 | 0.97556 | -0.46933 | 0 | 0
29 | 0.97668 | -0.44735 | 0.020632 | 0.0051709
30 | 0.97506 | -0.47923 | 0.020616 | 0.005167
31 | 0.99129 | -0.16479 | 0.0026075 | 0.0006535
32 | 0.99343 | -0.1241 | 0.0030367 | 0.00076107
33 | 0.9929 | -0.13402 | 0.0027407 | 0.00068688
34 | 0.99339 | -0.12687 | 0.0025766 | 0.00064574
35 | 0.99345 | -0.12562 | 0.0075627 | 0.0018954
36 | 0.98496 | -0.28978 | 0.0054586 | 0.001368
37 | 0.98503 | -0.28857 | 0.006415 | 0.0016077
38 | 0.99003 | -0.19137 | 0 | 0
39 | 0.97634 | -0.45397 | 0 | 0
40 | 0.97762 | -0.42896 | 0 | 0
41 | 0.97319 | -0.51595 | 0.085268 | 0.02137
42 | 0.98274 | -0.32904 | 0.0080687 | 0.0020222
43 | 0.9738 | -0.50396 | 0.041241 | 0.010336
44 | 0.9823 | -0.3377 | 0 | 0
45 | 0.98516 | -0.28594 | 0.006415 | 0.0016077
46 | 0.98567 | -0.27592 | 0.0087199 | 0.0021854
47 | 0.9879 | -0.23271 | 0 | 0
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.2133 | -0.054851 | 0.2134 | 0.054912 | 9.7286e-05 | 6.1734e-05 | 0.31941 | 0.31941 | 0.31941 | 0.99527 | -0.089226 | 0.99576 | -0.079847 | 21.9373
1 | 0.21152 | 0.054404 | -0.21145 | -0.054358 | 7.344e-05 | 4.6596e-05 | 0.31674 | 0.31674 | 0.31674 | 0.99527 | -0.089226 | 0.99489 | -0.096372 | 21.7545
2 | -0.21992 | -0.056547 | 0.2201 | 0.056657 | 0.00017403 | 0.00011049 | 0.32915 | 0.32915 | 0.32915 | 0.99576 | -0.079847 | 0.99662 | -0.063578 | 22.6066
3 | 0.20963 | 0.053903 | -0.2095 | -0.053821 | 0.00012934 | 8.2049e-05 | 0.31403 | 0.31403 | 0.31403 | 0.99489 | -0.096372 | 0.99422 | -0.10908 | 21.5679
4 | -0.2201 | -0.056657 | 0.22023 | 0.056744 | 0.0001364 | 8.6596e-05 | 0.32915 | 0.32915 | 0.32915 | 0.99662 | -0.063578 | 0.9973 | -0.050846 | 22.6065
5 | 0.20801 | 0.053445 | -0.20796 | -0.053416 | 4.52e-05 | 2.8671e-05 | 0.31179 | 0.31179 | 0.31179 | 0.99422 | -0.10908 | 0.99398 | -0.11355 | 21.4139
6 | -0.22715 | -0.058477 | 0.22771 | 0.058835 | 0.00056335 | 0.00035782 | 0.33947 | 0.33947 | 0.33947 | 0.9973 | -0.050846 | 1 | 0 | 23.315
7 | 0.20535 | 0.052762 | -0.20524 | -0.052695 | 0.00010515 | 6.6685e-05 | 0.30788 | 0.30788 | 0.30788 | 0.99398 | -0.11355 | 0.99343 | -0.1241 | 21.1454
8 | -0.0012074 | -0.00030231 | 0.0012074 | 0.00030211 | 2.0314e-08 | -2.0217e-07 | 0.001807 | 0.0018069 | 0.001807 | 0.99423 | -0.11052 | 0.99425 | -0.11017 | 0.49642
9 | 0.0012074 | 0.00030231 | -0.0012074 | -0.00030257 | 2.6433e-08 | -2.6302e-07 | 0.001807 | 0.0018071 | 0.0018071 | 0.99423 | -0.11052 | 0.99421 | -0.11098 | 0.49644
10 | -0.0037852 | -0.00094816 | 0.0037855 | 0.00094806 | 2.413e-07 | -1.0563e-07 | 0.0056649 | 0.0056648 | 0.0056649 | 0.99425 | -0.11017 | 0.99432 | -0.10883 | 1.5563
11 | 0.0012074 | 0.00030257 | -0.0012074 | -0.0003026 | 2.5655e-09 | -2.5527e-08 | 0.0018071 | 0.0018071 | 0.0018071 | 0.99421 | -0.11098 | 0.9942 | -0.11103 | 0.49645
12 | -0.0037855 | -0.00094806 | 0.0037858 | 0.00094791 | 3.3179e-07 | -1.4532e-07 | 0.0056648 | 0.0056647 | 0.0056648 | 0.99432 | -0.10883 | 0.99441 | -0.10699 | 1.5563
13 | -0.048067 | -0.012138 | 0.048101 | 0.01216 | 3.4142e-05 | 2.1623e-05 | 0.071958 | 0.071958 | 0.071958 | 0.99441 | -0.10699 | 0.99518 | -0.092179 | 19.7688
14 | 0.0069454 | 0.0017408 | -0.0069439 | -0.0017403 | 1.5576e-06 | 4.9813e-07 | 0.010393 | 0.010393 | 0.010393 | 0.99441 | -0.10699 | 0.99417 | -0.1117 | 2.8553
15 | 0.037336 | 0.0094494 | -0.03727 | -0.0094082 | 6.5431e-05 | 4.1153e-05 | 0.055901 | 0.055901 | 0.055901 | 0.99441 | -0.10699 | 0.99251 | -0.14357 | 15.3574
16 | 0.063515 | 0.015942 | -0.063454 | -0.015903 | 6.1251e-05 | 3.8963e-05 | 0.094682 | 0.094682 | 0.094682 | 0.99829 | -0.03282 | 0.99724 | -0.053061 | 26.0116
17 | -0.063515 | -0.015942 | 0.063615 | 0.016005 | 9.9589e-05 | 6.3349e-05 | 0.094682 | 0.094682 | 0.094682 | 0.99829 | -0.03282 | 1 | 0 | 26.0116
18 | 0.093294 | 0.023665 | -0.092883 | -0.023403 | 0.00041152 | 0.00026263 | 0.13892 | 0.13892 | 0.13892 | 1 | 0 | 0.99518 | -0.092179 | 38.1659
19 | 0.0074723 | 0.001873 | -0.0074702 | -0.0018722 | 2.1123e-06 | 7.721e-07 | 0.011203 | 0.011203 | 0.011203 | 0.99248 | -0.14414 | 0.99217 | -0.15007 | 3.0779
20 | -0.0074723 | -0.001873 | 0.0074725 | 0.0018731 | 2.014e-07 | 7.3599e-08 | 0.011203 | 0.011203 | 0.011203 | 0.99248 | -0.14414 | 0.99251 | -0.14357 | 3.0778
21 | 0.029798 | 0.0075352 | -0.029783 | -0.007526 | 1.4784e-05 | 9.207e-06 | 0.044698 | 0.044698 | 0.044698 | 0.99251 | -0.14357 | 0.99197 | -0.15392 | 12.2796
22 | 0.0071515 | 0.0017926 | -0.0071485 | -0.0017916 | 2.9969e-06 | 1.0103e-06 | 0.010693 | 0.010694 | 0.010694 | 0.99518 | -0.092179 | 0.99473 | -0.10098 | 2.9378
23 | 0.03763 | 0.0094503 | -0.03758 | -0.0094189 | 5.0045e-05 | 3.1482e-05 | 0.056272 | 0.056273 | 0.056273 | 0.99518 | -0.092179 | 0.99374 | -0.12009 | 15.4595
24 | 0.010142 | 0.0025422 | -0.010139 | -0.0025409 | 2.669e-06 | 1.3085e-06 | 0.015187 | 0.015187 | 0.015187 | 0.99374 | -0.12009 | 0.99345 | -0.12562 | 4.1722
25 | 0.027177 | 0.0068729 | -0.027128 | -0.0068427 | 4.8731e-05 | 3.0181e-05 | 0.040789 | 0.040789 | 0.040789 | 0.99197 | -0.15392 | 0.99003 | -0.19137 | 11.2059
26 | 0.19562 | 0.049809 | -0.19513 | -0.049496 | 0.0004942 | 0.00031321 | 0.29531 | 0.29531 | 0.29531 | 0.98664 | -0.25385 | 0.98391 | -0.30638 | 20.2824
27 | -0.19562 | -0.049809 | 0.19615 | 0.050141 | 0.00052467 | 0.0003325 | 0.29531 | 0.29531 | 0.29531 | 0.98664 | -0.25385 | 0.98953 | -0.1984 | 20.2823
28 | 0.1774 | 0.045052 | -0.17721 | -0.04493 | 0.0001932 | 0.0001222 | 0.2685 | 0.2685 | 0.2685 | 0.98391 | -0.30638 | 0.98274 | -0.32904 | 18.4409
29 | -0.19615 | -0.050141 | 0.19647 | 0.050344 | 0.00031949 | 0.00020246 | 0.29531 | 0.29531 | 0.29531 | 0.98953 | -0.1984 | 0.99129 | -0.16479 | 20.2822
30 | 0.061949 | 0.015557 | -0.061935 | -0.015549 | 1.3902e-05 | 8.0675e-06 | 0.094478 | 0.094479 | 0.094479 | 0.9758 | -0.46462 | 0.97556 | -0.46933 | 6.4889
31 | -0.061949 | -0.015557 | 0.062 | 0.015587 | 5.1112e-05 | 2.9657e-05 | 0.094478 | 0.094477 | 0.094478 | 0.9758 | -0.46462 | 0.97668 | -0.44735 | 6.4889
32 | 0.061935 | 0.015549 | -0.061906 | -0.015532 | 2.9245e-05 | 1.6973e-05 | 0.094479 | 0.094479 | 0.094479 | 0.97556 | -0.46933 | 0.97506 | -0.47923 | 6.489
33 | -0.082632 | -0.020758 | 0.082704 | 0.020802 | 7.2568e-05 | 4.3997e-05 | 0.12591 | 0.12591 | 0.12591 | 0.97668 | -0.44735 | 0.97762 | -0.42896 | 8.6477
34 | 0.041289 | 0.010365 | -0.041241 | -0.010336 | 4.8637e-05 | 2.95e-05 | 0.063017 | 0.063017 | 0.063017 | 0.97506 | -0.47923 | 0.9738 | -0.50396 | 8.6562
35 | -0.19907 | -0.050997 | 0.19937 | 0.051186 | 0.0002973 | 0.00018844 | 0.29922 | 0.29922 | 0.29922 | 0.99129 | -0.16479 | 0.9929 | -0.13402 | 20.551
36 | 0.20221 | 0.051934 | -0.20211 | -0.051873 | 9.7328e-05 | 6.1706e-05 | 0.30333 | 0.30333 | 0.30333 | 0.99343 | -0.1241 | 0.9929 | -0.13402 | 20.833
37 | -0.0025766 | -0.00064574 | 0.0025767 | 0.00064549 | 1.5408e-07 | -2.5855e-07 | 0.0038595 | 0.0038593 | 0.0038595 | 0.99339 | -0.12687 | 0.99345 | -0.12562 | 1.0603
38 | -0.0054586 | -0.001368 | 0.0054589 | 0.0013681 | 3.1496e-07 | 4.4367e-08 | 0.0082464 | 0.0082464 | 0.0082464 | 0.98496 | -0.28978 | 0.98503 | -0.28857 | 2.2655
39 | -0.011874 | -0.0029758 | 0.011875 | 0.0029766 | 1.4901e-06 | 7.9641e-07 | 0.017937 | 0.017937 | 0.017937 | 0.98503 | -0.28857 | 0.98516 | -0.28594 | 4.9278
40 | 0.027128 | 0.0068427 | -0.027075 | -0.0068095 | 5.3574e-05 | 3.3185e-05 | 0.040789 | 0.04079 | 0.04079 | 0.99003 | -0.19137 | 0.9879 | -0.23271 | 11.206
41 | -0.085521 | -0.021531 | 0.085623 | 0.021595 | 0.00010238 | 6.3714e-05 | 0.13038 | 0.13038 | 0.13038 | 0.97634 | -0.45397 | 0.97762 | -0.42896 | 11.9392
42 | 0.085521 | 0.021531 | -0.085268 | -0.02137 | 0.00025258 | 0.00016116 | 0.13038 | 0.13038 | 0.13038 | 0.97634 | -0.45397 | 0.97319 | -0.51595 | 35.8176
43 | -0.16833 | -0.042397 | 0.16907 | 0.042863 | 0.00073812 | 0.00046635 | 0.25629 | 0.25628 | 0.25629 | 0.97762 | -0.42896 | 0.9823 | -0.3377 | 17.602
44 | 0.16914 | 0.042908 | -0.16907 | -0.042863 | 7.0362e-05 | 4.4453e-05 | 0.25628 | 0.25628 | 0.25628 | 0.98274 | -0.32904 | 0.9823 | -0.3377 | 17.6019
45 | -0.01829 | -0.0045844 | 0.018299 | 0.0045896 | 8.7342e-06 | 5.2011e-06 | 0.027626 | 0.027626 | 0.027626 | 0.98516 | -0.28594 | 0.98567 | -0.27592 | 7.5897
46 | -0.027019 | -0.006775 | 0.027075 | 0.0068095 | 5.5761e-05 | 3.4546e-05 | 0.04079 | 0.04079 | 0.04079 | 0.98567 | -0.27592 | 0.9879 | -0.23271 | 11.2061

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38627 | 0.098505

## res_load
| p_mw | q_mvar
0 | 0.0017808 | 0.0004463
1 | 0.0065212 | 0.0016344
2 | 0.0018162 | 0.00045519
3 | 0.0014983 | 0.00037552
4 | 0.0069141 | 0.0017328
5 | 0.0026113 | 0.00065445
6 | 0.0025778 | 0.00064606
7 | 0.0012074 | 0.0003026
8 | 0.063454 | 0.015903
9 | 0.0074702 | 0.0018722
10 | 0.0069439 | 0.0017403
11 | 0.0071485 | 0.0017916
12 | 0.027438 | 0.0068767
13 | 0.0026058 | 0.00065308
14 | 0.017729 | 0.0044432
15 | 0.020632 | 0.0051709
16 | 0.020616 | 0.005167
17 | 0.0026075 | 0.0006535
18 | 0.0030367 | 0.00076107
19 | 0.0027407 | 0.00068688
20 | 0.0025766 | 0.00064574
21 | 0.0075627 | 0.0018954
22 | 0.0054586 | 0.001368
23 | 0.006415 | 0.0016077
24 | 0.085268 | 0.02137
25 | 0.0080687 | 0.0020222
26 | 0.041241 | 0.010336
27 | 0.006415 | 0.0016077
28 | 0.0087199 | 0.0021854

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1