## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2228-20_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2228-20_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2228-20_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2228-20_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2228-20_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2228-20_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2228-20_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_2228-20_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2228-20_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2228-20_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_2228-20_0_4_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_2228-20_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2228-20_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_2228-20_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_2228-20_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_2228-20_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_2228-20_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_2228-20_0_4_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_2228-20_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2228-20_0_4_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_2228-20_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2228-20_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2228-20_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2228-20_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2228-20_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_2228-20_0_4_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_2228-20_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_MV_505_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2228-20_0_4_load_0 | 0 | 0.0095092 | 0.0023832 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2228-20_0_4_load_5 | 4 | 0.012424 | 0.0031138 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2228-20_0_4_load_19 | 10 | 0.056093 | 0.014058 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2228-20_0_4_load_24 | 12 | 0.011129 | 0.0027893 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2228-20_0_4_load_27 | 13 | 0.044351 | 0.011115 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2228-20_0_4_load_29 | 14 | 0.072127 | 0.018077 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2228-20_0_4_load_26 | 15 | 0.013988 | 0.0035058 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2228-20_0_4_load_28 | 17 | 0.036617 | 0.0091772 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2228-20_0_4_load_20 | 19 | 0.0056214 | 0.0014089 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2228-20_0_4_load_12 | 21 | 0.0056214 | 0.0014089 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2228-20_0_4_load_11 | 22 | 0.041495 | 0.0104 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2228-20_0_4_load_25 | 25 | 0.093268 | 0.023375 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2228-20_0_4_load_23 | 26 | 0.0016355 | 0.00040989 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2228-20_0_4_line_0 |  | 0 | 1 | 0.064111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_2228-20_0_4_line_1 |  | 0 | 2 | 0.066355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2228-20_0_4_line_2 |  | 1 | 3 | 0.017204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2228-20_0_4_line_3 |  | 2 | 4 | 0.019406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2228-20_0_4_line_4 |  | 2 | 5 | 0.041047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2228-20_0_4_line_5 |  | 3 | 9 | 0.070625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2228-20_0_4_line_6 |  | 3 | 10 | 0.018695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2228-20_0_4_line_7 |  | 4 | 6 | 0.037661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2228-20_0_4_line_8 |  | 5 | 13 | 0.025467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2228-20_0_4_line_9 |  | 5 | 11 | 0.054567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2228-20_0_4_line_10 |  | 6 | 7 | 0.01946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2228-20_0_4_line_11 |  | 6 | 8 | 0.039842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2228-20_0_4_line_12 |  | 7 | 14 | 0.008166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2228-20_0_4_line_13 |  | 8 | 15 | 0.076647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2228-20_0_4_line_14 |  | 9 | 22 | 0.031756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2228-20_0_4_line_15 |  | 9 | 16 | 0.052517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2228-20_0_4_line_16 |  | 11 | 12 | 0.008418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2228-20_0_4_line_17 |  | 12 | 25 | 0.035039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2228-20_0_4_line_18 |  | 16 | 17 | 0.013712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2228-20_0_4_line_19 |  | 18 | 19 | 0.032519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2228-20_0_4_line_20 |  | 18 | 20 | 0.004651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2228-20_0_4_line_21 |  | 20 | 21 | 0.037653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2228-20_0_4_line_22 |  | 21 | 22 | 0.026497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2228-20_0_4_line_23 |  | 23 | 24 | 0.076218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2228-20_0_4_line_24 |  | 23 | 25 | 0.024069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2228-20_0_4_line_25 |  | 24 | 26 | 0.056895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2228-20_0_4_trafo_0 | 0.63 MVA 20/0.4 kV | 27 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2576831.629 | 1183323.0331 | 2576826.5815 | 1183332.491 | 2576820.1247 | 1183340.7315 | 2576816.3231 | 1183356.4878 | 2576819.691 | 1183364.6901 | 2576826.9045 | 1183370.4317 | 2576835.3575 | 1183372.1561
1 | 2576900.0792 | 1183379.2416 | 2576893.2508 | 1183382.2363 | 2576884.1278 | 1183382.1049 | 2576835.3575 | 1183372.1561
2 | 2576820.2564 | 1183311.7492 | 2576830.2027 | 1183317.4469 | 2576831.629 | 1183323.0331
3 | 2576900.0792 | 1183379.2416 | 2576904.4407 | 1183373.9776 | 2576906.0506 | 1183361.511
4 | 2576900.0792 | 1183379.2416 | 2576902.692 | 1183379.7651 | 2576909.5274 | 1183378.5825 | 2576911.9621 | 1183378.4397 | 2576914.1418 | 1183381.4662 | 2576915.241 | 1183385.3862 | 2576917.6775 | 1183385.7214 | 2576918.513 | 1183374.7458 | 2576918.9258 | 1183367.0179
5 | 2576756.4256 | 1183326.6941 | 2576757.8088 | 1183330.9798 | 2576766.6583 | 1183329.4557 | 2576771.5201 | 1183329.181 | 2576777.6211 | 1183327.6009 | 2576795.9045 | 1183317.7914 | 2576808.613 | 1183313.3175 | 2576820.2564 | 1183311.7492
6 | 2576820.2564 | 1183311.7492 | 2576823.4873 | 1183293.3357
7 | 2576910.8741 | 1183324.16 | 2576906.0506 | 1183361.511
8 | 2576918.9258 | 1183367.0179 | 2576922.3302 | 1183368.9057 | 2576927.303 | 1183371.6768 | 2576933.5147 | 1183373.0647 | 2576933.7768 | 1183363.5514
9 | 2576914.9606 | 1183421.4394 | 2576917.6775 | 1183385.7214 | 2576918.513 | 1183374.7458 | 2576918.9258 | 1183367.0179
10 | 2576905.5892 | 1183307.8164 | 2576911.7216 | 1183312.3395 | 2576910.8741 | 1183324.16
11 | 2576910.8741 | 1183324.16 | 2576921.276 | 1183323.3305 | 2576921.4079 | 1183310.0564 | 2576927.6273 | 1183311.4331 | 2576930.573 | 1183313.1337 | 2576932.3873 | 1183316.4173 | 2576933.6481 | 1183318.7025
12 | 2576899.0052 | 1183302.9616 | 2576905.5892 | 1183307.8164
13 | 2576933.6481 | 1183318.7025 | 2576951.4298 | 1183319.2674 | 2576957.853 | 1183322.0219 | 2576985.6488 | 1183326.0834 | 2576989.6578 | 1183328.3803 | 2576988.5033 | 1183343.7594 | 2576986.2577 | 1183345.4022 | 2576986.2853 | 1183346.353
14 | 2576756.4256 | 1183326.6941 | 2576755.4519 | 1183323.6629 | 2576741.1511 | 1183311.3011 | 2576743.1519 | 1183301.8415
15 | 2576756.4256 | 1183326.6941 | 2576757.8088 | 1183330.9798 | 2576766.6583 | 1183329.4557 | 2576771.5201 | 1183329.181 | 2576777.6211 | 1183327.6009 | 2576775.9277 | 1183355.4109
16 | 2576914.9606 | 1183421.4394 | 2576922.0466 | 1183421.9011 | 2576921.944 | 1183423.2141
17 | 2576919.2138 | 1183458.1463 | 2576921.944 | 1183423.2141
18 | 2576775.9277 | 1183355.4109 | 2576789.3596 | 1183358.3491
19 | 2576696.0618 | 1183302.7502 | 2576693.2913 | 1183285.3075 | 2576690.1381 | 1183271.546 | 2576689.936 | 1183270.8345
20 | 2576696.0618 | 1183302.7502 | 2576700.6231 | 1183303.7218
21 | 2576700.6231 | 1183303.7218 | 2576702.5955 | 1183294.665 | 2576704.0327 | 1183291.2576 | 2576704.1581 | 1183290.1454 | 2576704.8544 | 1183286.6298 | 2576724.4009 | 1183290.7812
22 | 2576743.1519 | 1183301.8415 | 2576744.2244 | 1183296.7704 | 2576742.7352 | 1183294.6751 | 2576724.4009 | 1183290.7812
23 | 2576900.9494 | 1183471.9088 | 2576899.3669 | 1183496.9279 | 2576899.7367 | 1183499.7836 | 2576900.3113 | 1183504.2503 | 2576902.8508 | 1183507.5533 | 2576908.2286 | 1183508.4775 | 2576908.7449 | 1183501.8498 | 2576910.8908 | 1183474.4383
24 | 2576910.8908 | 1183474.4383 | 2576917.886 | 1183475.1338 | 2576919.2138 | 1183458.1463
25 | 2576900.9494 | 1183471.9088 | 2576903.69 | 1183428.5422 | 2576903.64 | 1183423.5065 | 2576901.3374 | 1183418.3238 | 2576898.8596 | 1183417.1661

## bus_geodata
| x | y | coords
0 | 2576835.3575 | 1183372.1561
1 | 2576831.629 | 1183323.0331
2 | 2576900.0792 | 1183379.2416
3 | 2576820.2564 | 1183311.7492
4 | 2576906.0506 | 1183361.511
5 | 2576918.9258 | 1183367.0179
6 | 2576910.8741 | 1183324.16
7 | 2576905.5892 | 1183307.8164
8 | 2576933.6481 | 1183318.7025
9 | 2576756.4256 | 1183326.6941
10 | 2576823.4873 | 1183293.3357
11 | 2576914.9606 | 1183421.4394
12 | 2576921.944 | 1183423.2141
13 | 2576933.7768 | 1183363.5514
14 | 2576899.0052 | 1183302.9616
15 | 2576986.2853 | 1183346.353
16 | 2576775.9277 | 1183355.4109
17 | 2576789.3596 | 1183358.3491
18 | 2576696.0618 | 1183302.7502
19 | 2576689.936 | 1183270.8345
20 | 2576700.6231 | 1183303.7218
21 | 2576724.4009 | 1183290.7812
22 | 2576743.1519 | 1183301.8415
23 | 2576910.8908 | 1183474.4383
24 | 2576900.9494 | 1183471.9088
25 | 2576919.2138 | 1183458.1463
26 | 2576898.8596 | 1183417.1661
27 | 2576831.629 | 1183323.0331

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.40107 | -0.10205
1 | 0.99572 | -0.08162 | 0 | 0
2 | 0.99238 | -0.14506 | 0 | 0
3 | 0.99458 | -0.10364 | 0 | 0
4 | 0.99063 | -0.17897 | 0.012424 | 0.0031138
5 | 0.98953 | -0.19984 | 0 | 0
6 | 0.98764 | -0.23675 | 0 | 0
7 | 0.98635 | -0.26186 | 0 | 0
8 | 0.98713 | -0.24671 | 0 | 0
9 | 0.98878 | -0.2155 | 0 | 0
10 | 0.99362 | -0.12214 | 0.056093 | 0.014058
11 | 0.98418 | -0.3034 | 0 | 0
12 | 0.98336 | -0.31948 | 0.011129 | 0.0027893
13 | 0.9885 | -0.21997 | 0.044351 | 0.011115
14 | 0.98581 | -0.27242 | 0.072127 | 0.018077
15 | 0.98614 | -0.26591 | 0.013988 | 0.0035058
16 | 0.98701 | -0.24984 | 0 | 0
17 | 0.98655 | -0.25883 | 0.036617 | 0.0091772
18 | 0.98675 | -0.25499 | 0 | 0
19 | 0.98658 | -0.25826 | 0.0056214 | 0.0014089
20 | 0.98677 | -0.25452 | 0 | 0
21 | 0.98697 | -0.25073 | 0.0056214 | 0.0014089
22 | 0.98724 | -0.2454 | 0.041495 | 0.0104
23 | 0.98024 | -0.38032 | 0 | 0
24 | 0.98013 | -0.38259 | 0 | 0
25 | 0.98028 | -0.37961 | 0.093268 | 0.023375
26 | 0.98004 | -0.38428 | 0.0016355 | 0.00040989
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.14686 | 0.037353 | -0.14629 | -0.036987 | 0.00057511 | 0.00036639 | 0.21873 | 0.21873 | 0.21873 | 1 | 0 | 0.99572 | -0.08162 | 30.0452
1 | 0.25255 | 0.0647 | -0.25079 | -0.063574 | 0.0017618 | 0.0011258 | 0.3763 | 0.3763 | 0.3763 | 1 | 0 | 0.99238 | -0.14506 | 51.6898
2 | 0.14629 | 0.036987 | -0.14613 | -0.036888 | 0.00015433 | 9.8323e-05 | 0.21873 | 0.21873 | 0.21873 | 0.99572 | -0.08162 | 0.99458 | -0.10364 | 30.0453
3 | 0.099082 | 0.025041 | -0.098921 | -0.024938 | 0.00016079 | 0.00010265 | 0.14864 | 0.14864 | 0.14864 | 0.99238 | -0.14506 | 0.99063 | -0.17897 | 40.8354
4 | 0.15171 | 0.038534 | -0.15131 | -0.038279 | 0.0003989 | 0.00025424 | 0.22766 | 0.22766 | 0.22766 | 0.99238 | -0.14506 | 0.98953 | -0.19984 | 31.2722
5 | 0.089992 | 0.022798 | -0.089511 | -0.022492 | 0.00048072 | 0.00030675 | 0.13473 | 0.13473 | 0.13473 | 0.99458 | -0.10364 | 0.98878 | -0.2155 | 37.0127
6 | 0.056143 | 0.01409 | -0.056093 | -0.014058 | 4.9471e-05 | 3.1419e-05 | 0.084004 | 0.084004 | 0.084004 | 0.99458 | -0.10364 | 0.99362 | -0.12214 | 23.0779
7 | 0.086497 | 0.021824 | -0.086258 | -0.021672 | 0.0002386 | 0.00015222 | 0.12998 | 0.12998 | 0.12998 | 0.99063 | -0.17897 | 0.98764 | -0.23675 | 35.7084
8 | 0.044393 | 0.011142 | -0.044351 | -0.011115 | 4.2567e-05 | 2.6916e-05 | 0.066762 | 0.066762 | 0.066762 | 0.98953 | -0.19984 | 0.9885 | -0.21997 | 18.3413
9 | 0.10692 | 0.027137 | -0.10639 | -0.026799 | 0.00052975 | 0.00033834 | 0.1609 | 0.1609 | 0.1609 | 0.98953 | -0.19984 | 0.98418 | -0.3034 | 44.2032
10 | 0.07225 | 0.018155 | -0.072164 | -0.0181 | 8.6498e-05 | 5.511e-05 | 0.10887 | 0.10887 | 0.10887 | 0.98764 | -0.23675 | 0.98635 | -0.26186 | 29.9098
11 | 0.014008 | 0.0035168 | -0.014001 | -0.003513 | 6.6562e-06 | 3.7504e-06 | 0.021107 | 0.021107 | 0.021107 | 0.98764 | -0.23675 | 0.98713 | -0.24671 | 5.7986
12 | 0.072164 | 0.0181 | -0.072127 | -0.018077 | 3.6297e-05 | 2.3126e-05 | 0.10887 | 0.10887 | 0.10887 | 0.98635 | -0.26186 | 0.98581 | -0.27242 | 29.9098
13 | 0.014001 | 0.003513 | -0.013988 | -0.0035058 | 1.2805e-05 | 7.2165e-06 | 0.021107 | 0.021107 | 0.021107 | 0.98713 | -0.24671 | 0.98614 | -0.26591 | 5.7987
14 | 0.052818 | 0.013267 | -0.052743 | -0.013219 | 7.5258e-05 | 4.7758e-05 | 0.079497 | 0.079497 | 0.079497 | 0.98878 | -0.2155 | 0.98724 | -0.2454 | 21.8397
15 | 0.036693 | 0.0092248 | -0.036633 | -0.009187 | 6.0073e-05 | 3.7774e-05 | 0.05523 | 0.05523 | 0.05523 | 0.98878 | -0.2155 | 0.98701 | -0.24984 | 15.1731
16 | 0.10639 | 0.026799 | -0.10631 | -0.026747 | 8.1724e-05 | 5.2196e-05 | 0.1609 | 0.1609 | 0.1609 | 0.98418 | -0.3034 | 0.98336 | -0.31948 | 44.2032
17 | 0.095177 | 0.023957 | -0.094904 | -0.023783 | 0.00027268 | 0.00017407 | 0.14406 | 0.14406 | 0.14406 | 0.98336 | -0.31948 | 0.98028 | -0.37961 | 39.5766
18 | 0.036633 | 0.009187 | -0.036617 | -0.0091772 | 1.5685e-05 | 9.8632e-06 | 0.05523 | 0.05523 | 0.05523 | 0.98701 | -0.24984 | 0.98655 | -0.25883 | 15.1731
19 | 0.0056223 | 0.001409 | -0.0056214 | -0.0014089 | 8.7661e-07 | 1.4571e-07 | 0.0084784 | 0.0084786 | 0.0084786 | 0.98675 | -0.25499 | 0.98658 | -0.25826 | 2.3293
20 | -0.0056223 | -0.001409 | 0.0056224 | 0.001409 | 1.2537e-07 | 2.0827e-08 | 0.0084784 | 0.0084784 | 0.0084784 | 0.98675 | -0.25499 | 0.98677 | -0.25452 | 2.3292
21 | -0.0056224 | -0.001409 | 0.0056234 | 0.0014092 | 1.015e-06 | 1.6848e-07 | 0.0084784 | 0.0084782 | 0.0084784 | 0.98677 | -0.25452 | 0.98697 | -0.25073 | 2.3292
22 | -0.011245 | -0.0028181 | 0.011248 | 0.0028196 | 2.8559e-06 | 1.4891e-06 | 0.016953 | 0.016953 | 0.016953 | 0.98697 | -0.25073 | 0.98724 | -0.2454 | 4.6575
23 | 0.0016358 | 0.00040841 | -0.0016356 | -0.00040926 | 1.7618e-07 | -8.4794e-07 | 0.0024826 | 0.0024829 | 0.0024829 | 0.98024 | -0.38032 | 0.98013 | -0.38259 | 0.68213
24 | -0.0016358 | -0.00040841 | 0.0016359 | 0.00040814 | 5.5627e-08 | -2.6783e-07 | 0.0024826 | 0.0024825 | 0.0024826 | 0.98024 | -0.38032 | 0.98028 | -0.37961 | 0.68203
25 | 0.0016356 | 0.00040926 | -0.0016355 | -0.00040989 | 1.3155e-07 | -6.328e-07 | 0.0024829 | 0.0024832 | 0.0024832 | 0.98013 | -0.38259 | 0.98004 | -0.38428 | 0.6822

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41058 | 0.10444

## res_load
| p_mw | q_mvar
0 | 0.0095092 | 0.0023832
1 | 0.012424 | 0.0031138
2 | 0.056093 | 0.014058
3 | 0.011129 | 0.0027893
4 | 0.044351 | 0.011115
5 | 0.072127 | 0.018077
6 | 0.013988 | 0.0035058
7 | 0.036617 | 0.0091772
8 | 0.0056214 | 0.0014089
9 | 0.0056214 | 0.0014089
10 | 0.041495 | 0.0104
11 | 0.093268 | 0.023375
12 | 0.0016355 | 0.00040989

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1