## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2228-28_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2228-28_0_3_node_4 | 0.4 | n |  | TRUE
2 | bus_LV_2228-28_0_3_node_16 | 0.4 | n |  | TRUE
3 | bus_LV_2228-28_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2228-28_0_3_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_2228-28_0_3_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_2228-28_0_3_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_2228-28_0_3_node_1 | 0.4 | n |  | TRUE
8 | bus_LV_2228-28_0_3_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_2228-28_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2228-28_0_3_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_2228-28_0_3_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_2228-28_0_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_2228-28_0_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2228-28_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2228-28_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2228-28_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2228-28_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2228-28_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2228-28_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2228-28_0_3_node_68 | 0.4 | n |  | TRUE
21 | bus_LV_2228-28_0_3_node_67 | 0.4 | n |  | TRUE
22 | bus_LV_2228-28_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2228-28_0_3_node_40 | 0.4 | n |  | TRUE
24 | bus_LV_2228-28_0_3_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_2228-28_0_3_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_2228-28_0_3_node_71 | 0.4 | n |  | TRUE
27 | bus_LV_2228-28_0_3_node_69 | 0.4 | n |  | TRUE
28 | bus_LV_2228-28_0_3_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_2228-28_0_3_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_2228-28_0_3_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2228-28_0_3_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_2228-28_0_3_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2228-28_0_3_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_2228-28_0_3_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2228-28_0_3_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2228-28_0_3_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_2228-28_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_2228-28_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_2228-28_0_3_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_2228-28_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_2228-28_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_2228-28_0_3_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_2228-28_0_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_2228-28_0_3_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_2228-28_0_3_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_2228-28_0_3_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_2228-28_0_3_node_74 | 0.4 | n |  | TRUE
48 | bus_LV_2228-28_0_3_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_2228-28_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_2228-28_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_2228-28_0_3_node_62 | 0.4 | n |  | TRUE
52 | bus_LV_2228-28_0_3_node_64 | 0.4 | n |  | TRUE
53 | bus_LV_2228-28_0_3_node_65 | 0.4 | n |  | TRUE
54 | bus_LV_2228-28_0_3_node_61 | 0.4 | n |  | TRUE
55 | bus_LV_2228-28_0_3_node_63 | 0.4 | n |  | TRUE
56 | bus_LV_2228-28_0_3_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_2228-28_0_3_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_2228-28_0_3_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_2228-28_0_3_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_2228-28_0_3_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_2228-28_0_3_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_2228-28_0_3_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_2228-28_0_3_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_2228-28_0_3_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_2228-28_0_3_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_2228-28_0_3_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2228-28_0_3_node_70 | 0.4 | n |  | TRUE
68 | bus_LV_2228-28_0_3_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_2228-28_0_3_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_2228-28_0_3_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_2228-28_0_3_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_2228-28_0_3_node_75 | 0.4 | n |  | TRUE
73 | bus_LV_2228-28_0_3_node_58 | 0.4 | n |  | TRUE
74 | bus_LV_2228-28_0_3_node_59 | 0.4 | n |  | TRUE
75 | bus_LV_2228-28_0_3_node_60 | 0.4 | n |  | TRUE
76 | bus_MV_376_0_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2228-28_0_3_load_0 | 0 | 0.0022787 | 0.0005711 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2228-28_0_3_load_4 | 1 | 0.0029587 | 0.00074152 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2228-28_0_3_load_16 | 2 | 0.003128 | 0.00078395 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2228-28_0_3_load_2 | 3 | 0.0025525 | 0.00063971 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2228-28_0_3_load_22 | 4 | 0.0035175 | 0.00088156 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2228-28_0_3_load_24 | 5 | 0.0035649 | 0.00089346 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2228-28_0_3_load_20 | 6 | 0.0028965 | 0.00072593 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2228-28_0_3_load_3 | 8 | 0.0036417 | 0.0009127 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2228-28_0_3_load_5 | 9 | 0.0034341 | 0.00086067 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2228-28_0_3_load_25 | 10 | 0.0027496 | 0.00068913 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2228-28_0_3_load_26 | 11 | 0.0058603 | 0.0014687 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2228-28_0_3_load_15 | 12 | 0.0043007 | 0.0010778 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2228-28_0_3_load_18 | 13 | 0.0029304 | 0.00073444 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2228-28_0_3_load_6 | 14 | 0.0063096 | 0.0015813 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2228-28_0_3_load_9 | 17 | 0.011451 | 0.0028698 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2228-28_0_3_load_10 | 18 | 0.0062004 | 0.001554 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2228-28_0_3_load_11 | 19 | 0.0048909 | 0.0012258 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2228-28_0_3_load_68 | 20 | 0.0027088 | 0.0006789 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2228-28_0_3_load_67 | 21 | 0.006411 | 0.0016067 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2228-28_0_3_load_12 | 22 | 0.0060811 | 0.0015241 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2228-28_0_3_load_40 | 23 | 0.0042951 | 0.0010764 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2228-28_0_3_load_41 | 24 | 0.0032403 | 0.0008121 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2228-28_0_3_load_37 | 25 | 0.0025687 | 0.00064377 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2228-28_0_3_load_71 | 26 | 0.0039399 | 0.00098742 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2228-28_0_3_load_69 | 27 | 0.0011385 | 0.00028533 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2228-28_0_3_load_13 | 28 | 0.0036535 | 0.00091565 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2228-28_0_3_load_14 | 29 | 0.0059694 | 0.0014961 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2228-28_0_3_load_32 | 30 | 0.0020338 | 0.00050972 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2228-28_0_3_load_23 | 32 | 0.0045576 | 0.0011423 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2228-28_0_3_load_21 | 33 | 0.0058393 | 0.0014635 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2228-28_0_3_load_19 | 34 | 0.0051239 | 0.0012842 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2228-28_0_3_load_17 | 35 | 0.0023415 | 0.00058683 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2228-28_0_3_load_27 | 36 | 0.0027788 | 0.00069644 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2228-28_0_3_load_30 | 39 | 0.0081986 | 0.0020548 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2228-28_0_3_load_31 | 40 | 0.0018232 | 0.00045695 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2228-28_0_3_load_73 | 42 | 0.002803 | 0.00070249 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2228-28_0_3_load_34 | 43 | 0.0018142 | 0.00045468 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2228-28_0_3_load_35 | 44 | 0.0044833 | 0.0011236 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2228-28_0_3_load_36 | 45 | 0.0041224 | 0.0010332 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2228-28_0_3_load_39 | 46 | 0.0021487 | 0.00053851 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2228-28_0_3_load_74 | 47 | 0.0020488 | 0.00051347 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2228-28_0_3_load_43 | 49 | 0.0028408 | 0.00071196 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2228-28_0_3_load_44 | 50 | 0.0029994 | 0.00075172 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2228-28_0_3_load_64 | 52 | 0.0025872 | 0.00064841 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2228-28_0_3_load_61 | 54 | 0.0040808 | 0.0010228 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2228-28_0_3_load_63 | 55 | 0.0016413 | 0.00041136 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2228-28_0_3_load_45 | 56 | 0.0017403 | 0.00043617 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2228-28_0_3_load_46 | 57 | 0.0022527 | 0.00056459 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2228-28_0_3_load_76 | 58 | 0.0021644 | 0.00054244 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2228-28_0_3_load_47 | 59 | 0.0016905 | 0.00042367 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2228-28_0_3_load_51 | 60 | 0.0023463 | 0.00058804 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2228-28_0_3_load_54 | 61 | 0.0017191 | 0.00043084 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2228-28_0_3_load_50 | 64 | 0.0046392 | 0.0011627 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2228-28_0_3_load_52 | 65 | 0.0084908 | 0.002128 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2228-28_0_3_load_53 | 66 | 0.0057939 | 0.0014521 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2228-28_0_3_load_55 | 68 | 0.0023471 | 0.00058823 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2228-28_0_3_load_56 | 70 | 0.0041746 | 0.0010462 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2228-28_0_3_load_57 | 71 | 0.0022089 | 0.00055361 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2228-28_0_3_load_75 | 72 | 0.0043407 | 0.0010879 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2228-28_0_3_load_58 | 73 | 0.0025857 | 0.00064804 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2228-28_0_3_load_59 | 74 | 0.0016395 | 0.0004109 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2228-28_0_3_load_60 | 75 | 0.0031262 | 0.00078349 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2228-28_0_3_line_0 |  | 0 | 1 | 0.050147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2228-28_0_3_line_1 |  | 1 | 2 | 0.017752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2228-28_0_3_line_2 |  | 1 | 3 | 0.0039985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2228-28_0_3_line_3 |  | 2 | 12 | 0.015038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2228-28_0_3_line_4 |  | 3 | 7 | 0.016501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2228-28_0_3_line_5 |  | 4 | 5 | 0.0068482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2228-28_0_3_line_6 |  | 4 | 6 | 0.015148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2228-28_0_3_line_7 |  | 5 | 10 | 0.012176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2228-28_0_3_line_8 |  | 6 | 13 | 0.0033545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2228-28_0_3_line_9 |  | 7 | 8 | 0.024892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2228-28_0_3_line_10 |  | 8 | 9 | 0.010548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2228-28_0_3_line_11 |  | 9 | 10 | 0.061582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2228-28_0_3_line_12 |  | 10 | 11 | 0.016591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2228-28_0_3_line_13 |  | 11 | 36 | 0.0033365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2228-28_0_3_line_14 |  | 12 | 29 | 0.011545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2228-28_0_3_line_15 |  | 13 | 35 | 0.020882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2228-28_0_3_line_16 |  | 14 | 15 | 0.014345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2228-28_0_3_line_17 |  | 14 | 16 | 0.01158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2228-28_0_3_line_18 |  | 15 | 17 | 0.017211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2228-28_0_3_line_19 |  | 16 | 18 | 0.0090012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2228-28_0_3_line_20 |  | 16 | 19 | 0.0115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2228-28_0_3_line_21 |  | 18 | 22 | 0.022719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2228-28_0_3_line_22 |  | 20 | 21 | 0.0056839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2228-28_0_3_line_23 |  | 21 | 69 | 0.010119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2228-28_0_3_line_24 |  | 22 | 28 | 0.0099717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2228-28_0_3_line_25 |  | 23 | 24 | 0.019975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2228-28_0_3_line_26 |  | 23 | 25 | 0.0093568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2228-28_0_3_line_27 |  | 24 | 48 | 0.0028089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2228-28_0_3_line_28 |  | 25 | 44 | 0.0011565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2228-28_0_3_line_29 |  | 26 | 27 | 0.011927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2228-28_0_3_line_30 |  | 27 | 67 | 0.0085729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2228-28_0_3_line_31 |  | 28 | 29 | 0.011869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2228-28_0_3_line_32 |  | 30 | 31 | 0.017637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2228-28_0_3_line_33 |  | 30 | 32 | 0.0009341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2228-28_0_3_line_34 |  | 31 | 43 | 0.026461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2228-28_0_3_line_35 |  | 31 | 44 | 0.018143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2228-28_0_3_line_36 |  | 32 | 33 | 0.016613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2228-28_0_3_line_37 |  | 33 | 34 | 0.0074584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2228-28_0_3_line_38 |  | 34 | 35 | 0.0074475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2228-28_0_3_line_39 |  | 36 | 37 | 0.017985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2228-28_0_3_line_40 |  | 37 | 38 | 0.0429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2228-28_0_3_line_41 |  | 38 | 39 | 0.049878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2228-28_0_3_line_42 |  | 38 | 40 | 0.027975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2228-28_0_3_line_43 |  | 39 | 41 | 0.021007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2228-28_0_3_line_44 |  | 41 | 42 | 0.021052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2228-28_0_3_line_45 |  | 42 | 47 | 0.015291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2228-28_0_3_line_46 |  | 43 | 45 | 7.8137e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2228-28_0_3_line_47 |  | 45 | 46 | 0.0099858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2228-28_0_3_line_48 |  | 47 | 72 | 0.0029012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2228-28_0_3_line_49 |  | 48 | 49 | 0.0053368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2228-28_0_3_line_50 |  | 48 | 50 | 0.013023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2228-28_0_3_line_51 |  | 49 | 51 | 0.030472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2228-28_0_3_line_52 |  | 50 | 52 | 0.0090105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2228-28_0_3_line_53 |  | 51 | 53 | 0.017292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2228-28_0_3_line_54 |  | 51 | 54 | 0.017593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2228-28_0_3_line_55 |  | 52 | 55 | 0.00033957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2228-28_0_3_line_56 |  | 53 | 69 | 0.017021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2228-28_0_3_line_57 |  | 53 | 66 | 0.020543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2228-28_0_3_line_58 |  | 54 | 74 | 0.009342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2228-28_0_3_line_59 |  | 56 | 57 | 0.006001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2228-28_0_3_line_60 |  | 56 | 58 | 0.021907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2228-28_0_3_line_61 |  | 57 | 59 | 0.0064614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2228-28_0_3_line_62 |  | 59 | 60 | 0.013001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2228-28_0_3_line_63 |  | 60 | 61 | 0.007078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2228-28_0_3_line_64 |  | 61 | 68 | 0.015968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2228-28_0_3_line_65 |  | 62 | 63 | 0.021621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2228-28_0_3_line_66 |  | 62 | 64 | 0.029584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2228-28_0_3_line_67 |  | 63 | 65 | 0.023682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2228-28_0_3_line_68 |  | 63 | 66 | 0.014864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2228-28_0_3_line_69 |  | 65 | 67 | 0.0082125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2228-28_0_3_line_70 |  | 68 | 70 | 0.023573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2228-28_0_3_line_71 |  | 70 | 71 | 0.010716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2228-28_0_3_line_72 |  | 71 | 72 | 0.017962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2228-28_0_3_line_73 |  | 73 | 74 | 0.0080532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2228-28_0_3_line_74 |  | 73 | 75 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2228-28_0_3_trafo_35 | 0.63 MVA 20/0.4 kV | 76 | 44 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2577163.0002 | 1182128.2383 | 2577145.9887 | 1182175.4119
1 | 2577163.0002 | 1182128.2383 | 2577147.8533 | 1182123.4235 | 2577146.0752 | 1182122.8836
2 | 2577163.0002 | 1182128.2383 | 2577166.8108 | 1182129.4496
3 | 2577131.6863 | 1182118.5145 | 2577146.0752 | 1182122.8836
4 | 2577181.105 | 1182137.159 | 2577178.3635 | 1182135.0572 | 2577174.289 | 1182131.8267 | 2577166.8108 | 1182129.4496
5 | 2577211.9629 | 1182050.0535 | 2577205.6136 | 1182047.4876
6 | 2577191.5687 | 1182041.8118 | 2577205.6136 | 1182047.4876
7 | 2577211.9629 | 1182050.0535 | 2577223.2515 | 1182054.6154
8 | 2577191.5687 | 1182041.8118 | 2577188.4586 | 1182040.5549
9 | 2577181.105 | 1182137.159 | 2577193.7452 | 1182124.0817 | 2577198.1775 | 1182119.051
10 | 2577207.4894 | 1182114.1462 | 2577203.1901 | 1182116.0192 | 2577198.1775 | 1182119.051
11 | 2577223.2515 | 1182054.6154 | 2577207.4894 | 1182114.1462
12 | 2577223.2515 | 1182054.6154 | 2577238.6335 | 1182060.8315
13 | 2577238.6335 | 1182060.8315 | 2577241.7269 | 1182062.0816
14 | 2577131.6863 | 1182118.5145 | 2577120.6393 | 1182115.1602
15 | 2577169.0976 | 1182032.7308 | 2577188.4586 | 1182040.5549
16 | 2577044.2757 | 1182093.1495 | 2577058.152 | 1182096.787
17 | 2577069.3532 | 1182099.7232 | 2577058.152 | 1182096.787
18 | 2577044.2757 | 1182093.1495 | 2577027.5785 | 1182088.9751
19 | 2577069.3532 | 1182099.7232 | 2577072.8309 | 1182100.6437 | 2577078.0016 | 1182102.2137
20 | 2577069.3532 | 1182099.7232 | 2577065.8235 | 1182110.6681
21 | 2577078.0016 | 1182102.2137 | 2577099.7407 | 1182108.8145
22 | 2577038.3403 | 1182007.1499 | 2577032.7476 | 1182006.1358
23 | 2577022.7909 | 1182004.3304 | 2577032.7476 | 1182006.1358
24 | 2577099.7407 | 1182108.8145 | 2577109.2822 | 1182111.7117
25 | 2577094.2827 | 1182010.0587 | 2577094.2827 | 1182010.0587 | 2577075.2145 | 1182004.1087
26 | 2577094.2827 | 1182010.0587 | 2577103.5573 | 1182011.296
27 | 2577072.5331 | 1182003.272 | 2577075.2145 | 1182004.1087
28 | 2577104.7036 | 1182011.449 | 2577103.5573 | 1182011.296
29 | 2576992.7743 | 1182019.9764 | 2576981.0769 | 1182017.6472
30 | 2576973.6838 | 1182013.6689 | 2576978.37 | 1182017.1082 | 2576981.0769 | 1182017.6472
31 | 2577120.6393 | 1182115.1602 | 2577109.2822 | 1182111.7117
32 | 2577122.6564 | 1182013.9631 | 2577139.0088 | 1182020.5714
33 | 2577139.8749 | 1182020.9214 | 2577139.0088 | 1182020.5714
34 | 2577122.6564 | 1182013.9631 | 2577131.8192 | 1181989.1396
35 | 2577122.6564 | 1182013.9631 | 2577122.2282 | 1182013.7868 | 2577104.7036 | 1182011.449
36 | 2577155.2775 | 1182027.1458 | 2577139.8749 | 1182020.9214
37 | 2577155.2775 | 1182027.1458 | 2577162.1926 | 1182029.9404
38 | 2577169.0976 | 1182032.7308 | 2577162.1926 | 1182029.9404
39 | 2577259.0696 | 1182066.6582 | 2577245.9407 | 1182063.7845 | 2577241.7269 | 1182062.0816
40 | 2577259.0696 | 1182066.6582 | 2577261.2983 | 1182060.402 | 2577261.2781 | 1182055.0994 | 2577257.7524 | 1182045.5967 | 2577252.3795 | 1182034.2669 | 2577248.1147 | 1182027.1572
41 | 2577248.1147 | 1182027.1572 | 2577242.9584 | 1182018.5613 | 2577230.4009 | 1181999.3881 | 2577219.7227 | 1181986.2449
42 | 2577248.1147 | 1182027.1572 | 2577244.1261 | 1182026.4387 | 2577226.3248 | 1182010.4574
43 | 2577206.8459 | 1181969.6514 | 2577214.5358 | 1181979.8607 | 2577219.7227 | 1181986.2449
44 | 2577206.8459 | 1181969.6514 | 2577201.3395 | 1181969.3945 | 2577187.1837 | 1181962.9851
45 | 2577187.1837 | 1181962.9851 | 2577185.5139 | 1181962.229 | 2577172.8529 | 1181957.6676
46 | 2577131.8219 | 1181989.1323 | 2577131.8192 | 1181989.1396
47 | 2577131.8219 | 1181989.1323 | 2577134.7253 | 1181981.2665 | 2577135.805 | 1181980.084
48 | 2577170.1234 | 1181956.6842 | 2577172.8529 | 1181957.6676
49 | 2577072.5331 | 1182003.272 | 2577067.438 | 1182001.6845
50 | 2577072.5331 | 1182003.272 | 2577074.8142 | 1181994.7922 | 2577075.9209 | 1181990.6969
51 | 2577038.3455 | 1181992.6201 | 2577067.438 | 1182001.6845
52 | 2577075.9209 | 1181990.6969 | 2577067.3466 | 1181987.9273
53 | 2577021.7943 | 1181987.4588 | 2577038.3455 | 1181992.6201
54 | 2577038.3455 | 1181992.6201 | 2577043.7657 | 1181975.8833
55 | 2577067.3466 | 1181987.9273 | 2577067.0235 | 1181987.8229
56 | 2577021.7943 | 1181987.4588 | 2577021.1902 | 1181993.1752 | 2577022.7909 | 1182004.3304
57 | 2577021.7943 | 1181987.4588 | 2577002.1841 | 1181981.339
58 | 2577046.6439 | 1181966.9957 | 2577043.7657 | 1181975.8833
59 | 2577074.0395 | 1181927.5035 | 2577079.7292 | 1181929.411
60 | 2577074.0395 | 1181927.5035 | 2577070.2273 | 1181905.9303
61 | 2577085.8556 | 1181931.4649 | 2577079.7292 | 1181929.411
62 | 2577085.8556 | 1181931.4649 | 2577098.1824 | 1181935.5974
63 | 2577104.8933 | 1181937.8473 | 2577098.1824 | 1181935.5974
64 | 2577104.8933 | 1181937.8473 | 2577114.6957 | 1181941.1335 | 2577120.3007 | 1181941.6613
65 | 2576982.1715 | 1181965.3444 | 2576983.9609 | 1181968.0056 | 2576986.7546 | 1181975.6766 | 2576988.9846 | 1181985.6843
66 | 2576952.8035 | 1181961.1333 | 2576982.1715 | 1181965.3444
67 | 2576988.9846 | 1181985.6843 | 2576977.6236 | 1182006.4632
68 | 2576988.9846 | 1181985.6843 | 2576989.3486 | 1181985.027 | 2576994.3215 | 1181981.606 | 2576999.7312 | 1181980.5735 | 2577002.1841 | 1181981.339
69 | 2576973.6838 | 1182013.6689 | 2576977.6236 | 1182006.4632
70 | 2577143.0828 | 1181947.1381 | 2577129.1019 | 1181942.4901 | 2577120.3007 | 1181941.6613
71 | 2577143.0828 | 1181947.1381 | 2577150.127 | 1181949.4799 | 2577153.2246 | 1181950.596
72 | 2577170.1234 | 1181956.6842 | 2577153.2246 | 1181950.596
73 | 2577049.1251 | 1181959.3343 | 2577046.6439 | 1181966.9957
74 | 2577049.1251 | 1181959.3343 | 2577051.0304 | 1181953.451 | 2577036.0104 | 1181948.3722

## bus_geodata
| x | y | coords
0 | 2577145.9887 | 1182175.4119
1 | 2577163.0002 | 1182128.2383
2 | 2577146.0752 | 1182122.8836
3 | 2577166.8108 | 1182129.4496
4 | 2577205.6136 | 1182047.4876
5 | 2577211.9629 | 1182050.0535
6 | 2577191.5687 | 1182041.8118
7 | 2577181.105 | 1182137.159
8 | 2577198.1775 | 1182119.051
9 | 2577207.4894 | 1182114.1462
10 | 2577223.2515 | 1182054.6154
11 | 2577238.6335 | 1182060.8315
12 | 2577131.6863 | 1182118.5145
13 | 2577188.4586 | 1182040.5549
14 | 2577058.152 | 1182096.787
15 | 2577044.2757 | 1182093.1495
16 | 2577069.3532 | 1182099.7232
17 | 2577027.5785 | 1182088.975
18 | 2577078.0016 | 1182102.2137
19 | 2577065.8235 | 1182110.6681
20 | 2577038.3403 | 1182007.1499
21 | 2577032.7476 | 1182006.1358
22 | 2577099.7407 | 1182108.8145
23 | 2577094.2827 | 1182010.0587
24 | 2577075.2145 | 1182004.1087
25 | 2577103.5573 | 1182011.296
26 | 2576992.7743 | 1182019.9764
27 | 2576981.0769 | 1182017.6472
28 | 2577109.2822 | 1182111.7117
29 | 2577120.6393 | 1182115.1602
30 | 2577139.0088 | 1182020.5714
31 | 2577122.6564 | 1182013.9631
32 | 2577139.8749 | 1182020.9214
33 | 2577155.2775 | 1182027.1458
34 | 2577162.1926 | 1182029.9404
35 | 2577169.0976 | 1182032.7308
36 | 2577241.7269 | 1182062.0816
37 | 2577259.0696 | 1182066.6582
38 | 2577248.1147 | 1182027.1572
39 | 2577219.7227 | 1181986.2449
40 | 2577226.3248 | 1182010.4574
41 | 2577206.8459 | 1181969.6514
42 | 2577187.1837 | 1181962.9851
43 | 2577131.8192 | 1181989.1396
44 | 2577104.7036 | 1182011.4489
45 | 2577131.8219 | 1181989.1323
46 | 2577135.805 | 1181980.084
47 | 2577172.8529 | 1181957.6676
48 | 2577072.5331 | 1182003.272
49 | 2577067.438 | 1182001.6845
50 | 2577075.9209 | 1181990.6969
51 | 2577038.3455 | 1181992.6201
52 | 2577067.3466 | 1181987.9273
53 | 2577021.7943 | 1181987.4588
54 | 2577043.7657 | 1181975.8833
55 | 2577067.0235 | 1181987.8229
56 | 2577074.0395 | 1181927.5035
57 | 2577079.7292 | 1181929.411
58 | 2577070.2273 | 1181905.9303
59 | 2577085.8556 | 1181931.4649
60 | 2577098.1824 | 1181935.5974
61 | 2577104.8933 | 1181937.8473
62 | 2576982.1715 | 1181965.3444
63 | 2576988.9846 | 1181985.6843
64 | 2576952.8035 | 1181961.1333
65 | 2576977.6236 | 1182006.4632
66 | 2577002.1841 | 1181981.339
67 | 2576973.6838 | 1182013.6689
68 | 2577120.3007 | 1181941.6613
69 | 2577022.7909 | 1182004.3304
70 | 2577143.0828 | 1181947.1381
71 | 2577153.2246 | 1181950.596
72 | 2577170.1234 | 1181956.6842
73 | 2577049.1251 | 1181959.3343
74 | 2577046.6439 | 1181966.9957
75 | 2577036.0104 | 1181948.3722
76 | 2577122.6564 | 1182013.9631

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98056 | -0.37338 | 0.0022787 | 0.0005711
1 | 0.98067 | -0.3713 | 0.0029587 | 0.00074152
2 | 0.97981 | -0.38805 | 0.003128 | 0.00078395
3 | 0.98088 | -0.36716 | 0.0025525 | 0.00063971
4 | 0.98971 | -0.19602 | 0.0035175 | 0.00088156
5 | 0.98894 | -0.21086 | 0.0035649 | 0.00089346
6 | 0.99147 | -0.16233 | 0.0028965 | 0.00072593
7 | 0.98179 | -0.34931 | 0 | 0
8 | 0.98317 | -0.32244 | 0.0036417 | 0.0009127
9 | 0.98379 | -0.31038 | 0.0034341 | 0.00086067
10 | 0.98761 | -0.23652 | 0.0027496 | 0.00068913
11 | 0.98687 | -0.25091 | 0.0058603 | 0.0014687
12 | 0.97913 | -0.40139 | 0.0043007 | 0.0010778
13 | 0.99186 | -0.15471 | 0.0029304 | 0.00073444
14 | 0.97692 | -0.44487 | 0.0063096 | 0.0015813
15 | 0.97676 | -0.44787 | 0 | 0
16 | 0.97711 | -0.44111 | 0 | 0
17 | 0.97658 | -0.45147 | 0.011451 | 0.0028698
18 | 0.9773 | -0.43739 | 0.0062004 | 0.001554
19 | 0.97705 | -0.44214 | 0.0048909 | 0.0012258
20 | 0.99598 | -0.077222 | 0.0027088 | 0.0006789
21 | 0.996 | -0.076951 | 0.006411 | 0.0016067
22 | 0.9779 | -0.42544 | 0.0060811 | 0.0015241
23 | 0.9994 | -0.011451 | 0.0042951 | 0.0010764
24 | 0.99835 | -0.031645 | 0.0032403 | 0.0008121
25 | 0.99993 | -0.001305 | 0.0025687 | 0.00064377
26 | 0.99511 | -0.094008 | 0.0039399 | 0.00098742
27 | 0.99516 | -0.093181 | 0.0011385 | 0.00028533
28 | 0.97823 | -0.41909 | 0.0036535 | 0.00091565
29 | 0.97865 | -0.41075 | 0.0059694 | 0.0014961
30 | 0.99744 | -0.048464 | 0.0020338 | 0.00050972
31 | 0.99867 | -0.025176 | 0 | 0
32 | 0.99738 | -0.049682 | 0.0045576 | 0.0011423
33 | 0.99627 | -0.070712 | 0.0058393 | 0.0014635
34 | 0.99531 | -0.088868 | 0.0051239 | 0.0012842
35 | 0.99439 | -0.10636 | 0.0023415 | 0.00058683
36 | 0.98674 | -0.25346 | 0.0027788 | 0.00069644
37 | 0.98607 | -0.2663 | 0 | 0
38 | 0.98449 | -0.29701 | 0 | 0
39 | 0.98274 | -0.33119 | 0.0081986 | 0.0020548
40 | 0.98445 | -0.29793 | 0.0018232 | 0.00045695
41 | 0.98216 | -0.34251 | 0 | 0
42 | 0.98158 | -0.35387 | 0.002803 | 0.00070249
43 | 0.99847 | -0.028915 | 0.0018142 | 0.00045468
44 | 1 | 0 | -0.22793 | -0.057695
45 | 0.99847 | -0.028916 | 0.0041224 | 0.0010332
46 | 0.99846 | -0.029291 | 0.0021487 | 0.00053851
47 | 0.9812 | -0.36135 | 0.0020488 | 0.00051347
48 | 0.99821 | -0.034329 | 0 | 0
49 | 0.99798 | -0.038755 | 0.0028408 | 0.00071196
50 | 0.99813 | -0.035975 | 0.0029994 | 0.00075172
51 | 0.99674 | -0.062548 | 0 | 0
52 | 0.99809 | -0.036642 | 0.0025872 | 0.00064841
53 | 0.99622 | -0.072603 | 0 | 0
54 | 0.99656 | -0.066077 | 0.0040808 | 0.0010228
55 | 0.99809 | -0.036652 | 0.0016413 | 0.00041136
56 | 0.9799 | -0.38682 | 0.0017403 | 0.00043617
57 | 0.97992 | -0.38639 | 0.0022527 | 0.00056459
58 | 0.97985 | -0.38768 | 0.0021644 | 0.00054244
59 | 0.97996 | -0.38567 | 0.0016905 | 0.00042367
60 | 0.98005 | -0.38382 | 0.0023463 | 0.00058804
61 | 0.98012 | -0.38251 | 0.0017191 | 0.00043084
62 | 0.99544 | -0.087792 | 0 | 0
63 | 0.99553 | -0.086027 | 0 | 0
64 | 0.99531 | -0.090207 | 0.0046392 | 0.0011627
65 | 0.99523 | -0.091681 | 0.0084908 | 0.002128
66 | 0.99577 | -0.081268 | 0.0057939 | 0.0014521
67 | 0.9952 | -0.092415 | 0 | 0
68 | 0.98029 | -0.37906 | 0.0023471 | 0.00058823
69 | 0.99608 | -0.07533 | 0 | 0
70 | 0.9806 | -0.37296 | 0.0041746 | 0.0010462
71 | 0.98079 | -0.36938 | 0.0022089 | 0.00055361
72 | 0.98113 | -0.36266 | 0.0043407 | 0.0010879
73 | 0.99646 | -0.068091 | 0.0025857 | 0.00064804
74 | 0.9965 | -0.067283 | 0.0016395 | 0.0004109
75 | 0.99639 | -0.0693 | 0.0031262 | 0.00078349
76 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0022787 | -0.0005711 | 0.0022789 | 0.00057061 | 2.2485e-07 | -4.8873e-07 | 0.003458 | 0.0034577 | 0.003458 | 0.98056 | -0.37338 | 0.98067 | -0.3713 | 0.94999
1 | 0.052131 | 0.01312 | -0.052089 | -0.013094 | 4.1673e-05 | 2.6447e-05 | 0.07912 | 0.07912 | 0.07912 | 0.98067 | -0.3713 | 0.97981 | -0.38805 | 21.7363
2 | -0.057368 | -0.014432 | 0.05738 | 0.01444 | 1.1367e-05 | 7.2243e-06 | 0.087067 | 0.087067 | 0.087067 | 0.98067 | -0.3713 | 0.98088 | -0.36716 | 23.9196
3 | 0.048961 | 0.01231 | -0.04893 | -0.01229 | 3.1189e-05 | 1.9772e-05 | 0.07437 | 0.07437 | 0.07437 | 0.97981 | -0.38805 | 0.97913 | -0.40139 | 20.4313
4 | -0.059932 | -0.015079 | 0.059983 | 0.015112 | 5.1174e-05 | 3.2543e-05 | 0.090939 | 0.090939 | 0.090939 | 0.98088 | -0.36716 | 0.98179 | -0.34931 | 24.9834
5 | 0.1227 | 0.031149 | -0.12262 | -0.031093 | 8.7536e-05 | 5.5935e-05 | 0.18462 | 0.18462 | 0.18462 | 0.98971 | -0.19602 | 0.98894 | -0.21086 | 50.721
6 | -0.12622 | -0.032031 | 0.12643 | 0.032162 | 0.00020488 | 0.00013093 | 0.18991 | 0.18991 | 0.18991 | 0.98971 | -0.19602 | 0.99147 | -0.16233 | 52.1738
7 | 0.11905 | 0.0302 | -0.1189 | -0.030106 | 0.00014672 | 9.3744e-05 | 0.17926 | 0.17926 | 0.17926 | 0.98894 | -0.21086 | 0.98761 | -0.23652 | 49.2474
8 | -0.12932 | -0.032888 | 0.12937 | 0.032918 | 4.7471e-05 | 3.0338e-05 | 0.19426 | 0.19426 | 0.19426 | 0.99147 | -0.16233 | 0.99186 | -0.15471 | 53.3681
9 | -0.059983 | -0.015112 | 0.06006 | 0.015161 | 7.7197e-05 | 4.9091e-05 | 0.090939 | 0.090939 | 0.090939 | 0.98179 | -0.34931 | 0.98317 | -0.32244 | 24.9833
10 | -0.063702 | -0.016074 | 0.063739 | 0.016097 | 3.6796e-05 | 2.3416e-05 | 0.096451 | 0.096451 | 0.096451 | 0.98317 | -0.32244 | 0.98379 | -0.31038 | 26.4975
11 | -0.067173 | -0.016958 | 0.067412 | 0.01711 | 0.00023859 | 0.00015191 | 0.10165 | 0.10164 | 0.10165 | 0.98379 | -0.31038 | 0.98761 | -0.23652 | 27.9245
12 | 0.048743 | 0.012307 | -0.048709 | -0.012286 | 3.3585e-05 | 2.1282e-05 | 0.073473 | 0.073473 | 0.073473 | 0.98761 | -0.23652 | 0.98687 | -0.25091 | 20.1849
13 | 0.042849 | 0.010817 | -0.042844 | -0.010814 | 5.2273e-06 | 3.3029e-06 | 0.064637 | 0.064637 | 0.064637 | 0.98687 | -0.25091 | 0.98674 | -0.25346 | 17.7573
14 | 0.044629 | 0.011212 | -0.044609 | -0.0112 | 1.9921e-05 | 1.2605e-05 | 0.067834 | 0.067834 | 0.067834 | 0.97913 | -0.40139 | 0.97865 | -0.41075 | 18.6357
15 | -0.1323 | -0.033653 | 0.13261 | 0.03385 | 0.00030904 | 0.00019751 | 0.19866 | 0.19866 | 0.19866 | 0.99186 | -0.15471 | 0.99439 | -0.10636 | 54.5758
16 | 0.011454 | 0.0028717 | -0.011453 | -0.0028708 | 1.6375e-06 | 8.6844e-07 | 0.017447 | 0.017447 | 0.017447 | 0.97692 | -0.44487 | 0.97676 | -0.44787 | 4.7932
17 | -0.017764 | -0.004453 | 0.017767 | 0.0044549 | 3.1791e-06 | 1.8896e-06 | 0.027058 | 0.027058 | 0.027058 | 0.97692 | -0.44487 | 0.97711 | -0.44111 | 7.4335
18 | 0.011453 | 0.0028708 | -0.011451 | -0.0028698 | 1.9647e-06 | 1.042e-06 | 0.017447 | 0.017447 | 0.017447 | 0.97676 | -0.44787 | 0.97658 | -0.45147 | 4.7932
19 | -0.022658 | -0.0056807 | 0.022662 | 0.0056832 | 4.0191e-06 | 2.4595e-06 | 0.034506 | 0.034506 | 0.034506 | 0.97711 | -0.44111 | 0.9773 | -0.43739 | 9.4798
20 | 0.0048912 | 0.0012258 | -0.0048909 | -0.0012258 | 2.3927e-07 | 9.0965e-09 | 0.0074486 | 0.0074487 | 0.0074487 | 0.97711 | -0.44111 | 0.97705 | -0.44214 | 2.0463
21 | -0.028863 | -0.0072372 | 0.028879 | 0.0072474 | 1.6454e-05 | 1.0246e-05 | 0.043947 | 0.043947 | 0.043947 | 0.9773 | -0.43739 | 0.9779 | -0.42544 | 12.0734
22 | -0.0027088 | -0.0006789 | 0.0027089 | 0.00067885 | 3.491e-08 | -5.1629e-08 | 0.0040471 | 0.004047 | 0.0040471 | 0.99598 | -0.077222 | 0.996 | -0.076951 | 1.1118
23 | -0.0091199 | -0.0022856 | 0.0091206 | 0.0022859 | 7.0444e-07 | 3.1914e-07 | 0.013625 | 0.013625 | 0.013625 | 0.996 | -0.076951 | 0.99608 | -0.07533 | 3.7431
24 | -0.03496 | -0.0087715 | 0.034971 | 0.0087781 | 1.0583e-05 | 6.6482e-06 | 0.0532 | 0.0532 | 0.0532 | 0.9779 | -0.42544 | 0.97823 | -0.41909 | 14.6154
25 | 0.058027 | 0.014603 | -0.057971 | -0.014567 | 5.594e-05 | 3.554e-05 | 0.086418 | 0.086418 | 0.086418 | 0.9994 | -0.011451 | 0.99835 | -0.031645 | 23.7413
26 | -0.062322 | -0.015679 | 0.062353 | 0.015698 | 3.0226e-05 | 1.9222e-05 | 0.092813 | 0.092813 | 0.092813 | 0.9994 | -0.011451 | 0.99993 | -0.001305 | 25.4981
27 | 0.054731 | 0.013755 | -0.054724 | -0.013751 | 7.0117e-06 | 4.4508e-06 | 0.081589 | 0.081589 | 0.081589 | 0.99835 | -0.031645 | 0.99821 | -0.034329 | 22.4145
28 | -0.064921 | -0.016342 | 0.064925 | 0.016345 | 4.0499e-06 | 2.5768e-06 | 0.096636 | 0.096636 | 0.096636 | 0.99993 | -0.001305 | 1 | 0 | 26.5482
29 | -0.0039399 | -0.00098742 | 0.00394 | 0.00098737 | 1.5524e-07 | -5.5605e-08 | 0.0058914 | 0.0058913 | 0.0058914 | 0.99511 | -0.094008 | 0.99516 | -0.093181 | 1.6185
30 | -0.0050785 | -0.0012727 | 0.0050787 | 0.0012727 | 1.8538e-07 | 7.2538e-09 | 0.0075936 | 0.0075936 | 0.0075936 | 0.99516 | -0.093181 | 0.9952 | -0.092415 | 2.0862
31 | -0.038624 | -0.0096938 | 0.03864 | 0.0097035 | 1.5367e-05 | 9.6856e-06 | 0.058758 | 0.058758 | 0.058758 | 0.97823 | -0.41909 | 0.97865 | -0.41075 | 16.1422
32 | -0.1529 | -0.039089 | 0.15307 | 0.039199 | 0.00017248 | 0.00010992 | 0.22837 | 0.22837 | 0.22837 | 0.99744 | -0.048464 | 0.99867 | -0.025176 | 31.3702
33 | 0.15087 | 0.038579 | -0.15086 | -0.038573 | 8.8936e-06 | 5.6675e-06 | 0.22534 | 0.22534 | 0.22534 | 0.99744 | -0.048464 | 0.99738 | -0.049682 | 30.9534
34 | 0.0080867 | 0.0020268 | -0.0080853 | -0.0020262 | 1.4406e-06 | 5.7585e-07 | 0.012049 | 0.012049 | 0.012049 | 0.99867 | -0.025176 | 0.99847 | -0.028915 | 3.3103
35 | -0.16116 | -0.041225 | 0.16136 | 0.041351 | 0.00019664 | 0.00012537 | 0.24042 | 0.24042 | 0.24042 | 0.99867 | -0.025176 | 1 | 0 | 33.0252
36 | 0.1463 | 0.037431 | -0.14615 | -0.037336 | 0.00014877 | 9.4779e-05 | 0.21854 | 0.21854 | 0.21854 | 0.99738 | -0.049682 | 0.99627 | -0.070712 | 30.0194
37 | 0.14031 | 0.035873 | -0.14019 | -0.035794 | 0.00012313 | 7.8707e-05 | 0.20982 | 0.20982 | 0.20982 | 0.99627 | -0.070712 | 0.99531 | -0.088868 | 57.6428
38 | 0.13506 | 0.03451 | -0.13495 | -0.034437 | 0.00011414 | 7.2952e-05 | 0.20216 | 0.20216 | 0.20216 | 0.99531 | -0.088868 | 0.99439 | -0.10636 | 55.5384
39 | 0.040065 | 0.010118 | -0.04004 | -0.010102 | 2.4642e-05 | 1.5541e-05 | 0.060446 | 0.060446 | 0.060446 | 0.98674 | -0.25346 | 0.98607 | -0.2663 | 16.6061
40 | 0.04004 | 0.010102 | -0.039982 | -0.010065 | 5.878e-05 | 3.7073e-05 | 0.060446 | 0.060446 | 0.060446 | 0.98607 | -0.2663 | 0.98449 | -0.29701 | 16.6062
41 | 0.038158 | 0.0096085 | -0.038096 | -0.0095693 | 6.2252e-05 | 3.9208e-05 | 0.057691 | 0.057691 | 0.057691 | 0.98449 | -0.29701 | 0.98274 | -0.33119 | 15.8492
42 | 0.0018233 | 0.00045664 | -0.0018232 | -0.00045695 | 7.9673e-08 | -3.0471e-07 | 0.0027558 | 0.0027559 | 0.0027559 | 0.98449 | -0.29701 | 0.98445 | -0.29793 | 0.75711
43 | 0.029897 | 0.0075145 | -0.029881 | -0.0075044 | 1.6149e-05 | 1.007e-05 | 0.045277 | 0.045277 | 0.045277 | 0.98274 | -0.33119 | 0.98216 | -0.34251 | 12.4388
44 | 0.029881 | 0.0075044 | -0.029865 | -0.0074943 | 1.6184e-05 | 1.0091e-05 | 0.045277 | 0.045277 | 0.045277 | 0.98216 | -0.34251 | 0.98158 | -0.35387 | 12.4388
45 | 0.027062 | 0.0067919 | -0.027053 | -0.0067859 | 9.652e-06 | 5.9841e-06 | 0.041028 | 0.041028 | 0.041028 | 0.98158 | -0.35387 | 0.9812 | -0.36135 | 11.2715
46 | 0.0062711 | 0.0015716 | -0.0062711 | -0.0015716 | 2.5586e-10 | 4.7553e-11 | 0.0093457 | 0.0093457 | 0.0093457 | 0.99847 | -0.028915 | 0.99847 | -0.028916 | 2.5675
47 | 0.0021487 | 0.0005384 | -0.0021487 | -0.00053851 | 3.8398e-08 | -1.0603e-07 | 0.0032022 | 0.0032022 | 0.0032022 | 0.99847 | -0.028916 | 0.99846 | -0.029291 | 0.87973
48 | 0.025004 | 0.0062724 | -0.025002 | -0.0062714 | 1.5645e-06 | 9.6463e-07 | 0.037921 | 0.037921 | 0.037921 | 0.9812 | -0.36135 | 0.98113 | -0.36266 | 10.4179
49 | 0.047495 | 0.011939 | -0.047485 | -0.011933 | 1.0035e-05 | 6.3529e-06 | 0.070813 | 0.070813 | 0.070813 | 0.99821 | -0.034329 | 0.99798 | -0.038755 | 19.4542
50 | 0.0072286 | 0.0018116 | -0.007228 | -0.0018114 | 5.6707e-07 | 1.9269e-07 | 0.010776 | 0.010776 | 0.010776 | 0.99821 | -0.034329 | 0.99813 | -0.035975 | 2.9603
51 | 0.044645 | 0.011221 | -0.044594 | -0.011189 | 5.0651e-05 | 3.2019e-05 | 0.066577 | 0.066578 | 0.066578 | 0.99798 | -0.038755 | 0.99674 | -0.062548 | 18.2905
52 | 0.0042286 | 0.0010597 | -0.0042285 | -0.0010598 | 1.3428e-07 | -3.1823e-08 | 0.0063041 | 0.0063041 | 0.0063041 | 0.99813 | -0.035975 | 0.99809 | -0.036642 | 1.7319
53 | 0.033159 | 0.0083224 | -0.033143 | -0.0083124 | 1.5893e-05 | 9.9462e-06 | 0.049506 | 0.049507 | 0.049507 | 0.99674 | -0.062548 | 0.99622 | -0.072603 | 13.6007
54 | 0.011435 | 0.0028662 | -0.011433 | -0.0028652 | 1.9226e-06 | 1.0012e-06 | 0.017071 | 0.017071 | 0.017071 | 0.99674 | -0.062548 | 0.99656 | -0.066077 | 4.6899
55 | 0.0016413 | 0.00041135 | -0.0016413 | -0.00041136 | 7.6281e-10 | -3.9496e-09 | 0.002447 | 0.002447 | 0.002447 | 0.99809 | -0.036642 | 0.99809 | -0.036652 | 0.67225
56 | 0.0091217 | 0.0022864 | -0.0091206 | -0.0022859 | 1.1849e-06 | 5.3675e-07 | 0.013625 | 0.013625 | 0.013625 | 0.99622 | -0.072603 | 0.99608 | -0.07533 | 3.7431
57 | 0.024021 | 0.006026 | -0.024011 | -0.0060199 | 9.9184e-06 | 6.0804e-06 | 0.035882 | 0.035882 | 0.035882 | 0.99622 | -0.072603 | 0.99577 | -0.081268 | 9.8576
58 | 0.0073522 | 0.0018424 | -0.0073518 | -0.0018423 | 4.2219e-07 | 1.4849e-07 | 0.010978 | 0.010978 | 0.010978 | 0.99656 | -0.066077 | 0.9965 | -0.067283 | 3.0159
59 | -0.0039048 | -0.00097839 | 0.0039049 | 0.00097837 | 7.912e-08 | -2.496e-08 | 0.0059295 | 0.0059295 | 0.0059295 | 0.9799 | -0.38682 | 0.97992 | -0.38639 | 1.629
60 | 0.0021644 | 0.00054222 | -0.0021644 | -0.00054244 | 8.8749e-08 | -2.1916e-07 | 0.0032867 | 0.0032868 | 0.0032868 | 0.9799 | -0.38682 | 0.97985 | -0.38768 | 0.90297
61 | -0.0061576 | -0.001543 | 0.0061578 | 0.001543 | 2.1184e-07 | 5.4175e-08 | 0.0093503 | 0.0093502 | 0.0093503 | 0.97992 | -0.38639 | 0.97996 | -0.38567 | 2.5688
62 | -0.0078483 | -0.0019667 | 0.007849 | 0.001967 | 6.9239e-07 | 2.7932e-07 | 0.011917 | 0.011917 | 0.011917 | 0.97996 | -0.38567 | 0.98005 | -0.38382 | 3.2739
63 | -0.010195 | -0.002555 | 0.010196 | 0.0025553 | 6.36e-07 | 3.1784e-07 | 0.01548 | 0.015479 | 0.01548 | 0.98005 | -0.38382 | 0.98012 | -0.38251 | 4.2526
64 | -0.011915 | -0.0029862 | 0.011917 | 0.0029872 | 1.9595e-06 | 1.0528e-06 | 0.018089 | 0.018089 | 0.018089 | 0.98012 | -0.38251 | 0.98029 | -0.37906 | 4.9696
65 | -0.0046397 | -0.0011627 | 0.0046401 | 0.0011626 | 3.9e-07 | -3.1492e-08 | 0.0069356 | 0.0069355 | 0.0069356 | 0.99544 | -0.087792 | 0.99553 | -0.086027 | 1.9054
66 | 0.0046397 | 0.0011627 | -0.0046392 | -0.0011627 | 5.3366e-07 | -4.2996e-08 | 0.0069356 | 0.0069357 | 0.0069357 | 0.99544 | -0.087792 | 0.99531 | -0.090207 | 1.9054
67 | 0.013573 | 0.0034027 | -0.01357 | -0.0034007 | 3.6555e-06 | 2.0317e-06 | 0.020288 | 0.020288 | 0.020288 | 0.99553 | -0.086027 | 0.99523 | -0.091681 | 5.5738
68 | -0.018213 | -0.0045654 | 0.018218 | 0.0045678 | 4.1312e-06 | 2.4506e-06 | 0.027224 | 0.027224 | 0.027224 | 0.99553 | -0.086027 | 0.99577 | -0.081268 | 7.4791
69 | 0.0050789 | 0.0012727 | -0.0050787 | -0.0012727 | 1.7758e-07 | 6.9393e-09 | 0.0075936 | 0.0075936 | 0.0075936 | 0.99523 | -0.091681 | 0.9952 | -0.092415 | 2.0862
70 | -0.014264 | -0.0035754 | 0.014268 | 0.0035778 | 4.1443e-06 | 2.355e-06 | 0.021652 | 0.021652 | 0.021652 | 0.98029 | -0.37906 | 0.9806 | -0.37296 | 5.9484
71 | -0.018443 | -0.004624 | 0.018446 | 0.0046259 | 3.1474e-06 | 1.8791e-06 | 0.027987 | 0.027987 | 0.027987 | 0.9806 | -0.37296 | 0.98079 | -0.36938 | 7.6886
72 | -0.020655 | -0.0051795 | 0.020661 | 0.0051835 | 6.6149e-06 | 4.0068e-06 | 0.031338 | 0.031338 | 0.031338 | 0.98079 | -0.36938 | 0.98113 | -0.36266 | 8.6093
73 | -0.0057121 | -0.0014314 | 0.0057123 | 0.0014314 | 2.1972e-07 | 3.5713e-08 | 0.0085298 | 0.0085297 | 0.0085298 | 0.99646 | -0.068091 | 0.9965 | -0.067283 | 2.3433
74 | 0.0031263 | 0.00078332 | -0.0031262 | -0.00078349 | 1.8013e-07 | -1.7179e-07 | 0.0046685 | 0.0046686 | 0.0046686 | 0.99646 | -0.068091 | 0.99639 | -0.0693 | 1.2826

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23241 | 0.058819

## res_load
| p_mw | q_mvar
0 | 0.0022787 | 0.0005711
1 | 0.0029587 | 0.00074152
2 | 0.003128 | 0.00078395
3 | 0.0025525 | 0.00063971
4 | 0.0035175 | 0.00088156
5 | 0.0035649 | 0.00089346
6 | 0.0028965 | 0.00072593
7 | 0.0036417 | 0.0009127
8 | 0.0034341 | 0.00086067
9 | 0.0027496 | 0.00068913
10 | 0.0058603 | 0.0014687
11 | 0.0043007 | 0.0010778
12 | 0.0029304 | 0.00073444
13 | 0.0063096 | 0.0015813
14 | 0.011451 | 0.0028698
15 | 0.0062004 | 0.001554
16 | 0.0048909 | 0.0012258
17 | 0.0027088 | 0.0006789
18 | 0.006411 | 0.0016067
19 | 0.0060811 | 0.0015241
20 | 0.0042951 | 0.0010764
21 | 0.0032403 | 0.0008121
22 | 0.0025687 | 0.00064377
23 | 0.0039399 | 0.00098742
24 | 0.0011385 | 0.00028533
25 | 0.0036535 | 0.00091565
26 | 0.0059694 | 0.0014961
27 | 0.0020338 | 0.00050972
28 | 0.0045576 | 0.0011423
29 | 0.0058393 | 0.0014635
30 | 0.0051239 | 0.0012842
31 | 0.0023415 | 0.00058683
32 | 0.0027788 | 0.00069644
33 | 0.0081986 | 0.0020548
34 | 0.0018232 | 0.00045695
35 | 0.002803 | 0.00070249
36 | 0.0018142 | 0.00045468
37 | 0.0044833 | 0.0011236
38 | 0.0041224 | 0.0010332
39 | 0.0021487 | 0.00053851
40 | 0.0020488 | 0.00051347
41 | 0.0028408 | 0.00071196
42 | 0.0029994 | 0.00075172
43 | 0.0025872 | 0.00064841
44 | 0.0040808 | 0.0010228
45 | 0.0016413 | 0.00041136
46 | 0.0017403 | 0.00043617
47 | 0.0022527 | 0.00056459
48 | 0.0021644 | 0.00054244
49 | 0.0016905 | 0.00042367
50 | 0.0023463 | 0.00058804
51 | 0.0017191 | 0.00043084
52 | 0.0046392 | 0.0011627
53 | 0.0084908 | 0.002128
54 | 0.0057939 | 0.0014521
55 | 0.0023471 | 0.00058823
56 | 0.0041746 | 0.0010462
57 | 0.0022089 | 0.00055361
58 | 0.0043407 | 0.0010879
59 | 0.0025857 | 0.00064804
60 | 0.0016395 | 0.0004109
61 | 0.0031262 | 0.00078349

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1