## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2228-29_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2228-29_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2228-29_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2228-29_0_4_node_30 | 0.4 | n |  | TRUE
4 | bus_LV_2228-29_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2228-29_0_4_node_65 | 0.4 | n |  | TRUE
6 | bus_LV_2228-29_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_2228-29_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_2228-29_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2228-29_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2228-29_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2228-29_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2228-29_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2228-29_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_2228-29_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2228-29_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2228-29_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2228-29_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2228-29_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2228-29_0_4_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_2228-29_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2228-29_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2228-29_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_2228-29_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2228-29_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2228-29_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2228-29_0_4_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_2228-29_0_4_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_2228-29_0_4_node_42 | 0.4 | n |  | TRUE
29 | bus_LV_2228-29_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2228-29_0_4_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_2228-29_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2228-29_0_4_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_2228-29_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_2228-29_0_4_node_54 | 0.4 | n |  | TRUE
35 | bus_LV_2228-29_0_4_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_2228-29_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_2228-29_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2228-29_0_4_node_64 | 0.4 | n |  | TRUE
39 | bus_LV_2228-29_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_2228-29_0_4_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_2228-29_0_4_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_2228-29_0_4_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_2228-29_0_4_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_2228-29_0_4_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_2228-29_0_4_node_57 | 0.4 | n |  | TRUE
46 | bus_LV_2228-29_0_4_node_62 | 0.4 | n |  | TRUE
47 | bus_LV_2228-29_0_4_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_2228-29_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_2228-29_0_4_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2228-29_0_4_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_2228-29_0_4_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_2228-29_0_4_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_2228-29_0_4_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2228-29_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_2228-29_0_4_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_2228-29_0_4_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_2228-29_0_4_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_2228-29_0_4_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_2228-29_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_2228-29_0_4_node_56 | 0.4 | n |  | TRUE
61 | bus_MV_376_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2228-29_0_4_load_0 | 0 | 0.0028574 | 0.00071614 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2228-29_0_4_load_1 | 1 | 0.0041276 | 0.0010345 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2228-29_0_4_load_3 | 2 | 0.006282 | 0.0015744 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2228-29_0_4_load_30 | 3 | 0.0054268 | 0.0013601 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2228-29_0_4_load_65 | 5 | 0.0044783 | 0.0011224 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2228-29_0_4_load_18 | 7 | 0.0043585 | 0.0010923 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2228-29_0_4_load_7 | 9 | 0.007889 | 0.0019772 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2228-29_0_4_load_5 | 10 | 0.011498 | 0.0028817 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2228-29_0_4_load_6 | 11 | 0.0045491 | 0.0011401 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2228-29_0_4_load_8 | 12 | 0.0046715 | 0.0011708 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2228-29_0_4_load_11 | 14 | 0.026264 | 0.0065825 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2228-29_0_4_load_10 | 15 | 0.0031558 | 0.00079093 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2228-29_0_4_load_12 | 16 | 0.0024322 | 0.00060958 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2228-29_0_4_load_17 | 17 | 0.0066316 | 0.001662 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2228-29_0_4_load_15 | 18 | 0.0066237 | 0.0016601 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2228-29_0_4_load_29 | 19 | 0.024131 | 0.0060478 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2228-29_0_4_load_36 | 26 | 0.0079357 | 0.0019889 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2228-29_0_4_load_37 | 27 | 0.019698 | 0.0049369 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2228-29_0_4_load_42 | 28 | 0.021548 | 0.0054004 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2228-29_0_4_load_45 | 30 | 0.0073556 | 0.0018435 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2228-29_0_4_load_43 | 32 | 0.0088098 | 0.0022079 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2228-29_0_4_load_51 | 33 | 0.0062233 | 0.0015597 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2228-29_0_4_load_54 | 34 | 0.024075 | 0.0060337 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2228-29_0_4_load_58 | 35 | 0.02813 | 0.00705 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2228-29_0_4_load_64 | 38 | 0.012356 | 0.0030968 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2228-29_0_4_load_34 | 39 | 0.021895 | 0.0054875 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2228-29_0_4_load_40 | 41 | 0.014848 | 0.0037214 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2228-29_0_4_load_44 | 42 | 0.0037099 | 0.0009298 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2228-29_0_4_load_50 | 43 | 0.010201 | 0.0025567 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2228-29_0_4_load_55 | 44 | 0.02017 | 0.0050551 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2228-29_0_4_load_57 | 45 | 0.046724 | 0.01171 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2228-29_0_4_load_38 | 47 | 0.021075 | 0.005282 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2228-29_0_4_load_31 | 48 | 0.0082298 | 0.0020626 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2228-29_0_4_load_59 | 51 | 0.012265 | 0.0030739 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2228-29_0_4_load_39 | 53 | 0.01155 | 0.0028948 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2228-29_0_4_load_41 | 54 | 0.0013134 | 0.00032916 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2228-29_0_4_load_47 | 55 | 0.005067 | 0.0012699 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2228-29_0_4_load_46 | 56 | 0.0022995 | 0.0005763 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2228-29_0_4_load_48 | 57 | 0.0036622 | 0.00091783 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2228-29_0_4_load_49 | 58 | 0.00664 | 0.0016641 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2228-29_0_4_load_52 | 59 | 0.0094139 | 0.0023593 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2228-29_0_4_load_56 | 60 | 0.018496 | 0.0046355 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2228-29_0_4_line_0 |  | 0 | 1 | 0.024043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2228-29_0_4_line_1 |  | 1 | 2 | 0.01351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2228-29_0_4_line_2 |  | 2 | 3 | 0.015201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2228-29_0_4_line_3 |  | 3 | 7 | 0.021469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2228-29_0_4_line_4 |  | 4 | 5 | 0.023354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2228-29_0_4_line_5 |  | 4 | 6 | 0.025855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2228-29_0_4_line_6 |  | 6 | 8 | 0.029981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2228-29_0_4_line_7 |  | 6 | 9 | 0.01633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2228-29_0_4_line_8 |  | 7 | 20 | 0.01891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2228-29_0_4_line_9 |  | 8 | 13 | 0.006449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2228-29_0_4_line_10 |  | 8 | 14 | 0.070821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2228-29_0_4_line_11 |  | 9 | 10 | 0.027007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2228-29_0_4_line_12 |  | 10 | 11 | 0.0011892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2228-29_0_4_line_13 |  | 11 | 12 | 0.029411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2228-29_0_4_line_14 |  | 13 | 17 | 0.029503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2228-29_0_4_line_15 |  | 13 | 18 | 0.019892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2228-29_0_4_line_16 |  | 14 | 15 | 0.045164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2228-29_0_4_line_17 |  | 15 | 16 | 0.057395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2228-29_0_4_line_18 |  | 17 | 19 | 0.024642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2228-29_0_4_line_19 |  | 18 | 20 | 0.016655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2228-29_0_4_line_20 |  | 19 | 21 | 0.019216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2228-29_0_4_line_21 |  | 21 | 22 | 0.014393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2228-29_0_4_line_22 |  | 21 | 23 | 0.032143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2228-29_0_4_line_23 |  | 22 | 35 | 0.027992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2228-29_0_4_line_24 |  | 22 | 31 | 0.044468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2228-29_0_4_line_25 |  | 23 | 27 | 0.049555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2228-29_0_4_line_26 |  | 23 | 28 | 0.0082918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2228-29_0_4_line_27 |  | 24 | 25 | 0.020442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2228-29_0_4_line_28 |  | 24 | 26 | 0.023261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2228-29_0_4_line_29 |  | 25 | 39 | 0.0080486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2228-29_0_4_line_30 |  | 26 | 27 | 0.053166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2228-29_0_4_line_31 |  | 29 | 30 | 0.012476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2228-29_0_4_line_32 |  | 29 | 31 | 0.055907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2228-29_0_4_line_33 |  | 29 | 32 | 0.0057745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2228-29_0_4_line_34 |  | 31 | 33 | 0.018512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2228-29_0_4_line_35 |  | 31 | 34 | 0.019314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2228-29_0_4_line_36 |  | 32 | 42 | 0.01324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2228-29_0_4_line_37 |  | 33 | 43 | 0.041492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2228-29_0_4_line_38 |  | 34 | 44 | 0.02194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2228-29_0_4_line_39 |  | 35 | 45 | 0.032924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2228-29_0_4_line_40 |  | 36 | 37 | 0.059692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2228-29_0_4_line_41 |  | 36 | 38 | 0.090273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2228-29_0_4_line_42 |  | 37 | 40 | 0.005686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2228-29_0_4_line_43 |  | 37 | 41 | 0.044211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2228-29_0_4_line_44 |  | 38 | 46 | 0.016511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2228-29_0_4_line_45 |  | 39 | 40 | 0.017179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2228-29_0_4_line_46 |  | 41 | 47 | 0.0044788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2228-29_0_4_line_47 |  | 43 | 59 | 0.001985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2228-29_0_4_line_48 |  | 44 | 60 | 0.017071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2228-29_0_4_line_49 |  | 45 | 50 | 0.052904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2228-29_0_4_line_50 |  | 46 | 52 | 0.15786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2228-29_0_4_line_51 |  | 47 | 53 | 0.044822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2228-29_0_4_line_52 |  | 48 | 49 | 0.069715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2228-29_0_4_line_53 |  | 49 | 50 | 0.11107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2228-29_0_4_line_54 |  | 51 | 52 | 0.068679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2228-29_0_4_line_55 |  | 53 | 54 | 0.010276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2228-29_0_4_line_56 |  | 54 | 55 | 0.014899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2228-29_0_4_line_57 |  | 55 | 56 | 0.02102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2228-29_0_4_line_58 |  | 56 | 57 | 0.089038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2228-29_0_4_line_59 |  | 57 | 58 | 0.010232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2228-29_0_4_trafo_42 | 0.63 MVA 20/0.4 kV | 61 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2577113.7943 | 1182187.5631 | 2577090.588 | 1182181.274
1 | 2577077.5475 | 1182177.743 | 2577087.8742 | 1182180.5386 | 2577090.588 | 1182181.274
2 | 2577077.5475 | 1182177.743 | 2577062.8748 | 1182173.771
3 | 2577062.8748 | 1182173.771 | 2577042.1515 | 1182168.161
4 | 2577069.3532 | 1182099.7232 | 2577062.1848 | 1182121.9512
5 | 2577044.2757 | 1182093.1495 | 2577069.3532 | 1182099.7232
6 | 2577044.2757 | 1182093.1495 | 2577042.8568 | 1182097.4572 | 2577036.0027 | 1182121.9629
7 | 2577044.2757 | 1182093.1495 | 2577028.4331 | 1182089.1887
8 | 2577023.8989 | 1182163.2198 | 2577042.1515 | 1182168.161
9 | 2577036.0027 | 1182121.9629 | 2577034.2246 | 1182128.1619
10 | 2577036.0027 | 1182121.9629 | 2577006.5911 | 1182118.0964 | 2576969.6154 | 1182112.9806 | 2576965.8381 | 1182112.3563
11 | 2577001.9496 | 1182083.9162 | 2577005.1793 | 1182084.6177 | 2577026.4524 | 1182088.6935 | 2577028.4331 | 1182089.1887
12 | 2577001.9496 | 1182083.9162 | 2577000.7875 | 1182083.6638
13 | 2576972.0242 | 1182077.524 | 2576987.0755 | 1182080.6854 | 2577000.7875 | 1182083.6638
14 | 2577034.2246 | 1182128.1619 | 2577019.5194 | 1182126.3842 | 2577007.2278 | 1182124.8085 | 2577004.9458 | 1182124.533
15 | 2577034.2246 | 1182128.1619 | 2577028.6043 | 1182147.2439
16 | 2576930.5463 | 1182086.3286 | 2576943.976 | 1182099.3169 | 2576956.4052 | 1182110.7971 | 2576965.8381 | 1182112.3563
17 | 2576944.4337 | 1182061.6623 | 2576927.9799 | 1182059.9027 | 2576918.0324 | 1182060.3414 | 2576917.2316 | 1182062.5678 | 2576917.4599 | 1182070.2598 | 2576923.0669 | 1182078.7982 | 2576929.1841 | 1182085.0111 | 2576930.5463 | 1182086.3286
18 | 2577004.9458 | 1182124.533 | 2576999.9096 | 1182123.9251 | 2576993.7075 | 1182119.4467 | 2576989.8891 | 1182119.2724 | 2576984.7629 | 1182125.5394
19 | 2577023.8989 | 1182163.2198 | 2577028.6043 | 1182147.2439
20 | 2576974.5824 | 1182141.6986 | 2576980.1603 | 1182132.8281 | 2576980.3844 | 1182131.5377 | 2576984.1057 | 1182126.3428 | 2576984.7629 | 1182125.5394
21 | 2576974.5824 | 1182141.6986 | 2576963.012 | 1182133.0944
22 | 2576974.5824 | 1182141.6986 | 2576971.0727 | 1182146.3368 | 2576974.2625 | 1182149.8041 | 2576976.4318 | 1182153.9757 | 2576983.5145 | 1182159.151 | 2576982.902 | 1182160.6875 | 2576981.8614 | 1182164.0711 | 2576980.5736 | 1182166.7219
23 | 2576963.012 | 1182133.0944 | 2576956.1197 | 1182127.8293 | 2576940.7744 | 1182116.0931
24 | 2576930.2699 | 1182146.6389 | 2576950.1159 | 1182152.9211 | 2576963.012 | 1182133.0944
25 | 2576980.5736 | 1182166.7219 | 2577027.6837 | 1182182.0947
26 | 2576980.5736 | 1182166.7219 | 2576972.6012 | 1182164.4425
27 | 2577105.6601 | 1182223.1036 | 2577107.048 | 1182218.6515 | 2577107.305 | 1182213.9925 | 2577105.3646 | 1182209.7533 | 2577103.0264 | 1182207.3054 | 2577100.3406 | 1182205.8039
28 | 2577100.3406 | 1182205.8039 | 2577078.2271 | 1182198.5879
29 | 2577105.6601 | 1182223.1036 | 2577103.6608 | 1182230.8999
30 | 2577078.2271 | 1182198.5879 | 2577027.6837 | 1182182.0947
31 | 2576950.5526 | 1182182.9572 | 2576962.4407 | 1182186.8467
32 | 2576930.2699 | 1182146.6389 | 2576950.1159 | 1182152.9211 | 2576957.1241 | 1182156.5848 | 2576954.6723 | 1182166.2549 | 2576951.6447 | 1182179.0843 | 2576950.5526 | 1182182.9572
33 | 2576950.5526 | 1182182.9572 | 2576949.1666 | 1182187.8763 | 2576948.6205 | 1182188.2538
34 | 2576930.2699 | 1182146.6389 | 2576912.5154 | 1182141.3985
35 | 2576930.2699 | 1182146.6389 | 2576928.1285 | 1182155.6296 | 2576926.6659 | 1182160.46 | 2576925.0045 | 1182165.2023
36 | 2576936.8898 | 1182194.0491 | 2576942.8918 | 1182192.2139 | 2576948.6205 | 1182188.2538
37 | 2576872.8252 | 1182129.3192 | 2576882.3865 | 1182132.5057 | 2576912.5154 | 1182141.3985
38 | 2576925.0045 | 1182165.2023 | 2576922.7378 | 1182167.4677 | 2576918.9847 | 1182168.3716 | 2576911.972 | 1182169.4882 | 2576907.3339 | 1182170.5845 | 2576905.0662 | 1182172.5609
39 | 2576914.6219 | 1182096.0915 | 2576940.7744 | 1182116.0931
40 | 2577073.2184 | 1182298.9008 | 2577074.2874 | 1182292.938 | 2577073.1526 | 1182285.7386 | 2577073.791 | 1182280.9893 | 2577076.7287 | 1182280.4888 | 2577078.4043 | 1182279.4041 | 2577079.6878 | 1182277.6204 | 2577086.4371 | 1182259.6519 | 2577090.0099 | 1182251.5562 | 2577093.7928 | 1182246.4723
41 | 2577073.2184 | 1182298.9008 | 2577040.1522 | 1182295.5039 | 2576983.4173 | 1182289.6877
42 | 2577093.7928 | 1182246.4723 | 2577099.3936 | 1182247.5403
43 | 2577093.7928 | 1182246.4723 | 2577054.5182 | 1182238.9637 | 2577050.3718 | 1182238.154
44 | 2576966.9924 | 1182288.004 | 2576983.4173 | 1182289.6877
45 | 2577099.3936 | 1182247.5403 | 2577103.6608 | 1182230.8999
46 | 2577045.9761 | 1182237.2955 | 2577050.3718 | 1182238.154
47 | 2576872.8252 | 1182129.3192 | 2576870.942 | 1182128.6916
48 | 2576905.0329 | 1182189.6144 | 2576904.6909 | 1182178.1875 | 2576905.0662 | 1182172.5609
49 | 2576872.5993 | 1182063.9524 | 2576914.6219 | 1182096.0915
50 | 2576850.5104 | 1182323.9843 | 2576856.9028 | 1182277.1796 | 2576867.4582 | 1182278.0391 | 2576930.2982 | 1182284.3326 | 2576934.7665 | 1182284.7489 | 2576948.8362 | 1182286.1731 | 2576966.9924 | 1182288.004
51 | 2577045.9761 | 1182237.2955 | 2577001.9856 | 1182228.7049 | 2577001.9856 | 1182228.7049
52 | 2576847.0883 | 1182024.4529 | 2576890.8361 | 1182023.3051 | 2576916.779 | 1182022.6206
53 | 2576872.5993 | 1182063.9524 | 2576876.3563 | 1182060.0692 | 2576871.9975 | 1182056.4397 | 2576857.7988 | 1182045.5335 | 2576854.6515 | 1182041.2101 | 2576828.4513 | 1182020.9456 | 2576821.4878 | 1182017.0595 | 2576822.0402 | 1182015.7567 | 2576822.4563 | 1182014.7657 | 2576826.7638 | 1182016.9946 | 2576830.5006 | 1182019.7148 | 2576836.1426 | 1182013.6342 | 2576843.4934 | 1182020.8984 | 2576847.0883 | 1182024.4529
54 | 2576850.5104 | 1182323.9843 | 2576860.5502 | 1182325.8241 | 2576888.8361 | 1182331.0172 | 2576917.9344 | 1182337.03
55 | 2577001.9856 | 1182228.7049 | 2576991.8392 | 1182227.0771
56 | 2576977.1283 | 1182224.7169 | 2576991.8392 | 1182227.0771
57 | 2576956.3734 | 1182221.387 | 2576977.1283 | 1182224.7169
58 | 2576956.3734 | 1182221.387 | 2576938.3816 | 1182218.5005 | 2576868.8778 | 1182208.9644 | 2576868.231 | 1182208.8258
59 | 2576868.231 | 1182208.8258 | 2576858.2261 | 1182206.6814

## bus_geodata
| x | y | coords
0 | 2577113.7943 | 1182187.5631
1 | 2577090.588 | 1182181.274
2 | 2577077.5475 | 1182177.743
3 | 2577062.8748 | 1182173.771
4 | 2577069.3532 | 1182099.7232
5 | 2577062.1848 | 1182121.9512
6 | 2577044.2757 | 1182093.1495
7 | 2577042.1515 | 1182168.161
8 | 2577036.0027 | 1182121.9629
9 | 2577028.4331 | 1182089.1887
10 | 2577001.9496 | 1182083.9162
11 | 2577000.7875 | 1182083.6638
12 | 2576972.0242 | 1182077.524
13 | 2577034.2246 | 1182128.1619
14 | 2576965.8381 | 1182112.3563
15 | 2576930.5463 | 1182086.3286
16 | 2576944.4337 | 1182061.6623
17 | 2577004.9458 | 1182124.533
18 | 2577028.6043 | 1182147.2439
19 | 2576984.7629 | 1182125.5394
20 | 2577023.8989 | 1182163.2198
21 | 2576974.5824 | 1182141.6986
22 | 2576963.012 | 1182133.0944
23 | 2576980.5736 | 1182166.7219
24 | 2577100.3406 | 1182205.8039
25 | 2577105.6601 | 1182223.1036
26 | 2577078.2271 | 1182198.5879
27 | 2577027.6837 | 1182182.0947
28 | 2576972.6012 | 1182164.4425
29 | 2576950.5526 | 1182182.9572
30 | 2576962.4407 | 1182186.8467
31 | 2576930.2699 | 1182146.6389
32 | 2576948.6205 | 1182188.2538
33 | 2576912.5154 | 1182141.3985
34 | 2576925.0045 | 1182165.2023
35 | 2576940.7744 | 1182116.0931
36 | 2577073.2184 | 1182298.9008
37 | 2577093.7928 | 1182246.4723
38 | 2576983.4173 | 1182289.6877
39 | 2577103.6608 | 1182230.8999
40 | 2577099.3936 | 1182247.5403
41 | 2577050.3718 | 1182238.154
42 | 2576936.8898 | 1182194.0491
43 | 2576872.8252 | 1182129.3192
44 | 2576905.0662 | 1182172.5609
45 | 2576914.6219 | 1182096.0915
46 | 2576966.9924 | 1182288.004
47 | 2577045.9761 | 1182237.2955
48 | 2576916.779 | 1182022.6206
49 | 2576847.0883 | 1182024.4529
50 | 2576872.5993 | 1182063.9524
51 | 2576917.9344 | 1182337.03
52 | 2576850.5104 | 1182323.9843
53 | 2577001.9856 | 1182228.7049
54 | 2576991.8392 | 1182227.0771
55 | 2576977.1283 | 1182224.7169
56 | 2576956.3734 | 1182221.387
57 | 2576868.231 | 1182208.8258
58 | 2576858.2261 | 1182206.6814
59 | 2576870.942 | 1182128.6915
60 | 2576905.0329 | 1182189.6144
61 | 2576972.4787 | 1182164.4074

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98695 | -0.25109 | 0.0028574 | 0.00071614
1 | 0.98701 | -0.24986 | 0.0041276 | 0.0010345
2 | 0.9871 | -0.24817 | 0.006282 | 0.0015744
3 | 0.98728 | -0.24456 | 0.0054268 | 0.0013601
4 | 0.98754 | -0.23947 | 0 | 0
5 | 0.98745 | -0.24134 | 0.0044783 | 0.0011224
6 | 0.98765 | -0.2374 | 0 | 0
7 | 0.98765 | -0.23739 | 0.0043585 | 0.0010923
8 | 0.98856 | -0.21969 | 0 | 0
9 | 0.98722 | -0.24575 | 0.007889 | 0.0019772
10 | 0.98671 | -0.25576 | 0.011498 | 0.0028817
11 | 0.9867 | -0.25596 | 0.0045491 | 0.0011401
12 | 0.98657 | -0.25842 | 0.0046715 | 0.0011708
13 | 0.98895 | -0.21222 | 0 | 0
14 | 0.98649 | -0.26001 | 0.026264 | 0.0065825
15 | 0.98626 | -0.26453 | 0.0031558 | 0.00079093
16 | 0.98613 | -0.26703 | 0.0024322 | 0.00060958
17 | 0.99151 | -0.16259 | 0.0066316 | 0.001662
18 | 0.9884 | -0.22275 | 0.0066237 | 0.0016601
19 | 0.9938 | -0.11845 | 0.024131 | 0.0060478
20 | 0.98805 | -0.2296 | 0 | 0
21 | 0.99601 | -0.076025 | 0 | 0
22 | 0.99475 | -0.10028 | 0 | 0
23 | 0.99913 | -0.016547 | 0 | 0
24 | 0.98752 | -0.23811 | 0 | 0
25 | 0.98538 | -0.27948 | 0 | 0
26 | 0.98996 | -0.19125 | 0.0079357 | 0.0019889
27 | 0.99591 | -0.077584 | 0.019698 | 0.0049369
28 | 1 | 0 | -0.46457 | -0.1181
29 | 0.98931 | -0.20538 | 0 | 0
30 | 0.98923 | -0.20701 | 0.0073556 | 0.0018435
31 | 0.99033 | -0.18561 | 0 | 0
32 | 0.98924 | -0.20667 | 0.0088098 | 0.0022079
33 | 0.98989 | -0.19411 | 0.0062233 | 0.0015597
34 | 0.98922 | -0.20717 | 0.024075 | 0.0060337
35 | 0.99262 | -0.14133 | 0.02813 | 0.00705
36 | 0.98125 | -0.35993 | 0 | 0
37 | 0.98261 | -0.33335 | 0 | 0
38 | 0.97919 | -0.40026 | 0.012356 | 0.0030968
39 | 0.98454 | -0.29582 | 0.021895 | 0.0054875
40 | 0.98309 | -0.324 | 0 | 0
41 | 0.97989 | -0.38654 | 0.014848 | 0.0037214
42 | 0.9892 | -0.20754 | 0.0037099 | 0.0009298
43 | 0.98914 | -0.2086 | 0.010201 | 0.0025567
44 | 0.98844 | -0.22229 | 0.02017 | 0.0050551
45 | 0.99097 | -0.1734 | 0.046724 | 0.01171
46 | 0.979 | -0.40395 | 0 | 0
47 | 0.97968 | -0.39074 | 0.021075 | 0.005282
48 | 0.98921 | -0.20761 | 0.0082298 | 0.0020626
49 | 0.98973 | -0.19739 | 0 | 0
50 | 0.99057 | -0.18113 | 0 | 0
51 | 0.97642 | -0.45462 | 0.012265 | 0.0030739
52 | 0.9772 | -0.43923 | 0 | 0
53 | 0.97841 | -0.41562 | 0.01155 | 0.0028948
54 | 0.97823 | -0.41918 | 0.0013134 | 0.00032916
55 | 0.97798 | -0.42397 | 0.005067 | 0.0012699
56 | 0.97774 | -0.4288 | 0.0022995 | 0.0005763
57 | 0.97688 | -0.44555 | 0.0036622 | 0.00091783
58 | 0.97682 | -0.44679 | 0.00664 | 0.0016641
59 | 0.98913 | -0.20894 | 0.0094139 | 0.0023593
60 | 0.98815 | -0.22793 | 0.018496 | 0.0046355
61 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0028574 | -0.00071614 | 0.0028576 | 0.00071594 | 1.6734e-07 | -2.0018e-07 | 0.0043081 | 0.004308 | 0.0043081 | 0.98695 | -0.25109 | 0.98701 | -0.24986 | 1.1835
1 | -0.0069852 | -0.0017504 | 0.0069858 | 0.0017506 | 5.6184e-07 | 1.8689e-07 | 0.010531 | 0.010531 | 0.010531 | 0.98701 | -0.24986 | 0.9871 | -0.24817 | 2.8931
2 | -0.013268 | -0.003325 | 0.01327 | 0.0033263 | 2.2803e-06 | 1.265e-06 | 0.020001 | 0.020001 | 0.020001 | 0.9871 | -0.24817 | 0.98728 | -0.24456 | 5.4947
3 | -0.018697 | -0.0046864 | 0.018703 | 0.0046902 | 6.3933e-06 | 3.8171e-06 | 0.02818 | 0.02818 | 0.02818 | 0.98728 | -0.24456 | 0.98765 | -0.23739 | 7.7417
4 | 0.0044787 | 0.0011223 | -0.0044783 | -0.0011224 | 3.9883e-07 | -4.352e-08 | 0.0067483 | 0.0067484 | 0.0067484 | 0.98754 | -0.23947 | 0.98745 | -0.24134 | 1.854
5 | -0.0044787 | -0.0011223 | 0.0044791 | 0.0011223 | 4.4153e-07 | -4.8257e-08 | 0.0067483 | 0.0067482 | 0.0067483 | 0.98754 | -0.23947 | 0.98765 | -0.2374 | 1.8539
6 | -0.033109 | -0.0083052 | 0.033137 | 0.0083227 | 2.7978e-05 | 1.7522e-05 | 0.049885 | 0.049885 | 0.049885 | 0.98765 | -0.2374 | 0.98856 | -0.21969 | 13.7048
7 | 0.02863 | 0.0071829 | -0.028618 | -0.0071758 | 1.1395e-05 | 7.0841e-06 | 0.043137 | 0.043137 | 0.043137 | 0.98765 | -0.2374 | 0.98722 | -0.24575 | 11.8509
8 | -0.023062 | -0.0057825 | 0.02307 | 0.0057878 | 8.5611e-06 | 5.237e-06 | 0.034746 | 0.034746 | 0.034746 | 0.98765 | -0.23739 | 0.98805 | -0.2296 | 9.5457
9 | -0.065052 | -0.016344 | 0.065075 | 0.016358 | 2.3194e-05 | 1.4762e-05 | 0.097933 | 0.097933 | 0.097933 | 0.98856 | -0.21969 | 0.98895 | -0.21222 | 26.9047
10 | 0.031915 | 0.008021 | -0.031854 | -0.0079826 | 6.1312e-05 | 3.8334e-05 | 0.048048 | 0.048048 | 0.048048 | 0.98856 | -0.21969 | 0.98649 | -0.26001 | 13.2001
11 | 0.020729 | 0.0051987 | -0.02072 | -0.0051927 | 9.8878e-06 | 5.9831e-06 | 0.031246 | 0.031246 | 0.031246 | 0.98722 | -0.24575 | 0.98671 | -0.25576 | 8.5842
12 | 0.0092213 | 0.0023109 | -0.0092212 | -0.0023109 | 8.6242e-08 | 4.0005e-08 | 0.013906 | 0.013906 | 0.013906 | 0.98671 | -0.25576 | 0.9867 | -0.25596 | 3.8204
13 | 0.0046721 | 0.0011708 | -0.0046715 | -0.0011708 | 5.4754e-07 | -2.5185e-08 | 0.0070458 | 0.0070459 | 0.0070459 | 0.9867 | -0.25596 | 0.98657 | -0.25842 | 1.9357
14 | -0.094792 | -0.02382 | 0.095017 | 0.023964 | 0.00022514 | 0.00014371 | 0.14265 | 0.14265 | 0.14265 | 0.98895 | -0.21222 | 0.99151 | -0.16259 | 39.1898
15 | 0.029716 | 0.0074617 | -0.029702 | -0.0074524 | 1.4917e-05 | 9.2918e-06 | 0.044718 | 0.044718 | 0.044718 | 0.98895 | -0.21222 | 0.9884 | -0.22275 | 12.2852
16 | 0.0055896 | 0.0014002 | -0.0055884 | -0.0014 | 1.2039e-06 | 1.9403e-07 | 0.008431 | 0.0084312 | 0.0084312 | 0.98649 | -0.26001 | 0.98626 | -0.26453 | 2.3163
17 | 0.0024325 | 0.00060903 | -0.0024322 | -0.00060958 | 2.8989e-07 | -5.468e-07 | 0.0036699 | 0.0036701 | 0.0036701 | 0.98626 | -0.26453 | 0.98613 | -0.26703 | 1.0083
18 | -0.10165 | -0.025626 | 0.10186 | 0.025763 | 0.00021519 | 0.0001374 | 0.1526 | 0.1526 | 0.1526 | 0.99151 | -0.16259 | 0.9938 | -0.11845 | 41.924
19 | 0.023078 | 0.0057924 | -0.02307 | -0.0057878 | 7.5401e-06 | 4.6123e-06 | 0.034746 | 0.034746 | 0.034746 | 0.9884 | -0.22275 | 0.98805 | -0.2296 | 9.5457
20 | -0.12599 | -0.031811 | 0.12625 | 0.031975 | 0.00025669 | 0.00016403 | 0.18873 | 0.18873 | 0.18873 | 0.9938 | -0.11845 | 0.99601 | -0.076025 | 51.8501
21 | 0.19261 | 0.048682 | -0.19239 | -0.048539 | 0.00022368 | 0.00014278 | 0.2879 | 0.2879 | 0.2879 | 0.99601 | -0.076025 | 0.99475 | -0.10028 | 39.5464
22 | -0.31886 | -0.080657 | 0.31977 | 0.08124 | 0.00091277 | 0.00058291 | 0.47663 | 0.47663 | 0.47663 | 0.99601 | -0.076025 | 0.99913 | -0.016547 | 43.6476
23 | 0.083345 | 0.020986 | -0.083182 | -0.020882 | 0.00016325 | 0.00010412 | 0.12471 | 0.12471 | 0.12471 | 0.99475 | -0.10028 | 0.99262 | -0.14133 | 34.2603
24 | 0.10904 | 0.027553 | -0.1086 | -0.02727 | 0.00044409 | 0.00028364 | 0.16319 | 0.16319 | 0.16319 | 0.99475 | -0.10028 | 0.99033 | -0.18561 | 44.8326
25 | 0.14278 | 0.03662 | -0.14236 | -0.036352 | 0.00042132 | 0.00026835 | 0.21294 | 0.21294 | 0.21294 | 0.99913 | -0.016547 | 0.99591 | -0.077584 | 29.2504
26 | -0.46256 | -0.11786 | 0.46292 | 0.1181 | 0.00036964 | 0.00023614 | 0.68957 | 0.68957 | 0.68957 | 0.99913 | -0.016547 | 1 | 0 | 47.3609
27 | 0.1138 | 0.028833 | -0.11357 | -0.028689 | 0.00022569 | 0.00014418 | 0.17158 | 0.17158 | 0.17158 | 0.98752 | -0.23811 | 0.98538 | -0.27948 | 47.1385
28 | -0.1138 | -0.028833 | 0.11405 | 0.028997 | 0.00025681 | 0.00016406 | 0.17158 | 0.17158 | 0.17158 | 0.98752 | -0.23811 | 0.98996 | -0.19125 | 47.1385
29 | 0.11357 | 0.028689 | -0.11348 | -0.028632 | 8.886e-05 | 5.6768e-05 | 0.17158 | 0.17158 | 0.17158 | 0.98538 | -0.27948 | 0.98454 | -0.29582 | 47.1385
30 | -0.12199 | -0.030986 | 0.12266 | 0.031415 | 0.00067142 | 0.00042902 | 0.18351 | 0.18351 | 0.18351 | 0.98996 | -0.19125 | 0.99591 | -0.077584 | 50.4154
31 | 0.0073562 | 0.0018437 | -0.0073556 | -0.0018435 | 5.7276e-07 | 2.0638e-07 | 0.011064 | 0.011065 | 0.011065 | 0.98931 | -0.20538 | 0.98923 | -0.20701 | 3.0397
32 | -0.019877 | -0.0049818 | 0.019896 | 0.0049931 | 1.8739e-05 | 1.1274e-05 | 0.029897 | 0.029896 | 0.029897 | 0.98931 | -0.20538 | 0.99033 | -0.18561 | 8.2134
33 | 0.012521 | 0.0031381 | -0.01252 | -0.0031377 | 7.6798e-07 | 4.1737e-07 | 0.018832 | 0.018832 | 0.018832 | 0.98931 | -0.20538 | 0.98924 | -0.20667 | 5.1737
34 | 0.025863 | 0.0064904 | -0.025852 | -0.006484 | 1.0485e-05 | 6.4721e-06 | 0.038863 | 0.038863 | 0.038863 | 0.99033 | -0.18561 | 0.98989 | -0.19411 | 10.6767
35 | 0.062839 | 0.015786 | -0.062774 | -0.015745 | 6.4586e-05 | 4.1087e-05 | 0.094431 | 0.094431 | 0.094431 | 0.99033 | -0.18561 | 0.98922 | -0.20717 | 25.9427
36 | 0.0037101 | 0.00092973 | -0.0037099 | -0.0009298 | 1.5464e-07 | -7.1014e-08 | 0.0055807 | 0.0055807 | 0.0055807 | 0.98924 | -0.20667 | 0.9892 | -0.20754 | 1.5332
37 | 0.019629 | 0.0049243 | -0.019615 | -0.0049161 | 1.3548e-05 | 8.138e-06 | 0.029508 | 0.029508 | 0.029508 | 0.98989 | -0.19411 | 0.98914 | -0.2086 | 8.1067
38 | 0.038699 | 0.0097112 | -0.038671 | -0.0096936 | 2.7885e-05 | 1.7565e-05 | 0.058217 | 0.058217 | 0.058217 | 0.98922 | -0.20717 | 0.98844 | -0.22229 | 15.9937
39 | 0.055052 | 0.013832 | -0.054968 | -0.013778 | 8.4114e-05 | 5.3408e-05 | 0.082539 | 0.082539 | 0.082539 | 0.99262 | -0.14133 | 0.99097 | -0.1734 | 22.6756
40 | -0.024701 | -0.0062173 | 0.024732 | 0.0062367 | 3.1423e-05 | 1.9356e-05 | 0.037467 | 0.037467 | 0.037467 | 0.98125 | -0.35993 | 0.98261 | -0.33335 | 10.2932
41 | 0.024701 | 0.0062173 | -0.024653 | -0.006188 | 4.7522e-05 | 2.9276e-05 | 0.037467 | 0.037468 | 0.037468 | 0.98125 | -0.35993 | 0.97919 | -0.40026 | 10.2933
42 | -0.091423 | -0.023039 | 0.091464 | 0.023065 | 4.0897e-05 | 2.6102e-05 | 0.13849 | 0.13849 | 0.13849 | 0.98261 | -0.33335 | 0.98309 | -0.324 | 38.0472
43 | 0.066691 | 0.016803 | -0.066522 | -0.016695 | 0.00016921 | 0.00010773 | 0.10103 | 0.10103 | 0.10103 | 0.98261 | -0.33335 | 0.97989 | -0.38654 | 27.7542
44 | 0.012297 | 0.0030912 | -0.012295 | -0.00309 | 2.1629e-06 | 1.1766e-06 | 0.01869 | 0.01869 | 0.01869 | 0.97919 | -0.40026 | 0.979 | -0.40395 | 5.1347
45 | 0.091588 | 0.023144 | -0.091464 | -0.023065 | 0.00012356 | 7.8859e-05 | 0.13849 | 0.13849 | 0.13849 | 0.98454 | -0.29582 | 0.98309 | -0.324 | 38.0472
46 | 0.051673 | 0.012974 | -0.051663 | -0.012967 | 1.0344e-05 | 6.5635e-06 | 0.078477 | 0.078477 | 0.078477 | 0.97989 | -0.38654 | 0.97968 | -0.39074 | 21.5596
47 | 0.009414 | 0.0023594 | -0.0094139 | -0.0023593 | 1.493e-07 | 7.007e-08 | 0.014162 | 0.014162 | 0.014162 | 0.98914 | -0.2086 | 0.98913 | -0.20894 | 3.8907
48 | 0.018501 | 0.0046385 | -0.018496 | -0.0046355 | 4.9661e-06 | 2.9595e-06 | 0.027852 | 0.027852 | 0.027852 | 0.98844 | -0.22229 | 0.98815 | -0.22793 | 7.6517
49 | 0.0082433 | 0.0020682 | -0.0082402 | -0.0020669 | 3.04e-06 | 1.2643e-06 | 0.012379 | 0.012379 | 0.012379 | 0.99097 | -0.1734 | 0.99057 | -0.18113 | 3.4008
50 | 0.012295 | 0.00309 | -0.012274 | -0.0030788 | 2.068e-05 | 1.1254e-05 | 0.01869 | 0.018691 | 0.018691 | 0.979 | -0.40395 | 0.9772 | -0.43923 | 5.1349
51 | 0.030587 | 0.007685 | -0.030551 | -0.0076623 | 3.629e-05 | 2.2662e-05 | 0.046466 | 0.046466 | 0.046466 | 0.97968 | -0.39074 | 0.97841 | -0.41562 | 12.7654
52 | -0.0082298 | -0.0020626 | 0.0082338 | 0.0020643 | 4.0065e-06 | 1.6687e-06 | 0.01238 | 0.012379 | 0.01238 | 0.98921 | -0.20761 | 0.98973 | -0.19739 | 3.401
53 | -0.0082338 | -0.0020643 | 0.0082402 | 0.0020669 | 6.3828e-06 | 2.6564e-06 | 0.012379 | 0.012379 | 0.012379 | 0.98973 | -0.19739 | 0.99057 | -0.18113 | 3.4009
54 | -0.012265 | -0.0030739 | 0.012274 | 0.0030788 | 8.9975e-06 | 4.8987e-06 | 0.018691 | 0.018691 | 0.018691 | 0.97642 | -0.45462 | 0.9772 | -0.43923 | 5.1349
55 | 0.019001 | 0.0047675 | -0.018998 | -0.0047656 | 3.2184e-06 | 1.9307e-06 | 0.028899 | 0.028899 | 0.028899 | 0.97841 | -0.41562 | 0.97823 | -0.41918 | 7.9394
56 | 0.017684 | 0.0044364 | -0.01768 | -0.004434 | 4.0434e-06 | 2.4008e-06 | 0.026902 | 0.026902 | 0.026902 | 0.97823 | -0.41918 | 0.97798 | -0.42397 | 7.3906
57 | 0.012613 | 0.0031641 | -0.01261 | -0.0031625 | 2.9035e-06 | 1.5945e-06 | 0.019192 | 0.019192 | 0.019192 | 0.97798 | -0.42397 | 0.97774 | -0.4288 | 5.2726
58 | 0.010311 | 0.0025862 | -0.010303 | -0.0025821 | 8.2227e-06 | 4.1468e-06 | 0.015693 | 0.015693 | 0.015693 | 0.97774 | -0.4288 | 0.97688 | -0.44555 | 4.3113
59 | 0.0066404 | 0.0016643 | -0.00664 | -0.0016641 | 3.9257e-07 | 1.2315e-07 | 0.010115 | 0.010115 | 0.010115 | 0.97688 | -0.44555 | 0.97682 | -0.44679 | 2.7788

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48612 | 0.1235

## res_load
| p_mw | q_mvar
0 | 0.0028574 | 0.00071614
1 | 0.0041276 | 0.0010345
2 | 0.006282 | 0.0015744
3 | 0.0054268 | 0.0013601
4 | 0.0044783 | 0.0011224
5 | 0.0043585 | 0.0010923
6 | 0.007889 | 0.0019772
7 | 0.011498 | 0.0028817
8 | 0.0045491 | 0.0011401
9 | 0.0046715 | 0.0011708
10 | 0.026264 | 0.0065825
11 | 0.0031558 | 0.00079093
12 | 0.0024322 | 0.00060958
13 | 0.0066316 | 0.001662
14 | 0.0066237 | 0.0016601
15 | 0.024131 | 0.0060478
16 | 0.0079357 | 0.0019889
17 | 0.019698 | 0.0049369
18 | 0.021548 | 0.0054004
19 | 0.0073556 | 0.0018435
20 | 0.0088098 | 0.0022079
21 | 0.0062233 | 0.0015597
22 | 0.024075 | 0.0060337
23 | 0.02813 | 0.00705
24 | 0.012356 | 0.0030968
25 | 0.021895 | 0.0054875
26 | 0.014848 | 0.0037214
27 | 0.0037099 | 0.0009298
28 | 0.010201 | 0.0025567
29 | 0.02017 | 0.0050551
30 | 0.046724 | 0.01171
31 | 0.021075 | 0.005282
32 | 0.0082298 | 0.0020626
33 | 0.012265 | 0.0030739
34 | 0.01155 | 0.0028948
35 | 0.0013134 | 0.00032916
36 | 0.005067 | 0.0012699
37 | 0.0022995 | 0.0005763
38 | 0.0036622 | 0.00091783
39 | 0.00664 | 0.0016641
40 | 0.0094139 | 0.0023593
41 | 0.018496 | 0.0046355

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1