## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2228-8_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2228-8_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2228-8_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2228-8_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2228-8_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2228-8_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2228-8_0_6_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_2228-8_0_6_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2228-8_0_6_node_135 | 0.4 | n |  | TRUE
9 | bus_LV_2228-8_0_6_node_136 | 0.4 | n |  | TRUE
10 | bus_LV_2228-8_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2228-8_0_6_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_2228-8_0_6_node_85 | 0.4 | n |  | TRUE
13 | bus_LV_2228-8_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2228-8_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2228-8_0_6_node_134 | 0.4 | n |  | TRUE
16 | bus_LV_2228-8_0_6_node_71 | 0.4 | n |  | TRUE
17 | bus_LV_2228-8_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2228-8_0_6_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_2228-8_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2228-8_0_6_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_2228-8_0_6_node_133 | 0.4 | n |  | TRUE
22 | bus_LV_2228-8_0_6_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_2228-8_0_6_node_60 | 0.4 | n |  | TRUE
24 | bus_LV_2228-8_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2228-8_0_6_node_84 | 0.4 | n |  | TRUE
26 | bus_LV_2228-8_0_6_node_58 | 0.4 | n |  | TRUE
27 | bus_LV_2228-8_0_6_node_129 | 0.4 | n |  | TRUE
28 | bus_LV_2228-8_0_6_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_2228-8_0_6_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_2228-8_0_6_node_131 | 0.4 | n |  | TRUE
31 | bus_LV_2228-8_0_6_node_46 | 0.4 | n |  | TRUE
32 | bus_LV_2228-8_0_6_node_45 | 0.4 | n |  | TRUE
33 | bus_LV_2228-8_0_6_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_2228-8_0_6_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_2228-8_0_6_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_2228-8_0_6_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_2228-8_0_6_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2228-8_0_6_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_2228-8_0_6_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_2228-8_0_6_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_2228-8_0_6_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_2228-8_0_6_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_2228-8_0_6_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_2228-8_0_6_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_2228-8_0_6_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_2228-8_0_6_node_83 | 0.4 | n |  | TRUE
47 | bus_LV_2228-8_0_6_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_2228-8_0_6_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_2228-8_0_6_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_2228-8_0_6_node_53 | 0.4 | n |  | TRUE
51 | bus_LV_2228-8_0_6_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_2228-8_0_6_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_2228-8_0_6_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_2228-8_0_6_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_2228-8_0_6_node_132 | 0.4 | n |  | TRUE
56 | bus_LV_2228-8_0_6_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_2228-8_0_6_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_2228-8_0_6_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_2228-8_0_6_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_2228-8_0_6_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_2228-8_0_6_node_137 | 0.4 | n |  | TRUE
62 | bus_LV_2228-8_0_6_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_2228-8_0_6_node_78 | 0.4 | n |  | TRUE
64 | bus_LV_2228-8_0_6_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_2228-8_0_6_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_2228-8_0_6_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_2228-8_0_6_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_2228-8_0_6_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_2228-8_0_6_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_2228-8_0_6_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_2228-8_0_6_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_2228-8_0_6_node_72 | 0.4 | n |  | TRUE
73 | bus_LV_2228-8_0_6_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_2228-8_0_6_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_2228-8_0_6_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_2228-8_0_6_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_2228-8_0_6_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_2228-8_0_6_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_2228-8_0_6_node_121 | 0.4 | n |  | TRUE
80 | bus_LV_2228-8_0_6_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_2228-8_0_6_node_126 | 0.4 | n |  | TRUE
82 | bus_LV_2228-8_0_6_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_2228-8_0_6_node_101 | 0.4 | n |  | TRUE
84 | bus_LV_2228-8_0_6_node_120 | 0.4 | n |  | TRUE
85 | bus_LV_2228-8_0_6_node_125 | 0.4 | n |  | TRUE
86 | bus_LV_2228-8_0_6_node_122 | 0.4 | n |  | TRUE
87 | bus_LV_2228-8_0_6_node_127 | 0.4 | n |  | TRUE
88 | bus_LV_2228-8_0_6_node_102 | 0.4 | n |  | TRUE
89 | bus_LV_2228-8_0_6_node_107 | 0.4 | n |  | TRUE
90 | bus_LV_2228-8_0_6_node_124 | 0.4 | n |  | TRUE
91 | bus_LV_2228-8_0_6_node_128 | 0.4 | n |  | TRUE
92 | bus_LV_2228-8_0_6_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_2228-8_0_6_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_2228-8_0_6_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_2228-8_0_6_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_2228-8_0_6_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_2228-8_0_6_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_2228-8_0_6_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_2228-8_0_6_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_2228-8_0_6_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_2228-8_0_6_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_2228-8_0_6_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_2228-8_0_6_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_2228-8_0_6_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_2228-8_0_6_node_89 | 0.4 | n |  | TRUE
106 | bus_LV_2228-8_0_6_node_90 | 0.4 | n |  | TRUE
107 | bus_LV_2228-8_0_6_node_96 | 0.4 | n |  | TRUE
108 | bus_LV_2228-8_0_6_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_2228-8_0_6_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_2228-8_0_6_node_105 | 0.4 | n |  | TRUE
111 | bus_LV_2228-8_0_6_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_2228-8_0_6_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_2228-8_0_6_node_100 | 0.4 | n |  | TRUE
114 | bus_LV_2228-8_0_6_node_93 | 0.4 | n |  | TRUE
115 | bus_LV_2228-8_0_6_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_2228-8_0_6_node_118 | 0.4 | n |  | TRUE
117 | bus_LV_2228-8_0_6_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_2228-8_0_6_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_2228-8_0_6_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_2228-8_0_6_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_2228-8_0_6_node_117 | 0.4 | n |  | TRUE
122 | bus_LV_2228-8_0_6_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_2228-8_0_6_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_2228-8_0_6_node_112 | 0.4 | n |  | TRUE
125 | bus_LV_2228-8_0_6_node_113 | 0.4 | n |  | TRUE
126 | bus_LV_2228-8_0_6_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_2228-8_0_6_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_2228-8_0_6_node_116 | 0.4 | n |  | TRUE
129 | bus_LV_2228-8_0_6_node_130 | 0.4 | n |  | TRUE
130 | bus_LV_2228-8_0_6_node_123 | 0.4 | n |  | TRUE
131 | bus_MV_505_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2228-8_0_6_load_0 | 0 | 0.0020092 | 0.00050355 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2228-8_0_6_load_1 | 1 | 0.0097505 | 0.0024437 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2228-8_0_6_load_3 | 3 | 0.0041425 | 0.0010382 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2228-8_0_6_load_15 | 6 | 0.006565 | 0.0016453 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2228-8_0_6_load_16 | 7 | 0.016052 | 0.004023 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2228-8_0_6_load_135 | 8 | 0.009032 | 0.0022636 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2228-8_0_6_load_136 | 9 | 0.0042546 | 0.0010663 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2228-8_0_6_load_85 | 12 | 0.0026626 | 0.00066731 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2228-8_0_6_load_134 | 15 | 0.0010706 | 0.00026833 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2228-8_0_6_load_71 | 16 | 0.0016289 | 0.00040824 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2228-8_0_6_load_30 | 20 | 0.022331 | 0.0055967 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2228-8_0_6_load_133 | 21 | 0.00069547 | 0.0001743 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2228-8_0_6_load_61 | 22 | 0.0062614 | 0.0015693 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2228-8_0_6_load_60 | 23 | 0.0041539 | 0.0010411 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2228-8_0_6_load_84 | 25 | 0.0027872 | 0.00069854 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2228-8_0_6_load_58 | 26 | 0.0036523 | 0.00091536 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2228-8_0_6_load_129 | 27 | 0.035522 | 0.0089026 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2228-8_0_6_load_131 | 30 | 0.00070479 | 0.00017664 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2228-8_0_6_load_45 | 32 | 0.010634 | 0.0026652 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2228-8_0_6_load_25 | 34 | 0.022716 | 0.0056932 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2228-8_0_6_load_23 | 35 | 0.014228 | 0.0035658 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2228-8_0_6_load_24 | 36 | 0.014177 | 0.0035531 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2228-8_0_6_load_35 | 39 | 0.0061964 | 0.001553 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2228-8_0_6_load_26 | 42 | 0.013125 | 0.0032895 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2228-8_0_6_load_47 | 45 | 0.010078 | 0.0025257 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2228-8_0_6_load_83 | 46 | 0.0022734 | 0.00056977 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2228-8_0_6_load_38 | 48 | 0.0033181 | 0.00083161 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2228-8_0_6_load_36 | 49 | 0.010304 | 0.0025825 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2228-8_0_6_load_53 | 50 | 0.0032793 | 0.00082186 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2228-8_0_6_load_31 | 51 | 0.012916 | 0.0032369 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2228-8_0_6_load_41 | 52 | 0.014556 | 0.0036482 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2228-8_0_6_load_132 | 55 | 0.0032933 | 0.00082537 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2228-8_0_6_load_43 | 58 | 0.0051318 | 0.0012861 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2228-8_0_6_load_40 | 59 | 0.0038183 | 0.00095697 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2228-8_0_6_load_44 | 60 | 0.0052036 | 0.0013041 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2228-8_0_6_load_137 | 61 | 0.0026409 | 0.00066186 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2228-8_0_6_load_52 | 64 | 0.005352 | 0.0013413 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2228-8_0_6_load_51 | 65 | 0.0025861 | 0.00064814 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2228-8_0_6_load_50 | 66 | 0.007683 | 0.0019255 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2228-8_0_6_load_86 | 67 | 0.003447 | 0.0008639 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2228-8_0_6_load_55 | 68 | 0.0024704 | 0.00061915 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2228-8_0_6_load_57 | 70 | 0.0029543 | 0.00074043 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2228-8_0_6_load_59 | 71 | 0.0023337 | 0.00058489 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2228-8_0_6_load_72 | 72 | 0.0043387 | 0.0010874 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2228-8_0_6_load_73 | 73 | 0.0033792 | 0.0008469 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2228-8_0_6_load_63 | 75 | 0.0013762 | 0.0003449 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2228-8_0_6_load_70 | 77 | 0.00381 | 0.00095488 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2228-8_0_6_load_121 | 79 | 0.0037091 | 0.00092959 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2228-8_0_6_load_126 | 81 | 0.0024949 | 0.00062529 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2228-8_0_6_load_101 | 83 | 0.0092379 | 0.0023152 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2228-8_0_6_load_125 | 85 | 0.0024318 | 0.00060947 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2228-8_0_6_load_122 | 86 | 0.00469 | 0.0011754 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2228-8_0_6_load_127 | 87 | 0.0037316 | 0.00093522 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2228-8_0_6_load_102 | 88 | 0.0040009 | 0.0010027 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2228-8_0_6_load_107 | 89 | 0.0034006 | 0.00085227 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2228-8_0_6_load_128 | 91 | 0.0046752 | 0.0011717 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2228-8_0_6_load_74 | 92 | 0.0062832 | 0.0015747 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2228-8_0_6_load_75 | 93 | 0.0013431 | 0.00033661 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2228-8_0_6_load_76 | 94 | 0.002238 | 0.00056089 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2228-8_0_6_load_77 | 95 | 0.004172 | 0.0010456 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2228-8_0_6_load_79 | 96 | 0.002238 | 0.00056089 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2228-8_0_6_load_81 | 99 | 0.0027635 | 0.00069261 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2228-8_0_6_load_82 | 100 | 0.0012526 | 0.00031392 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2228-8_0_6_load_91 | 101 | 0.0041583 | 0.0010422 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2228-8_0_6_load_95 | 102 | 0.002792 | 0.00069973 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2228-8_0_6_load_92 | 103 | 0.006256 | 0.0015679 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2228-8_0_6_load_94 | 104 | 0.0026682 | 0.00066871 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2228-8_0_6_load_89 | 105 | 0.0041126 | 0.0010307 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2228-8_0_6_load_90 | 106 | 0.0046746 | 0.0011716 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2228-8_0_6_load_104 | 109 | 0.0042992 | 0.0010775 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2228-8_0_6_load_97 | 111 | 0.0041789 | 0.0010473 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2228-8_0_6_load_99 | 112 | 0.002862 | 0.00071729 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2228-8_0_6_load_100 | 113 | 0.0032661 | 0.00081856 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2228-8_0_6_load_93 | 114 | 0.0051255 | 0.0012846 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2228-8_0_6_load_118 | 116 | 0.0035022 | 0.00087774 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2228-8_0_6_load_108 | 117 | 0.0034196 | 0.00085702 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2228-8_0_6_load_103 | 118 | 0.0058108 | 0.0014563 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2228-8_0_6_load_109 | 119 | 0.005304 | 0.0013293 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2228-8_0_6_load_119 | 120 | 0.0046168 | 0.0011571 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2228-8_0_6_load_110 | 122 | 0.0042992 | 0.0010775 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2228-8_0_6_load_113 | 125 | 0.0017302 | 0.00043363 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2228-8_0_6_load_114 | 126 | 0.0049996 | 0.001253 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2228-8_0_6_load_115 | 127 | 0.0097252 | 0.0024374 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2228-8_0_6_load_130 | 129 | 0.005325 | 0.0013346 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2228-8_0_6_load_123 | 130 | 0.0062236 | 0.0015598 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2228-8_0_6_line_0 |  | 0 | 1 | 0.013475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2228-8_0_6_line_1 |  | 0 | 2 | 0.011665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2228-8_0_6_line_2 |  | 1 | 3 | 0.026692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2228-8_0_6_line_3 |  | 2 | 4 | 0.006649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2228-8_0_6_line_4 |  | 2 | 5 | 0.024831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2228-8_0_6_line_5 |  | 3 | 6 | 0.0066301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2228-8_0_6_line_6 |  | 4 | 7 | 0.034776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2228-8_0_6_line_7 |  | 5 | 8 | 0.018848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2228-8_0_6_line_8 |  | 5 | 9 | 0.010761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2228-8_0_6_line_9 |  | 7 | 11 | 0.015371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2228-8_0_6_line_10 |  | 10 | 11 | 0.019403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2228-8_0_6_line_11 |  | 10 | 12 | 0.010021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2228-8_0_6_line_12 |  | 11 | 24 | 0.008167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2228-8_0_6_line_13 |  | 12 | 25 | 0.028448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2228-8_0_6_line_14 |  | 13 | 14 | 0.13049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2228-8_0_6_line_15 |  | 13 | 15 | 0.091371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2228-8_0_6_line_16 |  | 14 | 16 | 0.0077476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2228-8_0_6_line_17 |  | 16 | 26 | 0.011719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2228-8_0_6_line_18 |  | 17 | 18 | 0.085585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2228-8_0_6_line_19 |  | 17 | 19 | 0.080196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2228-8_0_6_line_20 |  | 17 | 20 | 0.0516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2228-8_0_6_line_21 |  | 18 | 27 | 0.024109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2228-8_0_6_line_22 |  | 19 | 21 | 0.010973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2228-8_0_6_line_23 |  | 20 | 33 | 0.017566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2228-8_0_6_line_24 |  | 22 | 23 | 0.026443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2228-8_0_6_line_25 |  | 23 | 74 | 0.026842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2228-8_0_6_line_26 |  | 24 | 36 | 0.01955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2228-8_0_6_line_27 |  | 25 | 38 | 0.026305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2228-8_0_6_line_28 |  | 26 | 69 | 0.017519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2228-8_0_6_line_29 |  | 28 | 29 | 0.1351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2228-8_0_6_line_30 |  | 28 | 30 | 0.05275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2228-8_0_6_line_31 |  | 29 | 31 | 0.033849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2228-8_0_6_line_32 |  | 29 | 32 | 0.020071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2228-8_0_6_line_33 |  | 30 | 55 | 0.0039617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2228-8_0_6_line_34 |  | 31 | 56 | 0.008882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2228-8_0_6_line_35 |  | 32 | 57 | 0.011718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2228-8_0_6_line_36 |  | 33 | 51 | 0.015671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2228-8_0_6_line_37 |  | 33 | 42 | 0.017708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2228-8_0_6_line_38 |  | 34 | 35 | 0.0052567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2228-8_0_6_line_39 |  | 35 | 36 | 0.026856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2228-8_0_6_line_40 |  | 37 | 38 | 0.024731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2228-8_0_6_line_41 |  | 37 | 39 | 0.0064941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2228-8_0_6_line_42 |  | 38 | 46 | 0.023098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2228-8_0_6_line_43 |  | 39 | 41 | 0.011912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2228-8_0_6_line_44 |  | 40 | 41 | 0.028267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2228-8_0_6_line_45 |  | 40 | 42 | 0.020076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_2228-8_0_6_line_46 |  | 43 | 44 | 0.029232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2228-8_0_6_line_47 |  | 43 | 45 | 0.043015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2228-8_0_6_line_48 |  | 44 | 50 | 0.0085498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_2228-8_0_6_line_49 |  | 44 | 46 | 0.0027084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2228-8_0_6_line_50 |  | 47 | 48 | 0.023501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2228-8_0_6_line_51 |  | 47 | 49 | 0.011961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2228-8_0_6_line_52 |  | 48 | 53 | 0.01287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2228-8_0_6_line_53 |  | 49 | 54 | 0.010464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2228-8_0_6_line_54 |  | 50 | 65 | 0.035684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_2228-8_0_6_line_55 |  | 51 | 52 | 0.00085104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2228-8_0_6_line_56 |  | 52 | 53 | 0.011608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2228-8_0_6_line_57 |  | 53 | 59 | 0.011031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2228-8_0_6_line_58 |  | 54 | 57 | 0.037223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2228-8_0_6_line_59 |  | 56 | 61 | 0.069692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2228-8_0_6_line_60 |  | 57 | 58 | 0.018667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2228-8_0_6_line_61 |  | 58 | 60 | 0.0001916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2228-8_0_6_line_62 |  | 62 | 63 | 0.016009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_2228-8_0_6_line_63 |  | 62 | 64 | 0.077057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2228-8_0_6_line_64 |  | 63 | 67 | 0.021128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2228-8_0_6_line_65 |  | 64 | 66 | 0.012047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2228-8_0_6_line_66 |  | 65 | 66 | 0.01523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2228-8_0_6_line_67 |  | 67 | 98 | 0.0041949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2228-8_0_6_line_68 |  | 68 | 69 | 0.0082578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2228-8_0_6_line_69 |  | 68 | 70 | 0.0023776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2228-8_0_6_line_70 |  | 69 | 71 | 0.020732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2228-8_0_6_line_71 |  | 71 | 72 | 0.036282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2228-8_0_6_line_72 |  | 72 | 73 | 0.024268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2228-8_0_6_line_73 |  | 73 | 92 | 0.00043992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2228-8_0_6_line_74 |  | 74 | 75 | 0.017568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2228-8_0_6_line_75 |  | 74 | 76 | 0.066859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2228-8_0_6_line_76 |  | 75 | 77 | 0.015212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2228-8_0_6_line_77 |  | 76 | 78 | 0.14185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2228-8_0_6_line_78 |  | 76 | 79 | 0.019707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2228-8_0_6_line_79 |  | 78 | 84 | 0.055794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2228-8_0_6_line_80 |  | 78 | 85 | 0.036313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2228-8_0_6_line_81 |  | 78 | 80 | 0.084352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2228-8_0_6_line_82 |  | 78 | 82 | 0.018974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2228-8_0_6_line_83 |  | 79 | 86 | 0.035753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2228-8_0_6_line_84 |  | 80 | 81 | 0.0061208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2228-8_0_6_line_85 |  | 81 | 87 | 0.034499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2228-8_0_6_line_86 |  | 82 | 83 | 0.01291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_2228-8_0_6_line_87 |  | 83 | 88 | 0.044733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_2228-8_0_6_line_88 |  | 84 | 89 | 0.016589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2228-8_0_6_line_89 |  | 85 | 90 | 0.01662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2228-8_0_6_line_90 |  | 87 | 91 | 0.079907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2228-8_0_6_line_91 |  | 88 | 118 | 0.0010852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2228-8_0_6_line_92 |  | 89 | 110 | 0.068073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_2228-8_0_6_line_93 |  | 90 | 130 | 0.033433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2228-8_0_6_line_94 |  | 92 | 93 | 0.017896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2228-8_0_6_line_95 |  | 93 | 94 | 0.014265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2228-8_0_6_line_96 |  | 94 | 95 | 0.0081626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2228-8_0_6_line_97 |  | 95 | 96 | 0.00020818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2228-8_0_6_line_98 |  | 96 | 97 | 0.020804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2228-8_0_6_line_99 |  | 97 | 99 | 0.038869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2228-8_0_6_line_100 |  | 97 | 100 | 0.0097832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2228-8_0_6_line_101 |  | 98 | 105 | 0.015851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2228-8_0_6_line_102 |  | 98 | 106 | 0.022517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_2228-8_0_6_line_103 |  | 99 | 101 | 0.0027611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2228-8_0_6_line_104 |  | 100 | 102 | 0.013707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2228-8_0_6_line_105 |  | 101 | 103 | 0.010069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2228-8_0_6_line_106 |  | 102 | 104 | 0.010684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2228-8_0_6_line_107 |  | 103 | 114 | 0.014224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2228-8_0_6_line_108 |  | 104 | 107 | 0.003702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2228-8_0_6_line_109 |  | 105 | 107 | 0.02758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2228-8_0_6_line_110 |  | 106 | 108 | 0.017824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2228-8_0_6_line_111 |  | 107 | 111 | 0.013261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2228-8_0_6_line_112 |  | 108 | 112 | 0.033267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_2228-8_0_6_line_113 |  | 108 | 113 | 0.014761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2228-8_0_6_line_114 |  | 109 | 110 | 0.0013626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2228-8_0_6_line_115 |  | 110 | 115 | 0.018226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_2228-8_0_6_line_116 |  | 112 | 115 | 0.0107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_2228-8_0_6_line_117 |  | 113 | 116 | 0.00058913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2228-8_0_6_line_118 |  | 115 | 117 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2228-8_0_6_line_119 |  | 118 | 119 | 0.024191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2228-8_0_6_line_120 |  | 119 | 120 | 0.014602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2228-8_0_6_line_121 |  | 120 | 121 | 0.021521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2228-8_0_6_line_122 |  | 121 | 128 | 0.13319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2228-8_0_6_line_123 |  | 122 | 123 | 0.022388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2228-8_0_6_line_124 |  | 122 | 124 | 0.024974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2228-8_0_6_line_125 |  | 123 | 125 | 0.014122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2228-8_0_6_line_126 |  | 123 | 126 | 0.0047668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2228-8_0_6_line_127 |  | 124 | 127 | 0.020164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2228-8_0_6_line_128 |  | 126 | 128 | 0.1506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2228-8_0_6_line_129 |  | 127 | 129 | 0.0032737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2228-8_0_6_trafo_51 | 0.63 MVA 20/0.4 kV | 131 | 65 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2575467.5525 | 1182160.5955 | 2575468.9674 | 1182147.1949
1 | 2575465.1387 | 1182172.0034 | 2575467.4771 | 1182161.3104 | 2575467.5525 | 1182160.5955
2 | 2575468.9674 | 1182147.1949 | 2575470.8578 | 1182129.291 | 2575474.5822 | 1182121.4411
3 | 2575471.477 | 1182174.0673 | 2575465.1387 | 1182172.0034
4 | 2575445.3025 | 1182166.6043 | 2575452.227 | 1182170.0999 | 2575464.3368 | 1182175.6641 | 2575465.1387 | 1182172.0034
5 | 2575477.4242 | 1182115.451 | 2575474.5822 | 1182121.4411
6 | 2575471.477 | 1182174.0673 | 2575473.9419 | 1182166.2976 | 2575500.4139 | 1182169.1488
7 | 2575445.3025 | 1182166.6043 | 2575451.7809 | 1182148.9018
8 | 2575445.3025 | 1182166.6043 | 2575435.4424 | 1182162.2315
9 | 2575512.2877 | 1182173.8442 | 2575510.5574 | 1182168.9932 | 2575505.4598 | 1182169.6922 | 2575500.4139 | 1182169.1488
10 | 2575494.5654 | 1182181.2096 | 2575498.8518 | 1182178.1793 | 2575503.7593 | 1182175.8135 | 2575512.2877 | 1182173.8442
11 | 2575494.5654 | 1182181.2096 | 2575497.2073 | 1182188.6471 | 2575498.51 | 1182190.3294
12 | 2575520.1504 | 1182171.5552 | 2575512.2877 | 1182173.8442
13 | 2575522.7165 | 1182204.5262 | 2575501.2833 | 1182193.9109 | 2575498.51 | 1182190.3294
14 | 2575445.5204 | 1182290.09 | 2575436.8363 | 1182285.7123 | 2575421.0461 | 1182278.2067 | 2575412.1973 | 1182287.6147 | 2575405.6664 | 1182275.8354 | 2575407.5282 | 1182273.7044 | 2575405.4227 | 1182259.3167 | 2575407.5761 | 1182257.518 | 2575442.9991 | 1182239.5851 | 2575450.2331 | 1182236.6872 | 2575455.4354 | 1182235.4652 | 2575458.3953 | 1182232.9517
15 | 2575458.3953 | 1182232.9517 | 2575458.6636 | 1182229.5155 | 2575457.4474 | 1182227.1192 | 2575455.0202 | 1182225.4617 | 2575447.4841 | 1182223.6362 | 2575443.3901 | 1182221.4296 | 2575440.0302 | 1182217.6415 | 2575438.7033 | 1182212.4665 | 2575440.6426 | 1182208.7454 | 2575446.2115 | 1182207.5219 | 2575494.9029 | 1182216.9157
16 | 2575445.5204 | 1182290.09 | 2575452.563 | 1182293.3189
17 | 2575463.2158 | 1182298.203 | 2575452.563 | 1182293.3189
18 | 2575586.8344 | 1182082.7915 | 2575593.5085 | 1182088.545 | 2575602.8659 | 1182106.2827 | 2575608.9943 | 1182113.039 | 2575621.578 | 1182120.6026 | 2575626.1778 | 1182117.649 | 2575638.5505 | 1182112.796 | 2575641.9533 | 1182099.0527
19 | 2575586.8344 | 1182082.7915 | 2575593.2031 | 1182073.6163 | 2575602.7444 | 1182065.3619 | 2575642.1586 | 1182038.9762 | 2575647.2055 | 1182046.4039
20 | 2575586.8344 | 1182082.7915 | 2575582.691 | 1182089.0451 | 2575581.0448 | 1182093.5319 | 2575581.3968 | 1182099.3335 | 2575584.4823 | 1182106.9693 | 2575586.7761 | 1182118.9328 | 2575586.2631 | 1182126.0608 | 2575584.2792 | 1182131.6627
21 | 2575641.9533 | 1182099.0527 | 2575661.966 | 1182085.6089
22 | 2575647.2055 | 1182046.4039 | 2575656.3971 | 1182040.411
23 | 2575580.8355 | 1182148.7726 | 2575580.9207 | 1182147.1937 | 2575581.9385 | 1182138.4072 | 2575584.2326 | 1182131.7944 | 2575584.2792 | 1182131.6627
24 | 2575456.3299 | 1182381.5102 | 2575449.3593 | 1182373.2286 | 2575436.6399 | 1182364.1651
25 | 2575472.7375 | 1182402.7479 | 2575459.1036 | 1182384.8057 | 2575456.3299 | 1182381.5102
26 | 2575520.1504 | 1182171.5552 | 2575522.1263 | 1182165.5439 | 2575524.3237 | 1182152.5057
27 | 2575546.3469 | 1182216.0821 | 2575534.7869 | 1182210.5044 | 2575522.7165 | 1182204.5262
28 | 2575479.1409 | 1182305.5043 | 2575463.2158 | 1182298.203
29 | 2575682.6142 | 1182206.2761 | 2575687.3386 | 1182194.5508 | 2575696.9861 | 1182171.1327 | 2575700.123 | 1182163.327 | 2575708.1952 | 1182144.929 | 2575710.6149 | 1182140.9838 | 2575720.5666 | 1182124.7459 | 2575737.77 | 1182104.2209 | 2575741.1822 | 1182100.2383 | 2575751.4506 | 1182092.3814
30 | 2575751.4506 | 1182092.3814 | 2575747.6624 | 1182090.2735 | 2575728.7781 | 1182063.603 | 2575722.248 | 1182049.2868
31 | 2575670.2971 | 1182237.8094 | 2575676.8316 | 1182220.6183 | 2575682.6142 | 1182206.2761
32 | 2575682.6142 | 1182206.2761 | 2575663.7131 | 1182199.5237
33 | 2575720.6038 | 1182045.6824 | 2575722.248 | 1182049.2868
34 | 2575670.2971 | 1182237.8094 | 2575670.318 | 1182242.9564 | 2575672.3466 | 1182246.0943
35 | 2575652.678 | 1182195.5814 | 2575663.7131 | 1182199.5237
36 | 2575580.8355 | 1182148.7726 | 2575592.5269 | 1182150.9927 | 2575596.2184 | 1182151.7628
37 | 2575580.8355 | 1182148.7726 | 2575580.536 | 1182153.9321 | 2575579.3908 | 1182161.4407 | 2575577.1143 | 1182165.8304
38 | 2575528.1063 | 1182125.9231 | 2575528.7568 | 1182120.7067
39 | 2575528.1063 | 1182125.9231 | 2575526.1217 | 1182141.8374 | 2575524.3237 | 1182152.5057
40 | 2575546.3469 | 1182216.0821 | 2575547.1971 | 1182212.9993 | 2575551.3729 | 1182199.7642 | 2575558.7419 | 1182201.8351
41 | 2575558.7419 | 1182201.8351 | 2575564.9949 | 1182203.5882
42 | 2575546.3469 | 1182216.0821 | 2575552.3774 | 1182219.4592 | 2575565.6996 | 1182228.6518
43 | 2575563.467 | 1182194.0673 | 2575567.0639 | 1182196.0758 | 2575564.9949 | 1182203.5882
44 | 2575563.467 | 1182194.0673 | 2575564.0706 | 1182192.3083 | 2575565.1942 | 1182192.5928 | 2575569.0847 | 1182193.5774 | 2575570.3152 | 1182193.8836 | 2575573.1112 | 1182183.0332 | 2575564.5069 | 1182181.3786
45 | 2575564.5069 | 1182181.3786 | 2575575.959 | 1182168.0582 | 2575577.1143 | 1182165.8304
46 | 2575567.9289 | 1182230.19 | 2575578.2025 | 1182227.4355 | 2575583.9572 | 1182223.1208 | 2575587.5614 | 1182215.7356 | 2575588.2739 | 1182212.5866
47 | 2575588.2739 | 1182212.5866 | 2575607.3072 | 1182217.767 | 2575628.8763 | 1182223.1484 | 2575629.8962 | 1182223.4332
48 | 2575567.9289 | 1182230.19 | 2575574.3454 | 1182235.8404
49 | 2575567.9289 | 1182230.19 | 2575565.6996 | 1182228.6518
50 | 2575600.4814 | 1182189.8026 | 2575605.6074 | 1182166.8674
51 | 2575600.4814 | 1182189.8026 | 2575612.0476 | 1182192.8505
52 | 2575608.4146 | 1182154.3073 | 2575605.6074 | 1182166.8674
53 | 2575622.1665 | 1182195.517 | 2575612.0476 | 1182192.8505
54 | 2575603.6316 | 1182256.1587 | 2575578.2203 | 1182239.2527 | 2575574.3454 | 1182235.8404
55 | 2575597.0515 | 1182151.9366 | 2575596.2184 | 1182151.7628
56 | 2575608.4146 | 1182154.3073 | 2575597.0515 | 1182151.9366
57 | 2575608.4146 | 1182154.3073 | 2575619.2417 | 1182156.4174
58 | 2575622.1665 | 1182195.517 | 2575649.8549 | 1182203.5638 | 2575652.678 | 1182195.5814
59 | 2575672.3466 | 1182246.0943 | 2575605.0328 | 1182227.3369
60 | 2575652.678 | 1182195.5814 | 2575658.9019 | 1182177.9827
61 | 2575658.9658 | 1182177.8021 | 2575658.9019 | 1182177.9827
62 | 2575689.465 | 1182315.4273 | 2575702.4299 | 1182324.8683
63 | 2575689.465 | 1182315.4273 | 2575685.2687 | 1182312.454 | 2575653.7785 | 1182289.4258 | 2575626.3517 | 1182271.2516
64 | 2575702.4299 | 1182324.8683 | 2575692.849 | 1182343.6992
65 | 2575616.3116 | 1182264.5946 | 2575617.7798 | 1182265.5714 | 2575626.3517 | 1182271.2516
66 | 2575616.3116 | 1182264.5946 | 2575603.6316 | 1182256.1587
67 | 2575690.9468 | 1182347.4379 | 2575692.849 | 1182343.6992
68 | 2575479.1409 | 1182305.5043 | 2575478.3686 | 1182307.0972 | 2575472.7047 | 1182310.2607
69 | 2575470.6289 | 1182311.4201 | 2575472.7047 | 1182310.2607
70 | 2575479.1409 | 1182305.5043 | 2575481.2377 | 1182301.0712 | 2575495.8872 | 1182307.063
71 | 2575495.8872 | 1182307.063 | 2575510.4077 | 1182313.0021 | 2575529.9629 | 1182319.4589
72 | 2575553.25 | 1182326.1899 | 2575544.2625 | 1182324.1803 | 2575529.9629 | 1182319.4589
73 | 2575553.6793 | 1182326.2859 | 2575553.25 | 1182326.1899
74 | 2575472.7375 | 1182402.7479 | 2575482.605 | 1182388.213
75 | 2575472.7375 | 1182402.7479 | 2575487.4096 | 1182418.8294 | 2575513.8599 | 1182441.6883 | 2575522.3955 | 1182447.1451
76 | 2575493.0545 | 1182387.8456 | 2575486.3981 | 1182382.6258 | 2575482.605 | 1182388.213
77 | 2575522.3955 | 1182447.1451 | 2575541.8764 | 1182466.6865 | 2575560.4839 | 1182483.6748 | 2575580.1871 | 1182499.747 | 2575586.545 | 1182502.9782 | 2575595.3999 | 1182506.2882 | 2575596.556 | 1182507.0728 | 2575597.677 | 1182506.7347 | 2575609.6091 | 1182506.3746 | 2575611.2386 | 1182505.3119 | 2575640.8618 | 1182497.6425
78 | 2575522.3955 | 1182447.1451 | 2575529.4187 | 1182435.7214 | 2575531.5357 | 1182429.7912
79 | 2575640.8618 | 1182497.6425 | 2575642.8184 | 1182496.256 | 2575643.7642 | 1182494.1511 | 2575642.206 | 1182488.3766 | 2575641.0633 | 1182483.4009 | 2575641.384 | 1182477.7967 | 2575643.9749 | 1182474.6956 | 2575668.8709 | 1182457.3407
80 | 2575640.8618 | 1182497.6425 | 2575633.3328 | 1182489.9581 | 2575620.6119 | 1182478.5041 | 2575612.7863 | 1182475.3505
81 | 2575640.8618 | 1182497.6425 | 2575611.2386 | 1182505.3119 | 2575609.6091 | 1182506.3746 | 2575603.2497 | 1182521.4529 | 2575614.0602 | 1182530.6469 | 2575619.7277 | 1182533.0806 | 2575634.633 | 1182535.3876
82 | 2575640.8618 | 1182497.6425 | 2575655.3651 | 1182509.9231
83 | 2575531.5357 | 1182429.7912 | 2575535.7141 | 1182418.0865 | 2575538.0577 | 1182404.9478 | 2575528.8359 | 1182401.1352
84 | 2575634.633 | 1182535.3876 | 2575640.7312 | 1182535.9135
85 | 2575640.7312 | 1182535.9135 | 2575647.6782 | 1182536.5127 | 2575666.7657 | 1182540.2591 | 2575674.6625 | 1182541.9415
86 | 2575655.3651 | 1182509.9231 | 2575663.0949 | 1182510.7031 | 2575668.2022 | 1182511.2942
87 | 2575668.2022 | 1182511.2942 | 2575685.9191 | 1182513.3448 | 2575712.7853 | 1182514.6486
88 | 2575668.8709 | 1182457.3407 | 2575679.4092 | 1182444.5293
89 | 2575596.9338 | 1182470.6189 | 2575604.8271 | 1182472.143 | 2575612.7863 | 1182475.3505
90 | 2575674.6625 | 1182541.9415 | 2575680.4366 | 1182543.1716 | 2575752.571 | 1182559.6969
91 | 2575712.7853 | 1182514.6486 | 2575713.8692 | 1182514.7012
92 | 2575735.3423 | 1182408.567 | 2575697.8876 | 1182424.4165 | 2575691.3594 | 1182430.0015 | 2575679.4092 | 1182444.5293
93 | 2575596.9338 | 1182470.6189 | 2575587.5176 | 1182470.1016 | 2575574.2829 | 1182463.7413 | 2575575.4094 | 1182454.4909
94 | 2575571.1445 | 1182330.1911 | 2575553.6793 | 1182326.2859
95 | 2575571.1445 | 1182330.1911 | 2575573.4101 | 1182330.6977 | 2575584.9638 | 1182333.7246
96 | 2575584.9638 | 1182333.7246 | 2575592.8599 | 1182335.7932
97 | 2575593.0613 | 1182335.846 | 2575592.8599 | 1182335.7932
98 | 2575613.1866 | 1182341.1184 | 2575593.0613 | 1182335.846
99 | 2575613.1866 | 1182341.1184 | 2575606.5523 | 1182379.4166
100 | 2575613.1866 | 1182341.1184 | 2575620.5665 | 1182334.696
101 | 2575690.9468 | 1182347.4379 | 2575675.3493 | 1182344.6126
102 | 2575690.9468 | 1182347.4379 | 2575690.0071 | 1182369.9354
103 | 2575606.081 | 1182382.1372 | 2575606.5523 | 1182379.4166
104 | 2575634.055 | 1182337.1361 | 2575620.5665 | 1182334.696 | 2575620.5665 | 1182334.696
105 | 2575606.081 | 1182382.1372 | 2575604.3623 | 1182392.0587
106 | 2575644.5685 | 1182339.0379 | 2575634.055 | 1182337.1361
107 | 2575615.3557 | 1182401.0852 | 2575604.3623 | 1182392.0587
108 | 2575648.2113 | 1182339.6969 | 2575644.5685 | 1182339.0379
109 | 2575648.2113 | 1182339.6969 | 2575675.3493 | 1182344.6126
110 | 2575689.2632 | 1182387.7436 | 2575690.0071 | 1182369.9354
111 | 2575648.2113 | 1182339.6969 | 2575646.4936 | 1182352.8441
112 | 2575689.2632 | 1182387.7436 | 2575722.4503 | 1182390.0478
113 | 2575689.2632 | 1182387.7436 | 2575688.3795 | 1182402.4777
114 | 2575735.3423 | 1182408.567 | 2575736.5974 | 1182408.0365
115 | 2575735.3423 | 1182408.567 | 2575732.8015 | 1182401.4847 | 2575733.1245 | 1182390.789
116 | 2575733.1245 | 1182390.789 | 2575722.4503 | 1182390.0478
117 | 2575688.3442 | 1182403.0658 | 2575688.3795 | 1182402.4777
118 | 2575743.6945 | 1182391.5131 | 2575733.1245 | 1182390.789
119 | 2575738.0217 | 1182516.0374 | 2575730.9365 | 1182515.5295 | 2575713.8692 | 1182514.7012
120 | 2575738.0217 | 1182516.0374 | 2575752.5866 | 1182517.0816
121 | 2575774.0562 | 1182518.5671 | 2575771.1466 | 1182518.4122 | 2575752.5866 | 1182517.0816
122 | 2575774.0562 | 1182518.5671 | 2575808.5895 | 1182518.5938 | 2575816.9348 | 1182518.6378 | 2575855.901 | 1182519.8029 | 2575868.9632 | 1182519.4944 | 2575876.7499 | 1182519.2295 | 2575897.0644 | 1182518.6694 | 2575907.1856 | 1182517.9615
123 | 2575776.7158 | 1182440.2044 | 2575754.3333 | 1182439.702
124 | 2575729.3728 | 1182438.9071 | 2575742.3241 | 1182439.4325 | 2575754.3333 | 1182439.702
125 | 2575776.7158 | 1182440.2044 | 2575776.8953 | 1182454.3221
126 | 2575776.7158 | 1182440.2044 | 2575781.4813 | 1182440.3137
127 | 2575729.3728 | 1182438.9071 | 2575732.0271 | 1182458.8956
128 | 2575907.1856 | 1182517.9615 | 2575905.8456 | 1182515.1098 | 2575816.5455 | 1182450.8374 | 2575803.9321 | 1182443.2623 | 2575789.4829 | 1182440.4972 | 2575781.4813 | 1182440.3137
129 | 2575728.784 | 1182459.3423 | 2575732.0271 | 1182458.8956

## bus_geodata
| x | y | coords
0 | 2575467.5525 | 1182160.5955
1 | 2575468.9674 | 1182147.1949
2 | 2575465.1387 | 1182172.0034
3 | 2575474.5822 | 1182121.4411
4 | 2575471.477 | 1182174.0673
5 | 2575445.3025 | 1182166.6043
6 | 2575477.4242 | 1182115.451
7 | 2575500.4139 | 1182169.1488
8 | 2575451.7809 | 1182148.9018
9 | 2575435.4424 | 1182162.2315
10 | 2575494.5654 | 1182181.2096
11 | 2575512.2877 | 1182173.8442
12 | 2575498.51 | 1182190.3294
13 | 2575458.3953 | 1182232.9517
14 | 2575445.5204 | 1182290.09
15 | 2575494.9029 | 1182216.9157
16 | 2575452.563 | 1182293.3189
17 | 2575586.8344 | 1182082.7915
18 | 2575641.9533 | 1182099.0527
19 | 2575647.2055 | 1182046.4039
20 | 2575584.2792 | 1182131.6627
21 | 2575656.3971 | 1182040.411
22 | 2575436.6399 | 1182364.1651
23 | 2575456.3299 | 1182381.5102
24 | 2575520.1504 | 1182171.5552
25 | 2575522.7165 | 1182204.5262
26 | 2575463.2158 | 1182298.203
27 | 2575661.966 | 1182085.6089
28 | 2575751.4506 | 1182092.3814
29 | 2575682.6142 | 1182206.2761
30 | 2575722.248 | 1182049.2868
31 | 2575670.2971 | 1182237.8094
32 | 2575663.7131 | 1182199.5237
33 | 2575580.8355 | 1182148.7726
34 | 2575528.7568 | 1182120.7067
35 | 2575528.1063 | 1182125.9231
36 | 2575524.3237 | 1182152.5057
37 | 2575558.7419 | 1182201.8351
38 | 2575546.3469 | 1182216.0821
39 | 2575564.9949 | 1182203.5882
40 | 2575564.5069 | 1182181.3786
41 | 2575563.467 | 1182194.0673
42 | 2575577.1143 | 1182165.8304
43 | 2575588.2739 | 1182212.5866
44 | 2575567.9289 | 1182230.19
45 | 2575629.8962 | 1182223.4332
46 | 2575565.6996 | 1182228.6518
47 | 2575600.4814 | 1182189.8026
48 | 2575605.6074 | 1182166.8674
49 | 2575612.0476 | 1182192.8505
50 | 2575574.3454 | 1182235.8404
51 | 2575596.2184 | 1182151.7628
52 | 2575597.0515 | 1182151.9366
53 | 2575608.4146 | 1182154.3073
54 | 2575622.1665 | 1182195.517
55 | 2575720.6038 | 1182045.6824
56 | 2575672.3466 | 1182246.0943
57 | 2575652.678 | 1182195.5814
58 | 2575658.9019 | 1182177.9827
59 | 2575619.2417 | 1182156.4174
60 | 2575658.9658 | 1182177.8021
61 | 2575605.0328 | 1182227.3369
62 | 2575689.465 | 1182315.4273
63 | 2575702.4299 | 1182324.8683
64 | 2575626.3517 | 1182271.2516
65 | 2575603.6317 | 1182256.1587
66 | 2575616.3116 | 1182264.5946
67 | 2575692.849 | 1182343.6992
68 | 2575472.7047 | 1182310.2607
69 | 2575479.1409 | 1182305.5043
70 | 2575470.6289 | 1182311.4201
71 | 2575495.8872 | 1182307.063
72 | 2575529.9629 | 1182319.4589
73 | 2575553.25 | 1182326.1899
74 | 2575472.7375 | 1182402.7479
75 | 2575482.605 | 1182388.213
76 | 2575522.3955 | 1182447.1451
77 | 2575493.0545 | 1182387.8456
78 | 2575640.8618 | 1182497.6425
79 | 2575531.5357 | 1182429.7912
80 | 2575634.633 | 1182535.3876
81 | 2575640.7312 | 1182535.9135
82 | 2575655.3651 | 1182509.9231
83 | 2575668.2022 | 1182511.2942
84 | 2575668.8709 | 1182457.3407
85 | 2575612.7863 | 1182475.3505
86 | 2575528.8359 | 1182401.1352
87 | 2575674.6625 | 1182541.9415
88 | 2575712.7853 | 1182514.6486
89 | 2575679.4092 | 1182444.5293
90 | 2575596.9338 | 1182470.6189
91 | 2575752.571 | 1182559.6969
92 | 2575553.6793 | 1182326.2859
93 | 2575571.1445 | 1182330.1911
94 | 2575584.9638 | 1182333.7246
95 | 2575592.8599 | 1182335.7932
96 | 2575593.0613 | 1182335.846
97 | 2575613.1866 | 1182341.1184
98 | 2575690.9468 | 1182347.4379
99 | 2575606.5523 | 1182379.4166
100 | 2575620.5665 | 1182334.696
101 | 2575606.081 | 1182382.1372
102 | 2575634.055 | 1182337.136
103 | 2575604.3623 | 1182392.0587
104 | 2575644.5685 | 1182339.0379
105 | 2575675.3493 | 1182344.6126
106 | 2575690.0071 | 1182369.9354
107 | 2575648.2113 | 1182339.6969
108 | 2575689.2632 | 1182387.7436
109 | 2575736.5974 | 1182408.0365
110 | 2575735.3423 | 1182408.567
111 | 2575646.4936 | 1182352.8441
112 | 2575722.4503 | 1182390.0478
113 | 2575688.3795 | 1182402.4777
114 | 2575615.3557 | 1182401.0852
115 | 2575733.1245 | 1182390.789
116 | 2575688.3442 | 1182403.0658
117 | 2575743.6945 | 1182391.5131
118 | 2575713.8692 | 1182514.7012
119 | 2575738.0217 | 1182516.0374
120 | 2575752.5866 | 1182517.0816
121 | 2575774.0562 | 1182518.5671
122 | 2575754.3333 | 1182439.702
123 | 2575776.7158 | 1182440.2044
124 | 2575729.3728 | 1182438.9071
125 | 2575776.8953 | 1182454.3221
126 | 2575781.4813 | 1182440.3137
127 | 2575732.0271 | 1182458.8956
128 | 2575907.1856 | 1182517.9615
129 | 2575728.784 | 1182459.3423
130 | 2575575.4094 | 1182454.4909
131 | 2575567.9289 | 1182230.19

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9837 | -0.31342 | 0.0020092 | 0.00050355
1 | 0.98344 | -0.31839 | 0.0097505 | 0.0024437
2 | 0.98394 | -0.3087 | 0 | 0
3 | 0.98318 | -0.32354 | 0.0041425 | 0.0010382
4 | 0.98416 | -0.30442 | 0 | 0
5 | 0.98364 | -0.31465 | 0 | 0
6 | 0.98314 | -0.32433 | 0.006565 | 0.0016453
7 | 0.98531 | -0.28207 | 0.016052 | 0.004023
8 | 0.98348 | -0.31771 | 0.009032 | 0.0022636
9 | 0.98359 | -0.31547 | 0.0042546 | 0.0010663
10 | 0.98788 | -0.23205 | 0 | 0
11 | 0.98604 | -0.26779 | 0 | 0
12 | 0.98883 | -0.21365 | 0.0026626 | 0.00066731
13 | 0.98299 | -0.32704 | 0 | 0
14 | 0.98312 | -0.32451 | 0 | 0
15 | 0.9829 | -0.32881 | 0.0010706 | 0.00026833
16 | 0.98313 | -0.32436 | 0.0016289 | 0.00040824
17 | 0.98486 | -0.29076 | 0 | 0
18 | 0.98205 | -0.34555 | 0 | 0
19 | 0.98481 | -0.29177 | 0 | 0
20 | 0.98658 | -0.25723 | 0.022331 | 0.0055967
21 | 0.9848 | -0.29191 | 0.00069547 | 0.0001743
22 | 0.97848 | -0.41436 | 0.0062614 | 0.0015693
23 | 0.97863 | -0.41135 | 0.0041539 | 0.0010411
24 | 0.98565 | -0.27527 | 0 | 0
25 | 0.9916 | -0.16025 | 0.0027872 | 0.00069854
26 | 0.98316 | -0.32379 | 0.0036523 | 0.00091536
27 | 0.98126 | -0.36104 | 0.035522 | 0.0089026
28 | 0.9822 | -0.3427 | 0 | 0
29 | 0.9827 | -0.33294 | 0 | 0
30 | 0.98201 | -0.34651 | 0.00070479 | 0.00017664
31 | 0.98262 | -0.33455 | 0 | 0
32 | 0.98283 | -0.33053 | 0.010634 | 0.0026652
33 | 0.98753 | -0.23883 | 0 | 0
34 | 0.98371 | -0.31322 | 0.022716 | 0.0056932
35 | 0.98382 | -0.31107 | 0.014228 | 0.0035658
36 | 0.98473 | -0.29322 | 0.014177 | 0.0035531
37 | 0.99308 | -0.13173 | 0 | 0
38 | 0.99423 | -0.10984 | 0 | 0
39 | 0.99278 | -0.13749 | 0.0061964 | 0.001553
40 | 0.99101 | -0.17171 | 0 | 0
41 | 0.99226 | -0.14762 | 0 | 0
42 | 0.98967 | -0.19743 | 0.013125 | 0.0032895
43 | 0.99601 | -0.075807 | 0 | 0
44 | 0.99628 | -0.070631 | 0 | 0
45 | 0.99562 | -0.083426 | 0.010078 | 0.0025257
46 | 0.99606 | -0.074771 | 0.0022734 | 0.00056977
47 | 0.98465 | -0.29499 | 0 | 0
48 | 0.98547 | -0.27898 | 0.0033181 | 0.00083161
49 | 0.98423 | -0.30315 | 0.010304 | 0.0025825
50 | 0.99699 | -0.057071 | 0.0032793 | 0.00082186
51 | 0.98649 | -0.25917 | 0.012916 | 0.0032369
52 | 0.98644 | -0.26008 | 0.014556 | 0.0036482
53 | 0.98596 | -0.26945 | 0 | 0
54 | 0.98396 | -0.30835 | 0 | 0
55 | 0.982 | -0.34675 | 0.0032933 | 0.00082537
56 | 0.9826 | -0.33498 | 0 | 0
57 | 0.98301 | -0.32687 | 0 | 0
58 | 0.98283 | -0.33035 | 0.0051318 | 0.0012861
59 | 0.98592 | -0.27021 | 0.0038183 | 0.00095697
60 | 0.98283 | -0.33037 | 0.0052036 | 0.0013041
61 | 0.98243 | -0.3383 | 0.0026409 | 0.00066186
62 | 0.99353 | -0.12294 | 0 | 0
63 | 0.99255 | -0.1417 | 0 | 0
64 | 0.99825 | -0.033119 | 0.005352 | 0.0013413
65 | 1 | 0 | -0.495 | -0.12632
66 | 0.99901 | -0.018779 | 0.007683 | 0.0019255
67 | 0.99125 | -0.16653 | 0.003447 | 0.0008639
68 | 0.98322 | -0.32259 | 0.0024704 | 0.00061915
69 | 0.98326 | -0.32178 | 0 | 0
70 | 0.98321 | -0.32271 | 0.0029543 | 0.00074043
71 | 0.98348 | -0.31737 | 0.0023337 | 0.00058489
72 | 0.98396 | -0.30815 | 0.0043387 | 0.0010874
73 | 0.98437 | -0.30008 | 0.0033792 | 0.0008469
74 | 0.97889 | -0.40626 | 0 | 0
75 | 0.97881 | -0.40792 | 0.0013762 | 0.0003449
76 | 0.97986 | -0.3873 | 0 | 0
77 | 0.97876 | -0.40897 | 0.00381 | 0.00095488
78 | 0.98301 | -0.32567 | 0 | 0
79 | 0.97971 | -0.39031 | 0.0037091 | 0.00092959
80 | 0.98216 | -0.34228 | 0 | 0
81 | 0.9821 | -0.34349 | 0.0024949 | 0.00062529
82 | 0.98269 | -0.33196 | 0 | 0
83 | 0.98236 | -0.33838 | 0.0092379 | 0.0023152
84 | 0.98471 | -0.29264 | 0 | 0
85 | 0.98272 | -0.33135 | 0.0024318 | 0.00060947
86 | 0.97955 | -0.39335 | 0.00469 | 0.0011754
87 | 0.98183 | -0.34873 | 0.0037316 | 0.00093522
88 | 0.98141 | -0.35691 | 0.0040009 | 0.0010027
89 | 0.98522 | -0.28284 | 0.0034006 | 0.00085227
90 | 0.98263 | -0.33321 | 0 | 0
91 | 0.98149 | -0.35549 | 0.0046752 | 0.0011717
92 | 0.98438 | -0.29991 | 0.0062832 | 0.0015747
93 | 0.98484 | -0.29086 | 0.0013431 | 0.00033661
94 | 0.98523 | -0.28331 | 0.002238 | 0.00056089
95 | 0.98547 | -0.27867 | 0.004172 | 0.0010456
96 | 0.98547 | -0.27853 | 0.002238 | 0.00056089
97 | 0.9862 | -0.26431 | 0 | 0
98 | 0.991 | -0.17138 | 0 | 0
99 | 0.98555 | -0.27707 | 0.0027635 | 0.00069261
100 | 0.98671 | -0.25443 | 0.0012526 | 0.00031392
101 | 0.98551 | -0.27784 | 0.0041583 | 0.0010422
102 | 0.98744 | -0.24028 | 0.002792 | 0.00069973
103 | 0.9854 | -0.2799 | 0.006256 | 0.0015679
104 | 0.98804 | -0.22874 | 0.0026682 | 0.00066871
105 | 0.98996 | -0.19149 | 0.0041126 | 0.0010307
106 | 0.99014 | -0.18792 | 0.0046746 | 0.0011716
107 | 0.98825 | -0.22457 | 0 | 0
108 | 0.98948 | -0.20055 | 0 | 0
109 | 0.98736 | -0.24145 | 0.0042992 | 0.0010775
110 | 0.98736 | -0.24134 | 0 | 0
111 | 0.9882 | -0.22556 | 0.0041789 | 0.0010473
112 | 0.98833 | -0.22281 | 0.002862 | 0.00071729
113 | 0.98939 | -0.20232 | 0.0032661 | 0.00081856
114 | 0.98534 | -0.28121 | 0.0051255 | 0.0012846
115 | 0.98796 | -0.2298 | 0 | 0
116 | 0.98939 | -0.20236 | 0.0035022 | 0.00087774
117 | 0.98793 | -0.23044 | 0.0034196 | 0.00085702
118 | 0.98137 | -0.35773 | 0.0058108 | 0.0014563
119 | 0.98055 | -0.37351 | 0.005304 | 0.0013293
120 | 0.98014 | -0.38164 | 0.0046168 | 0.0011571
121 | 0.97961 | -0.39183 | 0 | 0
122 | 0.97221 | -0.53708 | 0.0042992 | 0.0010775
123 | 0.97261 | -0.5291 | 0 | 0
124 | 0.97186 | -0.54402 | 0 | 0
125 | 0.97259 | -0.52955 | 0.0017302 | 0.00043363
126 | 0.97271 | -0.52725 | 0.0049996 | 0.001253
127 | 0.97157 | -0.54962 | 0.0097252 | 0.0024374
128 | 0.97637 | -0.45515 | 0 | 0
129 | 0.97156 | -0.54994 | 0.005325 | 0.0013346
130 | 0.98244 | -0.33697 | 0.0062236 | 0.0015598
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.020466 | 0.0051316 | -0.020461 | -0.0051287 | 4.8432e-06 | 2.9287e-06 | 0.030959 | 0.030959 | 0.030959 | 0.9837 | -0.31342 | 0.98344 | -0.31839 | 8.5052
1 | -0.022475 | -0.0056352 | 0.02248 | 0.0056382 | 5.056e-06 | 3.0877e-06 | 0.033998 | 0.033998 | 0.033998 | 0.9837 | -0.31342 | 0.98394 | -0.3087 | 9.3401
2 | 0.01071 | 0.002685 | -0.010708 | -0.0026836 | 2.6288e-06 | 1.3438e-06 | 0.016206 | 0.016206 | 0.016206 | 0.98344 | -0.31839 | 0.98318 | -0.32354 | 4.4522
3 | -0.035772 | -0.0089709 | 0.035779 | 0.0089755 | 7.2976e-06 | 4.586e-06 | 0.0541 | 0.0541 | 0.0541 | 0.98394 | -0.3087 | 0.98416 | -0.30442 | 14.8626
4 | 0.013292 | 0.0033326 | -0.013288 | -0.0033305 | 3.7628e-06 | 2.0929e-06 | 0.020102 | 0.020102 | 0.020102 | 0.98394 | -0.3087 | 0.98364 | -0.31465 | 5.5225
5 | 0.0065653 | 0.0016454 | -0.006565 | -0.0016453 | 2.4548e-07 | 7.3027e-08 | 0.0099364 | 0.0099364 | 0.0099364 | 0.98318 | -0.32354 | 0.98314 | -0.32433 | 2.7298
6 | -0.035779 | -0.0089755 | 0.035817 | 0.0089994 | 3.8169e-05 | 2.3986e-05 | 0.0541 | 0.0541 | 0.0541 | 0.98416 | -0.30442 | 0.98531 | -0.28207 | 14.8626
7 | 0.0090334 | 0.0022643 | -0.009032 | -0.0022636 | 1.3199e-06 | 6.0555e-07 | 0.013666 | 0.013666 | 0.013666 | 0.98364 | -0.31465 | 0.98348 | -0.31771 | 3.7543
8 | 0.0042548 | 0.0010663 | -0.0042546 | -0.0010663 | 1.6718e-07 | -2.9591e-08 | 0.0064365 | 0.0064366 | 0.0064366 | 0.98364 | -0.31465 | 0.98359 | -0.31547 | 1.7683
9 | -0.051869 | -0.013022 | 0.051905 | 0.013045 | 3.5376e-05 | 2.2445e-05 | 0.078342 | 0.078342 | 0.078342 | 0.98531 | -0.28207 | 0.98604 | -0.26779 | 21.5225
10 | 0.1033 | 0.02603 | -0.10312 | -0.025918 | 0.00017627 | 0.00011256 | 0.15565 | 0.15565 | 0.15565 | 0.98788 | -0.23205 | 0.98604 | -0.26779 | 42.7598
11 | -0.1033 | -0.02603 | 0.10339 | 0.026088 | 9.1032e-05 | 5.8132e-05 | 0.15565 | 0.15565 | 0.15565 | 0.98788 | -0.23205 | 0.98883 | -0.21365 | 42.7597
12 | 0.051217 | 0.012873 | -0.051199 | -0.012861 | 1.8302e-05 | 1.1609e-05 | 0.077304 | 0.077304 | 0.077304 | 0.98604 | -0.26779 | 0.98565 | -0.27527 | 21.2373
13 | -0.10605 | -0.026756 | 0.10632 | 0.026929 | 0.00027191 | 0.00017366 | 0.15965 | 0.15965 | 0.15965 | 0.98883 | -0.21365 | 0.9916 | -0.16025 | 43.8605
14 | -0.0010707 | -0.00026723 | 0.0010709 | 0.00026566 | 1.2845e-07 | -1.5722e-06 | 0.0016204 | 0.0016199 | 0.0016204 | 0.98299 | -0.32704 | 0.98312 | -0.32451 | 0.44518
15 | 0.0010707 | 0.00026723 | -0.0010706 | -0.00026833 | 8.9994e-08 | -1.1006e-06 | 0.0016204 | 0.0016209 | 0.0016209 | 0.98299 | -0.32704 | 0.9829 | -0.32881 | 0.44529
16 | -0.0010709 | -0.00026566 | 0.0010709 | 0.00026556 | 7.6232e-09 | -9.3362e-08 | 0.0016199 | 0.0016198 | 0.0016199 | 0.98312 | -0.32451 | 0.98313 | -0.32436 | 0.44501
17 | -0.0026998 | -0.0006738 | 0.0026998 | 0.0006737 | 7.3341e-08 | -1.0167e-07 | 0.0040852 | 0.0040852 | 0.0040852 | 0.98313 | -0.32436 | 0.98316 | -0.32379 | 1.1223
18 | 0.035641 | 0.0089776 | -0.035548 | -0.0089191 | 9.3125e-05 | 5.8514e-05 | 0.053866 | 0.053867 | 0.053867 | 0.98486 | -0.29076 | 0.98205 | -0.34555 | 14.7985
19 | 0.00069551 | 0.00017317 | -0.00069547 | -0.00017416 | 3.3195e-08 | -9.992e-07 | 0.0010504 | 0.0010508 | 0.0010508 | 0.98486 | -0.29076 | 0.98481 | -0.29177 | 0.28868
20 | -0.036337 | -0.0091508 | 0.036395 | 0.0091875 | 5.8356e-05 | 3.669e-05 | 0.054917 | 0.054916 | 0.054917 | 0.98486 | -0.29076 | 0.98658 | -0.25723 | 15.087
21 | 0.035548 | 0.0089191 | -0.035522 | -0.0089026 | 2.6233e-05 | 1.6484e-05 | 0.053867 | 0.053867 | 0.053867 | 0.98205 | -0.34555 | 0.98126 | -0.36104 | 14.7985
22 | 0.00069547 | 0.00017416 | -0.00069547 | -0.0001743 | 4.5436e-09 | -1.367e-07 | 0.0010508 | 0.0010508 | 0.0010508 | 0.98481 | -0.29177 | 0.9848 | -0.29191 | 0.28869
23 | -0.058726 | -0.014784 | 0.058778 | 0.014817 | 5.1705e-05 | 3.2867e-05 | 0.088597 | 0.088597 | 0.088597 | 0.98658 | -0.25723 | 0.98753 | -0.23883 | 24.3399
24 | -0.0062614 | -0.0015693 | 0.0062623 | 0.0015695 | 8.9907e-07 | 2.4321e-07 | 0.009522 | 0.0095219 | 0.009522 | 0.97848 | -0.41436 | 0.97863 | -0.41135 | 2.6159
25 | -0.010416 | -0.0026106 | 0.010419 | 0.0026118 | 2.5248e-06 | 1.2786e-06 | 0.015838 | 0.015838 | 0.015838 | 0.97863 | -0.41135 | 0.97889 | -0.40626 | 4.3511
26 | 0.051199 | 0.012861 | -0.051155 | -0.012833 | 4.381e-05 | 2.779e-05 | 0.077304 | 0.077304 | 0.077304 | 0.98565 | -0.27527 | 0.98473 | -0.29322 | 21.2373
27 | -0.10911 | -0.027628 | 0.10938 | 0.027797 | 0.00026478 | 0.00016912 | 0.16383 | 0.16383 | 0.16383 | 0.9916 | -0.16025 | 0.99423 | -0.10984 | 45.0095
28 | -0.0063521 | -0.0015891 | 0.0063527 | 0.0015892 | 6.0709e-07 | 1.6636e-07 | 0.009613 | 0.0096129 | 0.009613 | 0.98316 | -0.32379 | 0.98326 | -0.32178 | 2.6409
29 | -0.0039988 | -0.0010018 | 0.0040007 | 0.0010013 | 1.8591e-06 | -5.2096e-07 | 0.006058 | 0.0060574 | 0.006058 | 0.9822 | -0.3427 | 0.9827 | -0.33294 | 1.6643
30 | 0.0039988 | 0.0010018 | -0.0039981 | -0.001002 | 7.2597e-07 | -2.0287e-07 | 0.006058 | 0.0060582 | 0.0060582 | 0.9822 | -0.3427 | 0.98201 | -0.34651 | 1.6643
31 | 0.0026415 | 0.00066087 | -0.0026413 | -0.00066117 | 2.0304e-07 | -2.9886e-07 | 0.0039994 | 0.0039996 | 0.0039996 | 0.9827 | -0.33294 | 0.98262 | -0.33455 | 1.0988
32 | -0.0066422 | -0.0016621 | 0.006643 | 0.0016624 | 7.6123e-07 | 2.3287e-07 | 0.010057 | 0.010057 | 0.010057 | 0.9827 | -0.33294 | 0.98283 | -0.33053 | 2.7629
33 | 0.0032933 | 0.00082534 | -0.0032933 | -0.00082537 | 3.6996e-08 | -2.6443e-08 | 0.0049902 | 0.0049903 | 0.0049903 | 0.98201 | -0.34651 | 0.982 | -0.34675 | 1.371
34 | 0.0026413 | 0.00066117 | -0.0026413 | -0.00066125 | 5.3282e-08 | -7.8408e-08 | 0.0039996 | 0.0039996 | 0.0039996 | 0.98262 | -0.33455 | 0.9826 | -0.33498 | 1.0988
35 | -0.017277 | -0.0043275 | 0.01728 | 0.0043293 | 3.0065e-06 | 1.7757e-06 | 0.026157 | 0.026157 | 0.026157 | 0.98283 | -0.33053 | 0.98301 | -0.32687 | 7.186
36 | 0.072717 | 0.018295 | -0.072647 | -0.01825 | 7.0587e-05 | 4.4975e-05 | 0.1096 | 0.1096 | 0.1096 | 0.98753 | -0.23883 | 0.98649 | -0.25917 | 30.1087
37 | -0.1315 | -0.033112 | 0.13176 | 0.033279 | 0.00026085 | 0.00016672 | 0.19819 | 0.19819 | 0.19819 | 0.98753 | -0.23883 | 0.98967 | -0.19743 | 54.4486
38 | -0.022716 | -0.0056932 | 0.022718 | 0.0056946 | 2.3275e-06 | 1.4229e-06 | 0.034362 | 0.034362 | 0.034362 | 0.98371 | -0.31322 | 0.98382 | -0.31107 | 9.44
39 | -0.036946 | -0.0092604 | 0.036978 | 0.0092802 | 3.1449e-05 | 1.9786e-05 | 0.055881 | 0.055881 | 0.055881 | 0.98382 | -0.31107 | 0.98473 | -0.29322 | 15.3519
40 | -0.15154 | -0.038413 | 0.1517 | 0.038514 | 0.00015959 | 0.00010118 | 0.22721 | 0.22721 | 0.22721 | 0.99308 | -0.13173 | 0.99423 | -0.10984 | 20.8071
41 | 0.15154 | 0.038413 | -0.15149 | -0.038386 | 4.1908e-05 | 2.6569e-05 | 0.22721 | 0.22721 | 0.22721 | 0.99308 | -0.13173 | 0.99278 | -0.13749 | 20.8071
42 | -0.26107 | -0.066311 | 0.26151 | 0.066592 | 0.00044151 | 0.00028166 | 0.39105 | 0.39105 | 0.39105 | 0.99423 | -0.10984 | 0.99606 | -0.074771 | 35.8102
43 | 0.1453 | 0.036833 | -0.14523 | -0.036788 | 7.0714e-05 | 4.4795e-05 | 0.21793 | 0.21793 | 0.21793 | 0.99278 | -0.13749 | 0.99226 | -0.14762 | 19.9566
44 | -0.14506 | -0.036682 | 0.14523 | 0.036788 | 0.00016781 | 0.0001063 | 0.21793 | 0.21793 | 0.21793 | 0.99101 | -0.17171 | 0.99226 | -0.14762 | 19.9567
45 | 0.14506 | 0.036682 | -0.14488 | -0.036568 | 0.00017877 | 0.0001139 | 0.21793 | 0.21793 | 0.21793 | 0.99101 | -0.17171 | 0.98967 | -0.19743 | 29.935
46 | -0.010081 | -0.0025275 | 0.010084 | 0.0025287 | 2.4868e-06 | 1.211e-06 | 0.015062 | 0.015062 | 0.015062 | 0.99601 | -0.075807 | 0.99628 | -0.070631 | 4.1379
47 | 0.010081 | 0.0025275 | -0.010078 | -0.0025257 | 3.6594e-06 | 1.7824e-06 | 0.015062 | 0.015062 | 0.015062 | 0.99601 | -0.075807 | 0.99562 | -0.083426 | 4.1379
48 | -0.27392 | -0.069725 | 0.2741 | 0.069839 | 0.00017922 | 0.00011437 | 0.40951 | 0.4095 | 0.40951 | 0.99628 | -0.070631 | 0.99699 | -0.057071 | 37.5005
49 | 0.26384 | 0.067196 | -0.26379 | -0.067162 | 5.2674e-05 | 3.3606e-05 | 0.39444 | 0.39444 | 0.39444 | 0.99628 | -0.070631 | 0.99606 | -0.074771 | 36.1212
50 | -0.037968 | -0.0095316 | 0.037997 | 0.0095499 | 2.9019e-05 | 1.8273e-05 | 0.057383 | 0.057383 | 0.057383 | 0.98465 | -0.29499 | 0.98547 | -0.27898 | 15.7646
51 | 0.037968 | 0.0095316 | -0.037953 | -0.0095223 | 1.477e-05 | 9.3004e-06 | 0.057383 | 0.057383 | 0.057383 | 0.98465 | -0.29499 | 0.98423 | -0.30315 | 15.7646
52 | -0.041315 | -0.010382 | 0.041333 | 0.010393 | 1.8788e-05 | 1.186e-05 | 0.062393 | 0.062393 | 0.062393 | 0.98547 | -0.27898 | 0.98596 | -0.26945 | 17.141
53 | 0.027648 | 0.0069398 | -0.027642 | -0.0069356 | 6.8578e-06 | 4.2561e-06 | 0.041804 | 0.041804 | 0.041804 | 0.98423 | -0.30315 | 0.98396 | -0.30835 | 11.4847
54 | -0.27738 | -0.070661 | 0.27815 | 0.07115 | 0.000766 | 0.00048884 | 0.4144 | 0.4144 | 0.4144 | 0.99699 | -0.057071 | 1 | 0 | 37.9487
55 | 0.059731 | 0.015013 | -0.059729 | -0.015011 | 2.5916e-06 | 1.6477e-06 | 0.090114 | 0.090114 | 0.090114 | 0.98649 | -0.25917 | 0.98644 | -0.26008 | 24.7565
56 | 0.045172 | 0.011363 | -0.045152 | -0.01135 | 2.022e-05 | 1.2793e-05 | 0.068156 | 0.068156 | 0.068156 | 0.98644 | -0.26008 | 0.98596 | -0.26945 | 18.7242
57 | 0.0038185 | 0.00095692 | -0.0038183 | -0.00095697 | 1.3738e-07 | -5.2752e-08 | 0.0057629 | 0.0057629 | 0.0057629 | 0.98596 | -0.26945 | 0.98592 | -0.27021 | 1.5832
58 | 0.027642 | 0.0069356 | -0.027617 | -0.0069205 | 2.4394e-05 | 1.514e-05 | 0.041804 | 0.041805 | 0.041805 | 0.98396 | -0.30835 | 0.98301 | -0.32687 | 11.4848
59 | 0.0026413 | 0.00066125 | -0.0026409 | -0.00066186 | 4.1811e-07 | -6.1503e-07 | 0.0039996 | 0.0039999 | 0.0039999 | 0.9826 | -0.33498 | 0.98243 | -0.3383 | 1.0989
60 | 0.010337 | 0.0025911 | -0.010335 | -0.0025903 | 1.714e-06 | 8.6034e-07 | 0.015648 | 0.015648 | 0.015648 | 0.98301 | -0.32687 | 0.98283 | -0.33035 | 4.2988
61 | 0.0052036 | 0.0013041 | -0.0052036 | -0.0013041 | 4.4598e-09 | 4.2538e-10 | 0.0078783 | 0.0078783 | 0.0078783 | 0.98283 | -0.33035 | 0.98283 | -0.33037 | 2.1644
62 | 0.20095 | 0.051134 | -0.20077 | -0.051018 | 0.0001816 | 0.0001156 | 0.30125 | 0.30125 | 0.30125 | 0.99353 | -0.12294 | 0.99255 | -0.1417 | 27.5866
63 | -0.20095 | -0.051134 | 0.20183 | 0.05169 | 0.00087409 | 0.00055641 | 0.30125 | 0.30124 | 0.30125 | 0.99353 | -0.12294 | 0.99825 | -0.033119 | 27.5866
64 | 0.20077 | 0.051018 | -0.20053 | -0.050866 | 0.00023967 | 0.00015257 | 0.30125 | 0.30125 | 0.30125 | 0.99255 | -0.1417 | 0.99125 | -0.16653 | 27.5866
65 | -0.20718 | -0.053032 | 0.20732 | 0.053123 | 0.00014398 | 9.1677e-05 | 0.30922 | 0.30922 | 0.30922 | 0.99825 | -0.033119 | 0.99901 | -0.018779 | 28.317
66 | 0.2152 | 0.055174 | -0.21501 | -0.055049 | 0.00019575 | 0.00012468 | 0.32067 | 0.32067 | 0.32067 | 1 | 0 | 0.99901 | -0.018779 | 29.365
67 | 0.19709 | 0.050002 | -0.19704 | -0.049973 | 4.5965e-05 | 2.9255e-05 | 0.29607 | 0.29607 | 0.29607 | 0.99125 | -0.16653 | 0.991 | -0.17138 | 27.1128
68 | -0.0054248 | -0.0013596 | 0.005425 | 0.0013596 | 2.0873e-07 | 2.8849e-08 | 0.00821 | 0.0082099 | 0.00821 | 0.98322 | -0.32259 | 0.98326 | -0.32178 | 2.2555
69 | 0.0029544 | 0.00074041 | -0.0029543 | -0.00074043 | 1.7824e-08 | -1.8746e-08 | 0.0044712 | 0.0044712 | 0.0044712 | 0.98322 | -0.32259 | 0.98321 | -0.32271 | 1.2283
70 | -0.011778 | -0.0029488 | 0.01178 | 0.0029501 | 2.4695e-06 | 1.3175e-06 | 0.017823 | 0.017823 | 0.017823 | 0.98326 | -0.32178 | 0.98348 | -0.31737 | 4.8964
71 | -0.014114 | -0.003535 | 0.01412 | 0.0035385 | 6.2039e-06 | 3.5098e-06 | 0.021354 | 0.021354 | 0.021354 | 0.98348 | -0.31737 | 0.98396 | -0.30815 | 5.8664
72 | -0.018459 | -0.0046259 | 0.018466 | 0.0046301 | 7.0915e-06 | 4.2302e-06 | 0.027915 | 0.027915 | 0.027915 | 0.98396 | -0.30815 | 0.98437 | -0.30008 | 7.6689
73 | -0.021845 | -0.005477 | 0.021845 | 0.0054771 | 1.799e-07 | 1.0954e-07 | 0.033023 | 0.033023 | 0.033023 | 0.98437 | -0.30008 | 0.98438 | -0.29991 | 9.0722
74 | 0.0051868 | 0.0012998 | -0.0051864 | -0.0012997 | 4.0954e-07 | 4.1271e-08 | 0.0078844 | 0.0078845 | 0.0078845 | 0.97889 | -0.40626 | 0.97881 | -0.40792 | 2.1661
75 | -0.015606 | -0.0039116 | 0.01562 | 0.0039198 | 1.4109e-05 | 8.1884e-06 | 0.023722 | 0.023722 | 0.023722 | 0.97889 | -0.40626 | 0.97986 | -0.3873 | 6.5171
76 | 0.0038102 | 0.00095482 | -0.00381 | -0.00095488 | 1.914e-07 | -6.8698e-08 | 0.0057924 | 0.0057924 | 0.0057924 | 0.97881 | -0.40792 | 0.97876 | -0.40897 | 1.5913
77 | -0.024021 | -0.0060253 | 0.024091 | 0.0060688 | 7.0788e-05 | 4.3512e-05 | 0.03648 | 0.036479 | 0.03648 | 0.97986 | -0.3873 | 0.98301 | -0.32567 | 10.0219
78 | 0.008401 | 0.0021055 | -0.0083998 | -0.002105 | 1.2028e-06 | 5.2162e-07 | 0.012758 | 0.012758 | 0.012758 | 0.97986 | -0.3873 | 0.97971 | -0.39031 | 3.5049
79 | -0.099032 | -0.024969 | 0.099189 | 0.025067 | 0.00015684 | 9.8251e-05 | 0.14996 | 0.14996 | 0.14996 | 0.98301 | -0.32567 | 0.98471 | -0.29264 | 13.7327
80 | 0.0086595 | 0.0021707 | -0.0086571 | -0.0021697 | 2.3398e-06 | 1.0373e-06 | 0.013108 | 0.013108 | 0.013108 | 0.98301 | -0.32567 | 0.98272 | -0.33135 | 3.6012
81 | 0.010915 | 0.0027379 | -0.010906 | -0.0027334 | 8.6356e-06 | 4.4584e-06 | 0.016523 | 0.016523 | 0.016523 | 0.98301 | -0.32567 | 0.98216 | -0.34228 | 4.5393
82 | 0.055366 | 0.013992 | -0.055349 | -0.013982 | 1.6676e-05 | 9.9511e-06 | 0.083851 | 0.083851 | 0.083851 | 0.98301 | -0.32567 | 0.98269 | -0.33196 | 7.6787
83 | 0.0046907 | 0.0011754 | -0.00469 | -0.0011754 | 6.8054e-07 | -1.4598e-08 | 0.0071244 | 0.0071246 | 0.0071246 | 0.97971 | -0.39031 | 0.97955 | -0.39335 | 1.9573
84 | 0.010906 | 0.0027334 | -0.010905 | -0.0027331 | 6.2664e-07 | 3.2359e-07 | 0.016523 | 0.016523 | 0.016523 | 0.98216 | -0.34228 | 0.9821 | -0.34349 | 4.5393
85 | 0.0084104 | 0.0021078 | -0.0084083 | -0.0021069 | 2.1007e-06 | 9.0805e-07 | 0.012743 | 0.012743 | 0.012743 | 0.9821 | -0.34349 | 0.98183 | -0.34873 | 3.5008
86 | 0.055349 | 0.013982 | -0.055332 | -0.013971 | 1.702e-05 | 1.0566e-05 | 0.083851 | 0.083851 | 0.083851 | 0.98269 | -0.33196 | 0.98236 | -0.33838 | 11.518
87 | 0.046095 | 0.011656 | -0.046054 | -0.011631 | 4.0932e-05 | 2.5065e-05 | 0.069858 | 0.069859 | 0.069859 | 0.98236 | -0.33838 | 0.98141 | -0.35691 | 9.596
88 | -0.099189 | -0.025067 | 0.099235 | 0.025097 | 4.6631e-05 | 2.921e-05 | 0.14996 | 0.14996 | 0.14996 | 0.98471 | -0.29264 | 0.98522 | -0.28284 | 13.7326
89 | 0.0062253 | 0.0015602 | -0.0062247 | -0.0015601 | 5.5379e-07 | 1.4387e-07 | 0.0094262 | 0.0094263 | 0.0094263 | 0.98272 | -0.33135 | 0.98263 | -0.33321 | 2.5896
90 | 0.0046767 | 0.0011717 | -0.0046752 | -0.0011717 | 1.5054e-06 | -4.6798e-08 | 0.0070876 | 0.007088 | 0.007088 | 0.98183 | -0.34873 | 0.98149 | -0.35549 | 1.9472
91 | 0.042053 | 0.010628 | -0.042051 | -0.010627 | 1.6561e-06 | 1.0462e-06 | 0.063793 | 0.063793 | 0.063793 | 0.98141 | -0.35691 | 0.98137 | -0.35773 | 17.5254
92 | -0.10264 | -0.025949 | 0.10284 | 0.026077 | 0.00020468 | 0.00012839 | 0.1551 | 0.15509 | 0.1551 | 0.98522 | -0.28284 | 0.98736 | -0.24134 | 14.2029
93 | 0.0062247 | 0.0015601 | -0.0062236 | -0.0015598 | 1.114e-06 | 2.8954e-07 | 0.0094263 | 0.0094264 | 0.0094264 | 0.98263 | -0.33321 | 0.98244 | -0.33697 | 2.5897
94 | -0.028128 | -0.0070519 | 0.028141 | 0.0070594 | 1.2134e-05 | 7.538e-06 | 0.042521 | 0.042521 | 0.042521 | 0.98438 | -0.29991 | 0.98484 | -0.29086 | 11.6815
95 | -0.029484 | -0.007396 | 0.029494 | 0.0074026 | 1.0617e-05 | 6.6133e-06 | 0.04455 | 0.04455 | 0.04455 | 0.98484 | -0.29086 | 0.98523 | -0.28331 | 12.239
96 | -0.031732 | -0.0079635 | 0.031739 | 0.0079679 | 7.0319e-06 | 4.3964e-06 | 0.04793 | 0.04793 | 0.04793 | 0.98523 | -0.28331 | 0.98547 | -0.27867 | 13.1675
97 | -0.035911 | -0.0090135 | 0.035912 | 0.0090137 | 2.2958e-07 | 1.4428e-07 | 0.054229 | 0.054229 | 0.054229 | 0.98547 | -0.27867 | 0.98547 | -0.27853 | 14.8982
98 | -0.03815 | -0.0095745 | 0.038175 | 0.0095908 | 2.5892e-05 | 1.6305e-05 | 0.057609 | 0.057609 | 0.057609 | 0.98547 | -0.27853 | 0.9862 | -0.26431 | 15.8266
99 | 0.018316 | 0.0045948 | -0.018305 | -0.0045882 | 1.1134e-05 | 6.63e-06 | 0.027638 | 0.027638 | 0.027638 | 0.9862 | -0.26431 | 0.98555 | -0.27707 | 7.5929
100 | -0.056492 | -0.014186 | 0.056518 | 0.014203 | 2.666e-05 | 1.6938e-05 | 0.085246 | 0.085246 | 0.085246 | 0.9862 | -0.26431 | 0.98671 | -0.25443 | 23.4194
101 | 0.071784 | 0.018129 | -0.071715 | -0.018085 | 6.9122e-05 | 4.4034e-05 | 0.10783 | 0.10784 | 0.10784 | 0.991 | -0.17138 | 0.98996 | -0.19149 | 29.625
102 | 0.12526 | 0.031843 | -0.12516 | -0.031781 | 9.9731e-05 | 6.2958e-05 | 0.18824 | 0.18824 | 0.18824 | 0.991 | -0.17138 | 0.99014 | -0.18792 | 17.2378
103 | 0.015542 | 0.0038956 | -0.015541 | -0.0038952 | 5.7012e-07 | 3.297e-07 | 0.023466 | 0.023466 | 0.023466 | 0.98555 | -0.27707 | 0.98551 | -0.27784 | 6.4466
104 | -0.057771 | -0.014517 | 0.05781 | 0.014541 | 3.9028e-05 | 2.4803e-05 | 0.087135 | 0.087135 | 0.087135 | 0.98671 | -0.25443 | 0.98744 | -0.24028 | 23.9383
105 | 0.011383 | 0.0028531 | -0.011382 | -0.0028525 | 1.1154e-06 | 5.8558e-07 | 0.017187 | 0.017187 | 0.017187 | 0.98551 | -0.27784 | 0.9854 | -0.2799 | 4.7217
106 | -0.060602 | -0.015241 | 0.060635 | 0.015262 | 3.3429e-05 | 2.1258e-05 | 0.091343 | 0.091343 | 0.091343 | 0.98744 | -0.24028 | 0.98804 | -0.22874 | 25.0941
107 | 0.0051258 | 0.0012846 | -0.0051255 | -0.0012846 | 3.1958e-07 | 2.3339e-08 | 0.0077403 | 0.0077404 | 0.0077404 | 0.9854 | -0.2799 | 0.98534 | -0.28121 | 2.1265
108 | -0.063304 | -0.015931 | 0.063316 | 0.015939 | 1.2624e-05 | 8.0321e-06 | 0.095361 | 0.095361 | 0.095361 | 0.98804 | -0.22874 | 0.98825 | -0.22457 | 26.1981
109 | 0.067602 | 0.017054 | -0.067495 | -0.016986 | 0.00010687 | 6.8044e-05 | 0.10165 | 0.10165 | 0.10165 | 0.98996 | -0.19149 | 0.98825 | -0.22457 | 27.9268
110 | 0.12048 | 0.030609 | -0.12041 | -0.030563 | 7.3161e-05 | 4.6136e-05 | 0.18121 | 0.18121 | 0.18121 | 0.99014 | -0.18792 | 0.98948 | -0.20055 | 16.5945
111 | 0.0041791 | 0.0010473 | -0.0041789 | -0.0010473 | 1.969e-07 | -4.3883e-08 | 0.0062925 | 0.0062925 | 0.0062925 | 0.98825 | -0.22457 | 0.9882 | -0.22556 | 1.7287
112 | 0.11364 | 0.028866 | -0.11352 | -0.02879 | 0.00012164 | 7.657e-05 | 0.17103 | 0.17103 | 0.17103 | 0.98948 | -0.20055 | 0.98833 | -0.22281 | 15.6624
113 | 0.0067689 | 0.0016965 | -0.0067683 | -0.0016963 | 5.7356e-07 | 1.775e-07 | 0.010179 | 0.010179 | 0.010179 | 0.98948 | -0.20055 | 0.98939 | -0.20232 | 2.7965
114 | -0.0042992 | -0.0010775 | 0.0042992 | 0.0010775 | 2.1451e-08 | -3.6989e-09 | 0.0064792 | 0.0064792 | 0.0064792 | 0.98736 | -0.24145 | 0.98736 | -0.24134 | 1.78
115 | -0.10714 | -0.027155 | 0.1072 | 0.027192 | 5.9476e-05 | 3.7365e-05 | 0.16157 | 0.16157 | 0.16157 | 0.98736 | -0.24134 | 0.98796 | -0.2298 | 14.7961
116 | 0.11066 | 0.028072 | -0.11062 | -0.028049 | 3.7178e-05 | 2.3383e-05 | 0.16672 | 0.16672 | 0.16672 | 0.98833 | -0.22281 | 0.98796 | -0.2298 | 15.2678
117 | 0.0035022 | 0.00087774 | -0.0035022 | -0.00087774 | 6.1291e-09 | -3.6431e-09 | 0.0052673 | 0.0052673 | 0.0052673 | 0.98939 | -0.20232 | 0.98939 | -0.20236 | 1.4471
118 | 0.0034197 | 0.00085695 | -0.0034196 | -0.00085702 | 1.0509e-07 | -6.8014e-08 | 0.0051505 | 0.0051505 | 0.0051505 | 0.98796 | -0.2298 | 0.98793 | -0.23044 | 1.415
119 | 0.03624 | 0.0091708 | -0.036213 | -0.0091536 | 2.7423e-05 | 1.7246e-05 | 0.054982 | 0.054982 | 0.054982 | 0.98137 | -0.35773 | 0.98055 | -0.37351 | 15.1049
120 | 0.030909 | 0.0078243 | -0.030897 | -0.0078168 | 1.2062e-05 | 7.5354e-06 | 0.046933 | 0.046933 | 0.046933 | 0.98055 | -0.37351 | 0.98014 | -0.38164 | 12.8937
121 | 0.02628 | 0.0066597 | -0.026267 | -0.0066517 | 1.2864e-05 | 7.9618e-06 | 0.039924 | 0.039924 | 0.039924 | 0.98014 | -0.38164 | 0.97961 | -0.39183 | 10.9682
122 | 0.026267 | 0.0066517 | -0.026188 | -0.0066024 | 7.9611e-05 | 4.928e-05 | 0.039924 | 0.039925 | 0.039925 | 0.97961 | -0.39183 | 0.97637 | -0.45515 | 10.9683
123 | -0.019359 | -0.0048546 | 0.019366 | 0.0048591 | 7.3709e-06 | 4.4396e-06 | 0.02963 | 0.02963 | 0.02963 | 0.97221 | -0.53708 | 0.97261 | -0.5291 | 8.1402
124 | 0.015059 | 0.0037772 | -0.015054 | -0.0037743 | 4.9759e-06 | 2.875e-06 | 0.02305 | 0.02305 | 0.02305 | 0.97221 | -0.53708 | 0.97186 | -0.54402 | 6.3325
125 | 0.0017302 | 0.00043348 | -0.0017302 | -0.00043363 | 3.7108e-08 | -1.5151e-07 | 0.0026471 | 0.0026471 | 0.0026471 | 0.97261 | -0.5291 | 0.97259 | -0.52955 | 0.72723
126 | -0.021096 | -0.0052926 | 0.021098 | 0.0052937 | 1.8623e-06 | 1.1327e-06 | 0.032277 | 0.032277 | 0.032277 | 0.97261 | -0.5291 | 0.97271 | -0.52725 | 8.8674
127 | 0.015054 | 0.0037743 | -0.01505 | -0.003772 | 4.0175e-06 | 2.3214e-06 | 0.02305 | 0.02305 | 0.02305 | 0.97186 | -0.54402 | 0.97157 | -0.54962 | 6.3325
128 | -0.026098 | -0.0065467 | 0.026188 | 0.0066024 | 9.0024e-05 | 5.5739e-05 | 0.039925 | 0.039925 | 0.039925 | 0.97271 | -0.52725 | 0.97637 | -0.45515 | 10.9685
129 | 0.0053251 | 0.0013346 | -0.005325 | -0.0013346 | 8.1656e-08 | 1.1719e-08 | 0.0081556 | 0.0081556 | 0.0081556 | 0.97157 | -0.54962 | 0.97156 | -0.54994 | 2.2406

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49759 | 0.12697

## res_load
| p_mw | q_mvar
0 | 0.0020092 | 0.00050355
1 | 0.0097505 | 0.0024437
2 | 0.0041425 | 0.0010382
3 | 0.006565 | 0.0016453
4 | 0.016052 | 0.004023
5 | 0.009032 | 0.0022636
6 | 0.0042546 | 0.0010663
7 | 0.0026626 | 0.00066731
8 | 0.0010706 | 0.00026833
9 | 0.0016289 | 0.00040824
10 | 0.022331 | 0.0055967
11 | 0.00069547 | 0.0001743
12 | 0.0062614 | 0.0015693
13 | 0.0041539 | 0.0010411
14 | 0.0027872 | 0.00069854
15 | 0.0036523 | 0.00091536
16 | 0.035522 | 0.0089026
17 | 0.00070479 | 0.00017664
18 | 0.010634 | 0.0026652
19 | 0.022716 | 0.0056932
20 | 0.014228 | 0.0035658
21 | 0.014177 | 0.0035531
22 | 0.0061964 | 0.001553
23 | 0.013125 | 0.0032895
24 | 0.010078 | 0.0025257
25 | 0.0022734 | 0.00056977
26 | 0.0033181 | 0.00083161
27 | 0.010304 | 0.0025825
28 | 0.0032793 | 0.00082186
29 | 0.012916 | 0.0032369
30 | 0.014556 | 0.0036482
31 | 0.0032933 | 0.00082537
32 | 0.0051318 | 0.0012861
33 | 0.0038183 | 0.00095697
34 | 0.0052036 | 0.0013041
35 | 0.0026409 | 0.00066186
36 | 0.005352 | 0.0013413
37 | 0.0025861 | 0.00064814
38 | 0.007683 | 0.0019255
39 | 0.003447 | 0.0008639
40 | 0.0024704 | 0.00061915
41 | 0.0029543 | 0.00074043
42 | 0.0023337 | 0.00058489
43 | 0.0043387 | 0.0010874
44 | 0.0033792 | 0.0008469
45 | 0.0013762 | 0.0003449
46 | 0.00381 | 0.00095488
47 | 0.0037091 | 0.00092959
48 | 0.0024949 | 0.00062529
49 | 0.0092379 | 0.0023152
50 | 0.0024318 | 0.00060947
51 | 0.00469 | 0.0011754
52 | 0.0037316 | 0.00093522
53 | 0.0040009 | 0.0010027
54 | 0.0034006 | 0.00085227
55 | 0.0046752 | 0.0011717
56 | 0.0062832 | 0.0015747
57 | 0.0013431 | 0.00033661
58 | 0.002238 | 0.00056089
59 | 0.004172 | 0.0010456
60 | 0.002238 | 0.00056089
61 | 0.0027635 | 0.00069261
62 | 0.0012526 | 0.00031392
63 | 0.0041583 | 0.0010422
64 | 0.002792 | 0.00069973
65 | 0.006256 | 0.0015679
66 | 0.0026682 | 0.00066871
67 | 0.0041126 | 0.0010307
68 | 0.0046746 | 0.0011716
69 | 0.0042992 | 0.0010775
70 | 0.0041789 | 0.0010473
71 | 0.002862 | 0.00071729
72 | 0.0032661 | 0.00081856
73 | 0.0051255 | 0.0012846
74 | 0.0035022 | 0.00087774
75 | 0.0034196 | 0.00085702
76 | 0.0058108 | 0.0014563
77 | 0.005304 | 0.0013293
78 | 0.0046168 | 0.0011571
79 | 0.0042992 | 0.0010775
80 | 0.0017302 | 0.00043363
81 | 0.0049996 | 0.001253
82 | 0.0097252 | 0.0024374
83 | 0.005325 | 0.0013346
84 | 0.0062236 | 0.0015598

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1