## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2228-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2228-9_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2228-9_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_2228-9_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2228-9_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2228-9_0_4_node_99 | 0.4 | n |  | TRUE
6 | bus_LV_2228-9_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2228-9_0_4_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_2228-9_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2228-9_0_4_node_79 | 0.4 | n |  | TRUE
10 | bus_LV_2228-9_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2228-9_0_4_node_131 | 0.4 | n |  | TRUE
12 | bus_LV_2228-9_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_2228-9_0_4_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_2228-9_0_4_node_67 | 0.4 | n |  | TRUE
15 | bus_LV_2228-9_0_4_node_63 | 0.4 | n |  | TRUE
16 | bus_LV_2228-9_0_4_node_80 | 0.4 | n |  | TRUE
17 | bus_LV_2228-9_0_4_node_78 | 0.4 | n |  | TRUE
18 | bus_LV_2228-9_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2228-9_0_4_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_2228-9_0_4_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_2228-9_0_4_node_111 | 0.4 | n |  | TRUE
22 | bus_LV_2228-9_0_4_node_110 | 0.4 | n |  | TRUE
23 | bus_LV_2228-9_0_4_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_2228-9_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2228-9_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2228-9_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2228-9_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2228-9_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2228-9_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2228-9_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2228-9_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2228-9_0_4_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_2228-9_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_2228-9_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_2228-9_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2228-9_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_2228-9_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2228-9_0_4_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_2228-9_0_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_2228-9_0_4_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_2228-9_0_4_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_2228-9_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2228-9_0_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_2228-9_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_2228-9_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_2228-9_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_2228-9_0_4_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_2228-9_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_2228-9_0_4_node_68 | 0.4 | n |  | TRUE
50 | bus_LV_2228-9_0_4_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_2228-9_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_2228-9_0_4_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_2228-9_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_2228-9_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_2228-9_0_4_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_2228-9_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_2228-9_0_4_node_86 | 0.4 | n |  | TRUE
58 | bus_LV_2228-9_0_4_node_88 | 0.4 | n |  | TRUE
59 | bus_LV_2228-9_0_4_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_2228-9_0_4_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_2228-9_0_4_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_2228-9_0_4_node_84 | 0.4 | n |  | TRUE
63 | bus_LV_2228-9_0_4_node_89 | 0.4 | n |  | TRUE
64 | bus_LV_2228-9_0_4_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_2228-9_0_4_node_104 | 0.4 | n |  | TRUE
66 | bus_LV_2228-9_0_4_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_2228-9_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_2228-9_0_4_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_2228-9_0_4_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_2228-9_0_4_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_2228-9_0_4_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_2228-9_0_4_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_2228-9_0_4_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_2228-9_0_4_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_2228-9_0_4_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_2228-9_0_4_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_2228-9_0_4_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_2228-9_0_4_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_2228-9_0_4_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_2228-9_0_4_node_90 | 0.4 | n |  | TRUE
81 | bus_LV_2228-9_0_4_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_2228-9_0_4_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_2228-9_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_2228-9_0_4_node_82 | 0.4 | n |  | TRUE
85 | bus_LV_2228-9_0_4_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_2228-9_0_4_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_2228-9_0_4_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_2228-9_0_4_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_2228-9_0_4_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_2228-9_0_4_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_2228-9_0_4_node_91 | 0.4 | n |  | TRUE
92 | bus_LV_2228-9_0_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_2228-9_0_4_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_2228-9_0_4_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_2228-9_0_4_node_94 | 0.4 | n |  | TRUE
96 | bus_LV_2228-9_0_4_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_2228-9_0_4_node_93 | 0.4 | n |  | TRUE
98 | bus_LV_2228-9_0_4_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_2228-9_0_4_node_96 | 0.4 | n |  | TRUE
100 | bus_LV_2228-9_0_4_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_2228-9_0_4_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_2228-9_0_4_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_2228-9_0_4_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_2228-9_0_4_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_2228-9_0_4_node_121 | 0.4 | n |  | TRUE
106 | bus_LV_2228-9_0_4_node_129 | 0.4 | n |  | TRUE
107 | bus_LV_2228-9_0_4_node_108 | 0.4 | n |  | TRUE
108 | bus_LV_2228-9_0_4_node_122 | 0.4 | n |  | TRUE
109 | bus_LV_2228-9_0_4_node_120 | 0.4 | n |  | TRUE
110 | bus_LV_2228-9_0_4_node_130 | 0.4 | n |  | TRUE
111 | bus_LV_2228-9_0_4_node_106 | 0.4 | n |  | TRUE
112 | bus_LV_2228-9_0_4_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_2228-9_0_4_node_109 | 0.4 | n |  | TRUE
114 | bus_LV_2228-9_0_4_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_2228-9_0_4_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_2228-9_0_4_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_2228-9_0_4_node_115 | 0.4 | n |  | TRUE
118 | bus_LV_2228-9_0_4_node_116 | 0.4 | n |  | TRUE
119 | bus_LV_2228-9_0_4_node_117 | 0.4 | n |  | TRUE
120 | bus_LV_2228-9_0_4_node_118 | 0.4 | n |  | TRUE
121 | bus_LV_2228-9_0_4_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_2228-9_0_4_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_2228-9_0_4_node_127 | 0.4 | n |  | TRUE
124 | bus_LV_2228-9_0_4_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_2228-9_0_4_node_125 | 0.4 | n |  | TRUE
126 | bus_LV_2228-9_0_4_node_126 | 0.4 | n |  | TRUE
127 | bus_MV_505_0_node_72 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2228-9_0_4_load_0 | 0 | 0.0070878 | 0.0017764 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2228-9_0_4_load_99 | 5 | 0.0021741 | 0.00054487 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2228-9_0_4_load_7 | 6 | 0.011724 | 0.0029384 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2228-9_0_4_load_8 | 10 | 0.0046094 | 0.0011552 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2228-9_0_4_load_131 | 11 | 0.0068092 | 0.0017066 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2228-9_0_4_load_28 | 12 | 0.010404 | 0.0026075 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2228-9_0_4_load_67 | 14 | 0.0082585 | 0.0020698 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2228-9_0_4_load_78 | 17 | 0.0026427 | 0.00066233 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2228-9_0_4_load_9 | 18 | 0.0048477 | 0.0012149 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2228-9_0_4_load_47 | 20 | 0.0039533 | 0.00099078 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2228-9_0_4_load_111 | 21 | 0.0036457 | 0.00091371 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2228-9_0_4_load_110 | 22 | 0.0048453 | 0.0012144 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2228-9_0_4_load_10 | 23 | 0.0065332 | 0.0016374 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2228-9_0_4_load_11 | 24 | 0.0065337 | 0.0016375 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2228-9_0_4_load_15 | 26 | 0.0047726 | 0.0011961 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2228-9_0_4_load_22 | 29 | 0.0065332 | 0.0016374 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2228-9_0_4_load_26 | 30 | 0.0047726 | 0.0011961 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2228-9_0_4_load_16 | 31 | 0.0035485 | 0.00088933 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2228-9_0_4_load_20 | 34 | 0.025036 | 0.0062746 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2228-9_0_4_load_17 | 35 | 0.0084722 | 0.0021233 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2228-9_0_4_load_23 | 36 | 0.0065337 | 0.0016375 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2228-9_0_4_load_27 | 37 | 0.004777 | 0.0011972 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2228-9_0_4_load_18 | 39 | 0.0084159 | 0.0021092 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2228-9_0_4_load_45 | 40 | 0.0095436 | 0.0023919 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2228-9_0_4_load_38 | 41 | 0.0047756 | 0.0011969 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2228-9_0_4_load_24 | 42 | 0.0065332 | 0.0016374 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2228-9_0_4_load_25 | 43 | 0.0065399 | 0.0016391 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2228-9_0_4_load_34 | 45 | 0.004777 | 0.0011972 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2228-9_0_4_load_35 | 46 | 0.004777 | 0.0011972 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2228-9_0_4_load_32 | 47 | 0.0047726 | 0.0011961 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2228-9_0_4_load_33 | 48 | 0.0047726 | 0.0011961 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2228-9_0_4_load_68 | 49 | 0.0035485 | 0.00088934 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2228-9_0_4_load_37 | 50 | 0.004777 | 0.0011972 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2228-9_0_4_load_36 | 51 | 0.004768 | 0.001195 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2228-9_0_4_load_39 | 52 | 0.004904 | 0.0012291 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2228-9_0_4_load_40 | 53 | 0.0049036 | 0.001229 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2228-9_0_4_load_42 | 54 | 0.0049041 | 0.0012291 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2228-9_0_4_load_48 | 55 | 0.0049036 | 0.001229 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2228-9_0_4_load_88 | 58 | 0.0039861 | 0.00099901 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2228-9_0_4_load_50 | 59 | 0.0049041 | 0.0012291 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2228-9_0_4_load_49 | 60 | 0.0035485 | 0.00088933 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2228-9_0_4_load_51 | 61 | 0.0035519 | 0.00089018 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2228-9_0_4_load_84 | 62 | 0.0039861 | 0.00099901 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2228-9_0_4_load_89 | 63 | 0.0042078 | 0.0010546 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2228-9_0_4_load_66 | 64 | 0.0035519 | 0.00089019 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2228-9_0_4_load_52 | 67 | 0.0035485 | 0.00088933 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2228-9_0_4_load_56 | 68 | 0.0035485 | 0.00088933 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2228-9_0_4_load_57 | 69 | 0.0049083 | 0.0012301 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2228-9_0_4_load_53 | 70 | 0.003547 | 0.00088897 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2228-9_0_4_load_55 | 71 | 0.0035488 | 0.00088941 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2228-9_0_4_load_58 | 72 | 0.003547 | 0.00088897 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2228-9_0_4_load_59 | 73 | 0.0052771 | 0.0013226 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2228-9_0_4_load_61 | 74 | 0.0035488 | 0.00088942 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2228-9_0_4_load_62 | 76 | 0.003547 | 0.00088897 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2228-9_0_4_load_64 | 77 | 0.0052703 | 0.0013209 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2228-9_0_4_load_65 | 78 | 0.0044223 | 0.0011083 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2228-9_0_4_load_69 | 79 | 0.0052703 | 0.0013209 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2228-9_0_4_load_90 | 80 | 0.0041738 | 0.001046 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2228-9_0_4_load_70 | 81 | 0.0020909 | 0.00052404 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2228-9_0_4_load_71 | 82 | 0.0020898 | 0.00052374 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2228-9_0_4_load_81 | 83 | 0.0020909 | 0.00052404 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2228-9_0_4_load_82 | 84 | 0.0020895 | 0.00052369 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2228-9_0_4_load_72 | 85 | 0.0026405 | 0.00066176 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2228-9_0_4_load_73 | 86 | 0.0026435 | 0.00066252 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2228-9_0_4_load_74 | 87 | 0.0028926 | 0.00072496 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2228-9_0_4_load_75 | 88 | 0.0026405 | 0.00066176 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2228-9_0_4_load_76 | 89 | 0.0026429 | 0.00066238 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2228-9_0_4_load_77 | 90 | 0.0026412 | 0.00066196 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2228-9_0_4_load_91 | 91 | 0.0020898 | 0.00052374 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2228-9_0_4_load_92 | 92 | 0.0020909 | 0.00052404 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2228-9_0_4_load_85 | 93 | 0.0042054 | 0.001054 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2228-9_0_4_load_87 | 94 | 0.0041766 | 0.0010468 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2228-9_0_4_load_94 | 95 | 0.0044195 | 0.0011076 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2228-9_0_4_load_95 | 96 | 0.0039859 | 0.00099897 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2228-9_0_4_load_93 | 97 | 0.0024265 | 0.00060815 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2228-9_0_4_load_97 | 98 | 0.0041785 | 0.0010472 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2228-9_0_4_load_96 | 99 | 0.0042078 | 0.0010546 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2228-9_0_4_load_100 | 100 | 0.0033501 | 0.00083961 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2228-9_0_4_load_105 | 104 | 0.0030804 | 0.00077202 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2228-9_0_4_load_129 | 106 | 0.0023739 | 0.00059495 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2228-9_0_4_load_108 | 107 | 0.0030811 | 0.00077219 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2228-9_0_4_load_122 | 108 | 0.0026418 | 0.0006621 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2228-9_0_4_load_120 | 109 | 0.0034237 | 0.00085807 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2228-9_0_4_load_130 | 110 | 0.0030359 | 0.00076087 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2228-9_0_4_load_106 | 111 | 0.0035922 | 0.0009003 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2228-9_0_4_load_107 | 112 | 0.0035245 | 0.00088332 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2228-9_0_4_load_109 | 113 | 0.0036235 | 0.00090812 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2228-9_0_4_load_112 | 114 | 0.0023018 | 0.00057689 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2228-9_0_4_load_113 | 115 | 0.0027175 | 0.00068107 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2228-9_0_4_load_114 | 116 | 0.0056009 | 0.0014037 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2228-9_0_4_load_116 | 118 | 0.0027657 | 0.00069314 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2228-9_0_4_load_117 | 119 | 0.003354 | 0.00084058 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2228-9_0_4_load_118 | 120 | 0.0029873 | 0.00074868 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2228-9_0_4_load_119 | 121 | 0.002204 | 0.00055237 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2228-9_0_4_load_128 | 122 | 0.0022583 | 0.00056599 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2228-9_0_4_load_127 | 123 | 0.0026936 | 0.00067508 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2228-9_0_4_load_123 | 124 | 0.0026661 | 0.00066818 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2228-9_0_4_load_125 | 125 | 0.0030792 | 0.00077171 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2228-9_0_4_load_126 | 126 | 0.0030638 | 0.00076787 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2228-9_0_4_line_0 |  | 0 | 1 | 0.0041144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2228-9_0_4_line_1 |  | 1 | 2 | 0.029451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2228-9_0_4_line_2 |  | 1 | 3 | 0.021005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2228-9_0_4_line_3 |  | 2 | 6 | 0.003143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2228-9_0_4_line_4 |  | 2 | 4 | 0.033643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2228-9_0_4_line_5 |  | 3 | 7 | 0.008795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2228-9_0_4_line_6 |  | 3 | 8 | 0.024124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2228-9_0_4_line_7 |  | 4 | 5 | 0.008877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2228-9_0_4_line_8 |  | 6 | 10 | 0.036479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2228-9_0_4_line_9 |  | 7 | 11 | 0.016835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2228-9_0_4_line_10 |  | 8 | 9 | 0.009058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2228-9_0_4_line_11 |  | 9 | 16 | 0.031159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2228-9_0_4_line_12 |  | 9 | 17 | 0.020123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2228-9_0_4_line_13 |  | 10 | 18 | 0.021552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2228-9_0_4_line_14 |  | 12 | 13 | 0.02374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2228-9_0_4_line_15 |  | 13 | 33 | 0.016181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2228-9_0_4_line_16 |  | 14 | 15 | 0.021894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2228-9_0_4_line_17 |  | 15 | 64 | 0.011615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2228-9_0_4_line_18 |  | 15 | 76 | 0.016548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2228-9_0_4_line_19 |  | 16 | 84 | 0.024852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2228-9_0_4_line_20 |  | 17 | 90 | 0.006252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2228-9_0_4_line_21 |  | 18 | 19 | 0.046601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2228-9_0_4_line_22 |  | 18 | 20 | 0.016661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2228-9_0_4_line_23 |  | 19 | 21 | 0.019257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2228-9_0_4_line_24 |  | 19 | 22 | 0.043482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2228-9_0_4_line_25 |  | 22 | 65 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2228-9_0_4_line_26 |  | 23 | 24 | 0.00043709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2228-9_0_4_line_27 |  | 24 | 25 | 0.021532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2228-9_0_4_line_28 |  | 25 | 26 | 0.012192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2228-9_0_4_line_29 |  | 26 | 30 | 0.0059341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2228-9_0_4_line_30 |  | 27 | 28 | 0.024074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2228-9_0_4_line_31 |  | 27 | 29 | 0.022737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2228-9_0_4_line_32 |  | 28 | 34 | 0.021187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2228-9_0_4_line_33 |  | 28 | 35 | 0.023106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2228-9_0_4_line_34 |  | 29 | 36 | 6.4989e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2228-9_0_4_line_35 |  | 30 | 37 | 0.0059368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2228-9_0_4_line_36 |  | 31 | 32 | 0.01199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2228-9_0_4_line_37 |  | 32 | 38 | 0.012003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2228-9_0_4_line_38 |  | 33 | 40 | 0.009646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2228-9_0_4_line_39 |  | 33 | 41 | 0.016881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2228-9_0_4_line_40 |  | 35 | 39 | 0.0042361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2228-9_0_4_line_41 |  | 36 | 42 | 6.4989e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2228-9_0_4_line_42 |  | 37 | 47 | 0.0059368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2228-9_0_4_line_43 |  | 38 | 52 | 0.012832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2228-9_0_4_line_44 |  | 40 | 49 | 0.011387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2228-9_0_4_line_45 |  | 41 | 50 | 0.0059394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2228-9_0_4_line_46 |  | 42 | 43 | 6.3168e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2228-9_0_4_line_47 |  | 43 | 44 | 0.022779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2228-9_0_4_line_48 |  | 44 | 45 | 0.0041745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2228-9_0_4_line_49 |  | 44 | 46 | 0.0041469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2228-9_0_4_line_50 |  | 45 | 48 | 0.0059368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2228-9_0_4_line_51 |  | 46 | 51 | 0.005934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2228-9_0_4_line_52 |  | 47 | 48 | 0.0059341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2228-9_0_4_line_53 |  | 49 | 64 | 0.00017437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2228-9_0_4_line_54 |  | 50 | 51 | 0.005934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2228-9_0_4_line_55 |  | 52 | 53 | 0.0057255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2228-9_0_4_line_56 |  | 53 | 54 | 0.0057255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2228-9_0_4_line_57 |  | 54 | 55 | 0.0057922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2228-9_0_4_line_58 |  | 55 | 59 | 0.0057253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2228-9_0_4_line_59 |  | 56 | 57 | 0.018811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2228-9_0_4_line_60 |  | 56 | 58 | 0.014863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2228-9_0_4_line_61 |  | 57 | 62 | 0.014526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2228-9_0_4_line_62 |  | 58 | 63 | 0.0086388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2228-9_0_4_line_63 |  | 59 | 66 | 0.011055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2228-9_0_4_line_64 |  | 60 | 61 | 0.0059379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2228-9_0_4_line_65 |  | 61 | 67 | 0.0059379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2228-9_0_4_line_66 |  | 62 | 93 | 0.0085183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2228-9_0_4_line_67 |  | 63 | 80 | 0.0088333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2228-9_0_4_line_68 |  | 65 | 101 | 0.059899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_2228-9_0_4_line_69 |  | 66 | 68 | 0.011703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2228-9_0_4_line_70 |  | 66 | 69 | 0.0071478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_2228-9_0_4_line_71 |  | 67 | 70 | 0.0059348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2228-9_0_4_line_72 |  | 68 | 72 | 0.0060005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_2228-9_0_4_line_73 |  | 68 | 71 | 0.0082535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2228-9_0_4_line_74 |  | 69 | 73 | 0.0024079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2228-9_0_4_line_75 |  | 70 | 71 | 0.0059385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2228-9_0_4_line_76 |  | 72 | 74 | 0.0059385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2228-9_0_4_line_77 |  | 73 | 75 | 0.011585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_2228-9_0_4_line_78 |  | 74 | 76 | 0.0059385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2228-9_0_4_line_79 |  | 75 | 77 | 0.017339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2228-9_0_4_line_80 |  | 75 | 78 | 0.004437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2228-9_0_4_line_81 |  | 77 | 79 | 0.0085655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2228-9_0_4_line_82 |  | 78 | 80 | 0.0089277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2228-9_0_4_line_83 |  | 79 | 81 | 0.022963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_2228-9_0_4_line_84 |  | 81 | 82 | 0.0082688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_2228-9_0_4_line_85 |  | 82 | 83 | 0.0079951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_2228-9_0_4_line_86 |  | 83 | 84 | 0.00824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2228-9_0_4_line_87 |  | 85 | 86 | 0.0062632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2228-9_0_4_line_88 |  | 85 | 87 | 0.0077984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2228-9_0_4_line_89 |  | 86 | 88 | 0.0062632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2228-9_0_4_line_90 |  | 88 | 89 | 0.0066887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2228-9_0_4_line_91 |  | 89 | 90 | 0.0062517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2228-9_0_4_line_92 |  | 91 | 92 | 0.0083796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2228-9_0_4_line_93 |  | 92 | 97 | 0.011564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2228-9_0_4_line_94 |  | 93 | 94 | 0.0088016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2228-9_0_4_line_95 |  | 94 | 95 | 0.0090607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2228-9_0_4_line_96 |  | 95 | 96 | 0.011785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2228-9_0_4_line_97 |  | 96 | 99 | 0.0086318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2228-9_0_4_line_98 |  | 97 | 98 | 0.0090658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2228-9_0_4_line_99 |  | 98 | 99 | 0.0088383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2228-9_0_4_line_100 |  | 100 | 101 | 0.037263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2228-9_0_4_line_101 |  | 100 | 102 | 0.012075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2228-9_0_4_line_102 |  | 101 | 103 | 0.04389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2228-9_0_4_line_103 |  | 102 | 104 | 0.019198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2228-9_0_4_line_104 |  | 103 | 105 | 0.014425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2228-9_0_4_line_105 |  | 103 | 106 | 0.010867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2228-9_0_4_line_106 |  | 104 | 107 | 0.00013152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2228-9_0_4_line_107 |  | 105 | 108 | 0.014926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2228-9_0_4_line_108 |  | 105 | 109 | 0.011863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2228-9_0_4_line_109 |  | 106 | 110 | 0.020208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2228-9_0_4_line_110 |  | 107 | 111 | 0.0031563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2228-9_0_4_line_111 |  | 108 | 124 | 0.0068184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2228-9_0_4_line_112 |  | 109 | 119 | 0.0078696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2228-9_0_4_line_113 |  | 111 | 112 | 0.01081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2228-9_0_4_line_114 |  | 112 | 113 | 0.01064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2228-9_0_4_line_115 |  | 114 | 115 | 0.0070705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2228-9_0_4_line_116 |  | 114 | 116 | 0.0057188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2228-9_0_4_line_117 |  | 115 | 117 | 0.0035756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2228-9_0_4_line_118 |  | 117 | 118 | 0.0053818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2228-9_0_4_line_119 |  | 117 | 119 | 0.014839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2228-9_0_4_line_120 |  | 118 | 120 | 0.018318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2228-9_0_4_line_121 |  | 120 | 121 | 0.00099884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2228-9_0_4_line_122 |  | 121 | 122 | 0.0096499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2228-9_0_4_line_123 |  | 122 | 123 | 0.005858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2228-9_0_4_line_124 |  | 123 | 126 | 0.0098636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2228-9_0_4_line_125 |  | 125 | 126 | 0.027705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2228-9_0_4_trafo_37 | 0.63 MVA 20/0.4 kV | 127 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2575300.8976 | 1182319.0681 | 2575300.12 | 1182315.0278
1 | 2575300.8976 | 1182319.0681 | 2575309.2438 | 1182321.1125 | 2575318.0014 | 1182322.955 | 2575329.6343 | 1182325.8529
2 | 2575300.8976 | 1182319.0681 | 2575302.9084 | 1182332.6447 | 2575303.3774 | 1182335.2774 | 2575304.1979 | 1182339.8097
3 | 2575329.6343 | 1182325.8529 | 2575332.6584 | 1182326.7089
4 | 2575329.6343 | 1182325.8529 | 2575333.493 | 1182313.6195 | 2575335.6483 | 1182306.7625 | 2575339.733 | 1182293.7611
5 | 2575295.6787 | 1182342.0906 | 2575304.1979 | 1182339.8097
6 | 2575284.9925 | 1182341.012 | 2575289.3711 | 1182338.1813 | 2575303.3774 | 1182335.2774 | 2575304.1979 | 1182339.8097
7 | 2575339.733 | 1182293.7611 | 2575348.4347 | 1182295.5162
8 | 2575332.6584 | 1182326.7089 | 2575347.9039 | 1182331.0246 | 2575367.7358 | 1182336.7232
9 | 2575295.6787 | 1182342.0906 | 2575290.6003 | 1182343.6902 | 2575286.7234 | 1182345.9741 | 2575284.1538 | 1182350.4982 | 2575284.0895 | 1182352.3052
10 | 2575276.4588 | 1182337.9235 | 2575280.0597 | 1182339.0648 | 2575284.9925 | 1182341.012
11 | 2575246.6171 | 1182335.3347 | 2575252.4182 | 1182333.0761 | 2575259.5086 | 1182332.4242 | 2575267.3571 | 1182334.1148 | 2575276.4588 | 1182337.9235
12 | 2575276.4588 | 1182337.9235 | 2575275.4221 | 1182340.1734 | 2575271.3163 | 1182346.1825 | 2575268.0883 | 1182355.8008 | 2575268.0854 | 1182356.0228
13 | 2575388.2912 | 1182343.1977 | 2575369.4151 | 1182337.2057 | 2575367.7358 | 1182336.7232
14 | 2575325.5729 | 1182403.5546 | 2575320.1274 | 1182392.1045 | 2575316.3105 | 1182381.7228
15 | 2575309.3536 | 1182403.0325 | 2575325.5729 | 1182403.5546
16 | 2575276.547 | 1182401.6008 | 2575277.7729 | 1182379.7407
17 | 2575276.547 | 1182401.6008 | 2575288.1354 | 1182402.3888
18 | 2575276.547 | 1182401.6008 | 2575275.6098 | 1182418.1224
19 | 2575246.6171 | 1182335.3347 | 2575247.4515 | 1182343.2242 | 2575247.0901 | 1182353.6534 | 2575246.5643 | 1182360.1155
20 | 2575268.0047 | 1182362.2743 | 2575268.0854 | 1182356.0228
21 | 2575388.2912 | 1182343.1977 | 2575393.612 | 1182344.8099 | 2575405.0622 | 1182349.7209 | 2575421.1956 | 1182357.1694 | 2575431.1476 | 1182361.6753
22 | 2575388.2912 | 1182343.1977 | 2575393.7423 | 1182327.4541
23 | 2575431.1476 | 1182361.6753 | 2575422.5373 | 1182378.9086
24 | 2575431.1476 | 1182361.6753 | 2575436.6399 | 1182364.1651 | 2575449.3593 | 1182373.2286 | 2575459.1036 | 1182384.8057 | 2575463.1579 | 1182390.1411
25 | 2575472.7375 | 1182402.7479 | 2575463.1579 | 1182390.1411
26 | 2575325.1602 | 1182490.5779 | 2575325.5932 | 1182490.6371
27 | 2575303.8173 | 1182487.7328 | 2575308.7292 | 1182488.3351 | 2575325.1602 | 1182490.5779
28 | 2575303.8173 | 1182487.7328 | 2575304.6121 | 1182475.5663
29 | 2575304.9989 | 1182469.6449 | 2575304.6121 | 1182475.5663
30 | 2575361.6387 | 1182430.642 | 2575357.4535 | 1182432.2268 | 2575347.6399 | 1182439.0042 | 2575352.4137 | 1182445.0098
31 | 2575352.4137 | 1182445.0098 | 2575329.7333 | 1182443.4059
32 | 2575382.1444 | 1182426.3775 | 2575372.2197 | 1182426.6296 | 2575361.6387 | 1182430.642
33 | 2575361.6387 | 1182430.642 | 2575349.2859 | 1182411.1147
34 | 2575329.6685 | 1182443.4013 | 2575329.7333 | 1182443.4059
35 | 2575304.9989 | 1182469.6449 | 2575305.3858 | 1182463.7207
36 | 2575271.9002 | 1182483.4182 | 2575283.7827 | 1182485.0209
37 | 2575271.9002 | 1182483.4182 | 2575267.5922 | 1182482.9914 | 2575261.7788 | 1182482.2484 | 2575259.9455 | 1182482.0226
38 | 2575299.6797 | 1182402.9947 | 2575309.3536 | 1182403.0325
39 | 2575309.3536 | 1182403.0325 | 2575308.2517 | 1182419.8779
40 | 2575347.0212 | 1182407.5348 | 2575349.2859 | 1182411.1147
41 | 2575329.6037 | 1182443.3967 | 2575329.6685 | 1182443.4013
42 | 2575305.3858 | 1182463.7207 | 2575305.7728 | 1182457.7966
43 | 2575259.9455 | 1182482.0226 | 2575260.4064 | 1182473.494 | 2575260.662 | 1182469.2111
44 | 2575299.6797 | 1182402.9947 | 2575292.1118 | 1182402.6591 | 2575288.3094 | 1182402.4006
45 | 2575307.864 | 1182425.8046 | 2575308.2517 | 1182419.8779
46 | 2575329.5407 | 1182443.3922 | 2575329.6037 | 1182443.3967
47 | 2575306.8187 | 1182441.7854 | 2575329.5407 | 1182443.3922
48 | 2575306.8187 | 1182441.7854 | 2575306.5466 | 1182445.951
49 | 2575306.8187 | 1182441.7854 | 2575307.0894 | 1182437.6473
50 | 2575306.1596 | 1182451.8751 | 2575306.5466 | 1182445.951
51 | 2575307.0894 | 1182437.6473 | 2575307.4767 | 1182431.7259
52 | 2575305.7728 | 1182457.7966 | 2575306.1596 | 1182451.8751
53 | 2575288.3094 | 1182402.4006 | 2575288.1354 | 1182402.3888
54 | 2575307.4767 | 1182431.7259 | 2575307.864 | 1182425.8046
55 | 2575260.662 | 1182469.2111 | 2575261.0031 | 1182463.4957
56 | 2575261.0031 | 1182463.4957 | 2575261.3442 | 1182457.7803
57 | 2575261.3442 | 1182457.7803 | 2575261.4416 | 1182456.1473 | 2575261.6503 | 1182451.9962
58 | 2575261.6503 | 1182451.9962 | 2575261.9378 | 1182446.2782
59 | 2575220.7231 | 1182476.2488 | 2575239.3944 | 1182478.9395
60 | 2575239.3944 | 1182478.9395 | 2575239.7087 | 1182464.5307 | 2575239.736 | 1182464.0805
61 | 2575220.7231 | 1182476.2488 | 2575221.4096 | 1182461.7395
62 | 2575239.736 | 1182464.0805 | 2575240.2582 | 1182455.4575
63 | 2575262.8821 | 1182435.2638 | 2575261.9777 | 1182445.484 | 2575261.9378 | 1182446.2782
64 | 2575272.781 | 1182467.9223 | 2575273.118 | 1182461.994
65 | 2575273.118 | 1182461.994 | 2575273.455 | 1182456.0656
66 | 2575221.4096 | 1182461.7395 | 2575221.5443 | 1182458.8919 | 2575221.9479 | 1182453.2387
67 | 2575240.2582 | 1182455.4575 | 2575240.7922 | 1182446.6403
68 | 2575472.7375 | 1182402.7479 | 2575487.4096 | 1182418.8294 | 2575513.8599 | 1182441.6883 | 2575512.4973 | 1182444.551
69 | 2575262.8821 | 1182435.2638 | 2575274.5973 | 1182435.9712
70 | 2575262.8821 | 1182435.2638 | 2575255.7646 | 1182434.6055
71 | 2575273.455 | 1182456.0656 | 2575273.7919 | 1182450.1403
72 | 2575274.5973 | 1182435.9712 | 2575274.9371 | 1182429.9803
73 | 2575274.5973 | 1182435.9712 | 2575274.1289 | 1182444.2114
74 | 2575255.7646 | 1182434.6055 | 2575253.3669 | 1182434.3837
75 | 2575273.7919 | 1182450.1403 | 2575274.1289 | 1182444.2114
76 | 2575274.9371 | 1182429.9803 | 2575275.2735 | 1182424.0514
77 | 2575241.8316 | 1182433.3167 | 2575253.3669 | 1182434.3837
78 | 2575275.2735 | 1182424.0514 | 2575275.6098 | 1182418.1224
79 | 2575241.8316 | 1182433.3167 | 2575242.9517 | 1182419.8939 | 2575243.229 | 1182416.0341
80 | 2575241.8316 | 1182433.3167 | 2575241.4643 | 1182437.7384
81 | 2575243.229 | 1182416.0341 | 2575243.8427 | 1182407.4907
82 | 2575240.7922 | 1182446.6403 | 2575240.9735 | 1182443.6479 | 2575241.4643 | 1182437.7384
83 | 2575243.8427 | 1182407.4907 | 2575244.7491 | 1182394.8735 | 2575245.0405 | 1182384.564
84 | 2575245.0405 | 1182384.564 | 2575245.2742 | 1182376.2985
85 | 2575245.2742 | 1182376.2985 | 2575245.2884 | 1182375.7946 | 2575245.896 | 1182368.3283
86 | 2575245.896 | 1182368.3283 | 2575246.5643 | 1182360.1155
87 | 2575266.7046 | 1182387.6982 | 2575267.1493 | 1182381.4508
88 | 2575266.6341 | 1182395.4942 | 2575266.6363 | 1182388.6573 | 2575266.7046 | 1182387.6982
89 | 2575267.1493 | 1182381.4508 | 2575267.594 | 1182375.2034
90 | 2575267.594 | 1182375.2034 | 2575267.8918 | 1182371.0207 | 2575267.924 | 1182368.5255
91 | 2575267.924 | 1182368.5255 | 2575268.0047 | 1182362.2743
92 | 2575226.8306 | 1182377.2714 | 2575226.6731 | 1182381.1413 | 2575226.3908 | 1182385.639
93 | 2575225.667 | 1182397.1801 | 2575225.6848 | 1182396.8869 | 2575226.3908 | 1182385.639
94 | 2575221.9479 | 1182453.2387 | 2575222.3597 | 1182447.4715 | 2575222.5919 | 1182444.4607
95 | 2575222.5919 | 1182444.4607 | 2575223.2886 | 1182435.4268
96 | 2575223.2886 | 1182435.4268 | 2575223.5261 | 1182432.3477 | 2575224.0571 | 1182423.6672
97 | 2575224.0571 | 1182423.6672 | 2575224.5841 | 1182415.0515
98 | 2575225.1193 | 1182406.2294 | 2575225.667 | 1182397.1801
99 | 2575224.5841 | 1182415.0515 | 2575224.6987 | 1182413.1773 | 2575225.1193 | 1182406.2294
100 | 2575512.4973 | 1182444.551 | 2575512.5686 | 1182481.8135
101 | 2575512.5242 | 1182493.8877 | 2575512.5839 | 1182489.8409 | 2575512.5686 | 1182481.8135
102 | 2575512.4973 | 1182444.551 | 2575502.5484 | 1182450.028 | 2575496.7218 | 1182451.6527 | 2575481.7489 | 1182451.5474 | 2575470.1709 | 1182452.6289
103 | 2575512.5242 | 1182493.8877 | 2575493.3265 | 1182493.7308
104 | 2575470.1709 | 1182452.6289 | 2575469.3314 | 1182452.7102 | 2575461.2278 | 1182455.7673 | 2575457.4617 | 1182458.9844
105 | 2575470.1709 | 1182452.6289 | 2575470.7057 | 1182443.4108 | 2575471.1573 | 1182441.8414
106 | 2575493.195 | 1182493.7297 | 2575493.3265 | 1182493.7308
107 | 2575457.4617 | 1182458.9844 | 2575454.8748 | 1182461.1851 | 2575451.5685 | 1182470.4035 | 2575451.4265 | 1182472.1336
108 | 2575457.4617 | 1182458.9844 | 2575453.4411 | 1182454.1651 | 2575448.3859 | 1182451.7873
109 | 2575476.4163 | 1182426.5897 | 2575476.7791 | 1182438.6834 | 2575476.597 | 1182440.8408 | 2575476.2413 | 1182441.6093 | 2575474.3476 | 1182441.5615 | 2575471.1573 | 1182441.8414
110 | 2575490.0389 | 1182493.7039 | 2575493.195 | 1182493.7297
111 | 2575451.4265 | 1182472.1336 | 2575450.8684 | 1182478.9291
112 | 2575441.2667 | 1182448.4335 | 2575442.6164 | 1182449.0736 | 2575448.3859 | 1182451.7873
113 | 2575490.0389 | 1182493.7039 | 2575479.2297 | 1182493.6155
114 | 2575479.2297 | 1182493.6155 | 2575468.5898 | 1182493.5286
115 | 2575432.0809 | 1182432.3017 | 2575429.2773 | 1182438.7926
116 | 2575434.3486 | 1182427.0517 | 2575432.0809 | 1182432.3017
117 | 2575427.8595 | 1182442.0751 | 2575429.2773 | 1182438.7926
118 | 2575427.8595 | 1182442.0751 | 2575425.1874 | 1182446.7468
119 | 2575427.8595 | 1182442.0751 | 2575441.2667 | 1182448.4335
120 | 2575425.1874 | 1182446.7468 | 2575424.2966 | 1182448.3041 | 2575421.3229 | 1182452.9633 | 2575416.9992 | 1182456.1494 | 2575414.9585 | 1182459.3261 | 2575414.6288 | 1182461.1468
121 | 2575414.4508 | 1182462.1297 | 2575414.6288 | 1182461.1468
122 | 2575414.4508 | 1182462.1297 | 2575414.4508 | 1182462.1297 | 2575415.9817 | 1182464.9248 | 2575415.0852 | 1182467.8522 | 2575414.3277 | 1182471.1682 | 2575414.3277 | 1182471.1682
123 | 2575414.3277 | 1182471.1682 | 2575414.703 | 1182477.0141 | 2575414.703 | 1182477.0141
124 | 2575414.703 | 1182477.0141 | 2575416.3608 | 1182480.9649 | 2575416.9934 | 1182484.3975 | 2575416.9466 | 1182486.4857
125 | 2575432.7773 | 1182503.4869 | 2575426.4153 | 1182502.9795 | 2575423.7433 | 1182501.2007 | 2575418.1453 | 1182497.1216 | 2575416.3624 | 1182494.3275 | 2575416.8709 | 1182489.8675 | 2575416.9466 | 1182486.4857

## bus_geodata
| x | y | coords
0 | 2575300.12 | 1182315.0278
1 | 2575300.8976 | 1182319.0681
2 | 2575329.6343 | 1182325.8529
3 | 2575304.1979 | 1182339.8097
4 | 2575339.733 | 1182293.7611
5 | 2575348.4347 | 1182295.5162
6 | 2575332.6584 | 1182326.7089
7 | 2575295.6787 | 1182342.0906
8 | 2575284.9925 | 1182341.012
9 | 2575276.4588 | 1182337.9235
10 | 2575367.7358 | 1182336.7232
11 | 2575284.0895 | 1182352.3052
12 | 2575316.3105 | 1182381.7228
13 | 2575325.5729 | 1182403.5546
14 | 2575277.7729 | 1182379.7407
15 | 2575276.547 | 1182401.6008
16 | 2575246.6171 | 1182335.3347
17 | 2575268.0854 | 1182356.0228
18 | 2575388.2912 | 1182343.1977
19 | 2575431.1476 | 1182361.6753
20 | 2575393.7423 | 1182327.4541
21 | 2575422.5373 | 1182378.9086
22 | 2575463.1579 | 1182390.1411
23 | 2575325.5932 | 1182490.6371
24 | 2575325.1602 | 1182490.5779
25 | 2575303.8173 | 1182487.7328
26 | 2575304.6121 | 1182475.5663
27 | 2575352.4137 | 1182445.0098
28 | 2575361.6387 | 1182430.642
29 | 2575329.7333 | 1182443.4059
30 | 2575304.9989 | 1182469.6449
31 | 2575283.7827 | 1182485.0209
32 | 2575271.9002 | 1182483.4182
33 | 2575309.3536 | 1182403.0325
34 | 2575382.1444 | 1182426.3775
35 | 2575349.2859 | 1182411.1147
36 | 2575329.6685 | 1182443.4013
37 | 2575305.3858 | 1182463.7207
38 | 2575259.9455 | 1182482.0226
39 | 2575347.0212 | 1182407.5348
40 | 2575299.6797 | 1182402.9947
41 | 2575308.2517 | 1182419.8779
42 | 2575329.6037 | 1182443.3967
43 | 2575329.5407 | 1182443.3922
44 | 2575306.8187 | 1182441.7854
45 | 2575306.5466 | 1182445.951
46 | 2575307.0894 | 1182437.6473
47 | 2575305.7728 | 1182457.7966
48 | 2575306.1596 | 1182451.8751
49 | 2575288.3094 | 1182402.4006
50 | 2575307.864 | 1182425.8046
51 | 2575307.4767 | 1182431.7259
52 | 2575260.662 | 1182469.2111
53 | 2575261.0031 | 1182463.4957
54 | 2575261.3442 | 1182457.7803
55 | 2575261.6503 | 1182451.9962
56 | 2575239.3944 | 1182478.9395
57 | 2575220.7231 | 1182476.2488
58 | 2575239.736 | 1182464.0805
59 | 2575261.9378 | 1182446.2782
60 | 2575272.781 | 1182467.9223
61 | 2575273.118 | 1182461.994
62 | 2575221.4096 | 1182461.7395
63 | 2575240.2582 | 1182455.4575
64 | 2575288.1354 | 1182402.3888
65 | 2575472.7375 | 1182402.7479
66 | 2575262.8821 | 1182435.2638
67 | 2575273.455 | 1182456.0656
68 | 2575274.5973 | 1182435.9712
69 | 2575255.7646 | 1182434.6055
70 | 2575273.7919 | 1182450.1403
71 | 2575274.1289 | 1182444.2114
72 | 2575274.9371 | 1182429.9803
73 | 2575253.3669 | 1182434.3837
74 | 2575275.2735 | 1182424.0514
75 | 2575241.8316 | 1182433.3167
76 | 2575275.6098 | 1182418.1224
77 | 2575243.229 | 1182416.0341
78 | 2575241.4643 | 1182437.7384
79 | 2575243.8427 | 1182407.4907
80 | 2575240.7922 | 1182446.6403
81 | 2575245.0405 | 1182384.564
82 | 2575245.2742 | 1182376.2985
83 | 2575245.896 | 1182368.3283
84 | 2575246.5643 | 1182360.1155
85 | 2575266.7046 | 1182387.6982
86 | 2575267.1493 | 1182381.4508
87 | 2575266.6341 | 1182395.4942
88 | 2575267.594 | 1182375.2034
89 | 2575267.924 | 1182368.5255
90 | 2575268.0047 | 1182362.2743
91 | 2575226.8306 | 1182377.2714
92 | 2575226.3908 | 1182385.639
93 | 2575221.9479 | 1182453.2387
94 | 2575222.5919 | 1182444.4607
95 | 2575223.2886 | 1182435.4268
96 | 2575224.0571 | 1182423.6672
97 | 2575225.667 | 1182397.1801
98 | 2575225.1193 | 1182406.2294
99 | 2575224.5841 | 1182415.0515
100 | 2575512.5686 | 1182481.8135
101 | 2575512.4973 | 1182444.551
102 | 2575512.5242 | 1182493.8877
103 | 2575470.1709 | 1182452.6289
104 | 2575493.3265 | 1182493.7308
105 | 2575457.4617 | 1182458.9844
106 | 2575471.1573 | 1182441.8414
107 | 2575493.195 | 1182493.7297
108 | 2575451.4265 | 1182472.1336
109 | 2575448.3859 | 1182451.7873
110 | 2575476.4163 | 1182426.5897
111 | 2575490.0389 | 1182493.7039
112 | 2575479.2297 | 1182493.6155
113 | 2575468.5898 | 1182493.5286
114 | 2575432.0809 | 1182432.3017
115 | 2575429.2773 | 1182438.7926
116 | 2575434.3486 | 1182427.0517
117 | 2575427.8595 | 1182442.0751
118 | 2575425.1874 | 1182446.7468
119 | 2575441.2667 | 1182448.4335
120 | 2575414.6288 | 1182461.1468
121 | 2575414.4508 | 1182462.1297
122 | 2575414.3277 | 1182471.1682
123 | 2575414.703 | 1182477.0141
124 | 2575450.8684 | 1182478.9291
125 | 2575432.7773 | 1182503.4869
126 | 2575416.9466 | 1182486.4857
127 | 2575306.8187 | 1182441.7854

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98206 | -0.34419 | 0.0070878 | 0.0017764
1 | 0.98209 | -0.34367 | 0 | 0
2 | 0.98114 | -0.362 | 0 | 0
3 | 0.9828 | -0.32972 | 0 | 0
4 | 0.98108 | -0.36333 | 0 | 0
5 | 0.98106 | -0.36368 | 0.0021741 | 0.00054487
6 | 0.98105 | -0.36392 | 0.011724 | 0.0029384
7 | 0.98275 | -0.3308 | 0 | 0
8 | 0.98368 | -0.31273 | 0 | 0
9 | 0.98401 | -0.30636 | 0 | 0
10 | 0.98003 | -0.38362 | 0.0046094 | 0.0011552
11 | 0.98264 | -0.33287 | 0.0068092 | 0.0017066
12 | 0.99742 | -0.049016 | 0.010404 | 0.0026075
13 | 0.99764 | -0.04469 | 0 | 0
14 | 0.99467 | -0.10125 | 0.0082585 | 0.0020698
15 | 0.99484 | -0.098069 | 0 | 0
16 | 0.98532 | -0.28099 | 0 | 0
17 | 0.98366 | -0.31315 | 0.0026427 | 0.00066233
18 | 0.97947 | -0.39467 | 0.0048477 | 0.0012149
19 | 0.97837 | -0.41612 | 0 | 0
20 | 0.97941 | -0.39587 | 0.0039533 | 0.00099078
21 | 0.9783 | -0.4174 | 0.0036457 | 0.00091371
22 | 0.97739 | -0.43522 | 0.0048453 | 0.0012144
23 | 0.99702 | -0.057229 | 0.0065332 | 0.0016374
24 | 0.99702 | -0.057179 | 0.0065337 | 0.0016375
25 | 0.99728 | -0.052247 | 0 | 0
26 | 0.99743 | -0.049455 | 0.0047726 | 0.0011961
27 | 0.99603 | -0.076252 | 0 | 0
28 | 0.99511 | -0.094 | 0 | 0
29 | 0.9969 | -0.059518 | 0.0065332 | 0.0016374
30 | 0.99752 | -0.0476 | 0.0047726 | 0.0011961
31 | 0.99032 | -0.18485 | 0.0035485 | 0.00088933
32 | 0.99036 | -0.1841 | 0 | 0
33 | 0.9978 | -0.041742 | 0 | 0
34 | 0.99463 | -0.10334 | 0.025036 | 0.0062746
35 | 0.99476 | -0.10087 | 0.0084722 | 0.0021233
36 | 0.9969 | -0.059463 | 0.0065337 | 0.0016375
37 | 0.99764 | -0.045249 | 0.004777 | 0.0011972
38 | 0.99039 | -0.18334 | 0 | 0
39 | 0.99472 | -0.1015 | 0.0084159 | 0.0021092
40 | 0.9969 | -0.058784 | 0.0095436 | 0.0023919
41 | 0.99942 | -0.010968 | 0.0047756 | 0.0011969
42 | 0.99691 | -0.0594 | 0.0065332 | 0.0016374
43 | 0.99691 | -0.059332 | 0.0065399 | 0.0016391
44 | 0.99832 | -0.032179 | 0 | 0
45 | 0.99816 | -0.035224 | 0.004777 | 0.0011972
46 | 0.99874 | -0.02422 | 0.004777 | 0.0011972
47 | 0.99779 | -0.042402 | 0.0047726 | 0.0011961
48 | 0.99797 | -0.039061 | 0.0047726 | 0.0011961
49 | 0.99588 | -0.078304 | 0.0035485 | 0.00088934
50 | 1 | 0 | -0.44337 | -0.11255
51 | 0.99936 | -0.012349 | 0.004768 | 0.001195
52 | 0.99044 | -0.18253 | 0.004904 | 0.0012291
53 | 0.99048 | -0.18167 | 0.0049036 | 0.001229
54 | 0.99055 | -0.18031 | 0.0049041 | 0.0012291
55 | 0.99065 | -0.17843 | 0.0049036 | 0.001229
56 | 0.9879 | -0.23139 | 0 | 0
57 | 0.98729 | -0.24341 | 0 | 0
58 | 0.98839 | -0.2219 | 0.0039861 | 0.00099901
59 | 0.99077 | -0.17608 | 0.0049041 | 0.0012291
60 | 0.99161 | -0.15991 | 0.0035485 | 0.00088933
61 | 0.99163 | -0.15954 | 0.0035519 | 0.00089018
62 | 0.98681 | -0.25271 | 0.0039861 | 0.00099901
63 | 0.98871 | -0.21577 | 0.0042078 | 0.0010546
64 | 0.99586 | -0.078599 | 0.0035519 | 0.00089019
65 | 0.97706 | -0.44171 | 0 | 0
66 | 0.99105 | -0.17057 | 0 | 0
67 | 0.99167 | -0.15879 | 0.0035485 | 0.00088933
68 | 0.99194 | -0.15358 | 0.0035485 | 0.00088933
69 | 0.99057 | -0.17977 | 0.0049083 | 0.0012301
70 | 0.99173 | -0.15767 | 0.003547 | 0.00088897
71 | 0.9918 | -0.15618 | 0.0035488 | 0.00088941
72 | 0.99243 | -0.14413 | 0.003547 | 0.00088897
73 | 0.99042 | -0.18281 | 0.0052771 | 0.0013226
74 | 0.99293 | -0.13466 | 0.0035488 | 0.00088942
75 | 0.98968 | -0.19705 | 0 | 0
76 | 0.99343 | -0.12507 | 0.003547 | 0.00088897
77 | 0.98885 | -0.21298 | 0.0052703 | 0.0013209
78 | 0.98946 | -0.2012 | 0.0044223 | 0.0011083
79 | 0.98845 | -0.2206 | 0.0052703 | 0.0013209
80 | 0.98907 | -0.20885 | 0.0041738 | 0.001046
81 | 0.98742 | -0.24032 | 0.0020909 | 0.00052404
82 | 0.98706 | -0.24733 | 0.0020898 | 0.00052374
83 | 0.98671 | -0.25401 | 0.0020909 | 0.00052404
84 | 0.98636 | -0.26079 | 0.0020895 | 0.00052369
85 | 0.98334 | -0.31934 | 0.0026405 | 0.00066176
86 | 0.98338 | -0.31871 | 0.0026435 | 0.00066252
87 | 0.98332 | -0.31974 | 0.0028926 | 0.00072496
88 | 0.98342 | -0.31779 | 0.0026405 | 0.00066176
89 | 0.98349 | -0.31648 | 0.0026429 | 0.00066238
90 | 0.98357 | -0.31497 | 0.0026412 | 0.00066196
91 | 0.98561 | -0.276 | 0.0020898 | 0.00052374
92 | 0.98563 | -0.27569 | 0.0020909 | 0.00052404
93 | 0.98656 | -0.25756 | 0.0042054 | 0.001054
94 | 0.98634 | -0.2619 | 0.0041766 | 0.0010468
95 | 0.98614 | -0.2657 | 0.0044195 | 0.0011076
96 | 0.98594 | -0.26971 | 0.0039859 | 0.00099897
97 | 0.98567 | -0.27482 | 0.0024265 | 0.00060815
98 | 0.98573 | -0.27374 | 0.0041785 | 0.0010472
99 | 0.98582 | -0.27203 | 0.0042078 | 0.0010546
100 | 0.97448 | -0.4925 | 0.0033501 | 0.00083961
101 | 0.97518 | -0.47866 | 0 | 0
102 | 0.97429 | -0.49625 | 0 | 0
103 | 0.97422 | -0.49765 | 0 | 0
104 | 0.97399 | -0.50221 | 0.0030804 | 0.00077202
105 | 0.97365 | -0.50872 | 0 | 0
106 | 0.97416 | -0.49873 | 0.0023739 | 0.00059495
107 | 0.97398 | -0.50224 | 0.0030811 | 0.00077219
108 | 0.97358 | -0.51018 | 0.0026418 | 0.0006621
109 | 0.97325 | -0.51667 | 0.0034237 | 0.00085807
110 | 0.9741 | -0.49986 | 0.0030359 | 0.00076087
111 | 0.97395 | -0.50286 | 0.0035922 | 0.0009003
112 | 0.97388 | -0.50428 | 0.0035245 | 0.00088332
113 | 0.97384 | -0.50499 | 0.0036235 | 0.00090812
114 | 0.97251 | -0.5313 | 0.0023018 | 0.00057689
115 | 0.97256 | -0.53027 | 0.0027175 | 0.00068107
116 | 0.97248 | -0.53189 | 0.0056009 | 0.0014037
117 | 0.9726 | -0.52957 | 0 | 0
118 | 0.9725 | -0.53146 | 0.0027657 | 0.00069314
119 | 0.97301 | -0.52146 | 0.003354 | 0.00084058
120 | 0.97222 | -0.53696 | 0.0029873 | 0.00074868
121 | 0.97221 | -0.5372 | 0.002204 | 0.00055237
122 | 0.97211 | -0.53918 | 0.0022583 | 0.00056599
123 | 0.97206 | -0.54013 | 0.0026936 | 0.00067508
124 | 0.97356 | -0.51051 | 0.0026661 | 0.00066818
125 | 0.97193 | -0.54283 | 0.0030792 | 0.00077171
126 | 0.97201 | -0.54125 | 0.0030638 | 0.00076787
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0070878 | -0.0017764 | 0.007088 | 0.0017764 | 1.7795e-07 | 6.1828e-08 | 0.010739 | 0.010739 | 0.010739 | 0.98206 | -0.34419 | 0.98209 | -0.34367 | 2.9504
1 | 0.10387 | 0.026268 | -0.10377 | -0.026211 | 9.1272e-05 | 5.7297e-05 | 0.15746 | 0.15746 | 0.15746 | 0.98209 | -0.34367 | 0.98114 | -0.362 | 14.4192
2 | -0.11095 | -0.028044 | 0.11103 | 0.028091 | 7.4278e-05 | 4.674e-05 | 0.1682 | 0.1682 | 0.1682 | 0.98209 | -0.34367 | 0.9828 | -0.32972 | 15.4026
3 | 0.1016 | 0.025666 | -0.10159 | -0.02566 | 9.3367e-06 | 5.8565e-06 | 0.15416 | 0.15416 | 0.15416 | 0.98114 | -0.362 | 0.98105 | -0.36392 | 14.1172
4 | 0.0021742 | 0.00054444 | -0.0021741 | -0.00054478 | 1.3717e-07 | -3.3707e-07 | 0.0032973 | 0.0032974 | 0.0032974 | 0.98114 | -0.362 | 0.98108 | -0.36333 | 0.90589
5 | 0.0068103 | 0.0017069 | -0.0068099 | -0.0017068 | 3.5065e-07 | 1.1297e-07 | 0.010311 | 0.010311 | 0.010311 | 0.9828 | -0.32972 | 0.98275 | -0.3308 | 2.8327
6 | -0.11784 | -0.029798 | 0.11793 | 0.029859 | 9.6088e-05 | 6.0579e-05 | 0.17851 | 0.17851 | 0.17851 | 0.9828 | -0.32972 | 0.98368 | -0.31273 | 16.3468
7 | 0.0021741 | 0.00054478 | -0.0021741 | -0.00054487 | 3.6196e-08 | -8.8926e-08 | 0.0032974 | 0.0032975 | 0.0032975 | 0.98108 | -0.36333 | 0.98106 | -0.36368 | 0.9059
8 | 0.089866 | 0.022722 | -0.089781 | -0.022669 | 8.4808e-05 | 5.2897e-05 | 0.13638 | 0.13638 | 0.13638 | 0.98105 | -0.36392 | 0.98003 | -0.38362 | 12.4888
9 | 0.0068099 | 0.0017068 | -0.0068092 | -0.0017066 | 6.7122e-07 | 2.1629e-07 | 0.010311 | 0.010311 | 0.010311 | 0.98275 | -0.3308 | 0.98264 | -0.33287 | 2.8328
10 | -0.11793 | -0.029859 | 0.11797 | 0.029881 | 3.6079e-05 | 2.2745e-05 | 0.17851 | 0.17851 | 0.17851 | 0.98368 | -0.31273 | 0.98401 | -0.30636 | 16.3468
11 | -0.13672 | -0.034584 | 0.13689 | 0.03469 | 0.00016668 | 0.00010548 | 0.20687 | 0.20687 | 0.20687 | 0.98401 | -0.30636 | 0.98532 | -0.28099 | 18.9439
12 | 0.018754 | 0.0047031 | -0.018748 | -0.0046995 | 6.0693e-06 | 3.6288e-06 | 0.02836 | 0.02836 | 0.02836 | 0.98401 | -0.30636 | 0.98366 | -0.31315 | 7.7913
13 | 0.085172 | 0.021514 | -0.085127 | -0.021486 | 4.5094e-05 | 2.8046e-05 | 0.12938 | 0.12938 | 0.12938 | 0.98003 | -0.38362 | 0.97947 | -0.39467 | 11.8479
14 | -0.010404 | -0.0026075 | 0.010406 | 0.0026085 | 2.1447e-06 | 1.0627e-06 | 0.015521 | 0.015521 | 0.015521 | 0.99742 | -0.049016 | 0.99764 | -0.04469 | 4.2641
15 | -0.010406 | -0.0026085 | 0.010408 | 0.0026093 | 1.4618e-06 | 7.2423e-07 | 0.015521 | 0.015521 | 0.015521 | 0.99764 | -0.04469 | 0.9978 | -0.041742 | 4.2641
16 | -0.0082585 | -0.0020698 | 0.0082597 | 0.0020703 | 1.2532e-06 | 5.1781e-07 | 0.012355 | 0.012354 | 0.012355 | 0.99467 | -0.10125 | 0.99484 | -0.098069 | 3.3941
17 | -0.28875 | -0.073497 | 0.28902 | 0.07367 | 0.00027132 | 0.00017319 | 0.43229 | 0.43229 | 0.43229 | 0.99484 | -0.098069 | 0.99586 | -0.078599 | 39.5869
18 | 0.28049 | 0.071427 | -0.28012 | -0.071194 | 0.00036477 | 0.00023281 | 0.41993 | 0.41993 | 0.41993 | 0.99484 | -0.098069 | 0.99343 | -0.12507 | 38.4556
19 | -0.13689 | -0.03469 | 0.13702 | 0.034774 | 0.00013294 | 8.4131e-05 | 0.20687 | 0.20687 | 0.20687 | 0.98532 | -0.28099 | 0.98636 | -0.26079 | 18.9438
20 | 0.016105 | 0.0040371 | -0.016103 | -0.0040363 | 1.3915e-06 | 8.1123e-07 | 0.024363 | 0.024363 | 0.024363 | 0.98366 | -0.31315 | 0.98357 | -0.31497 | 6.693
21 | 0.076325 | 0.01928 | -0.076247 | -0.019232 | 7.8395e-05 | 4.8415e-05 | 0.11601 | 0.11601 | 0.11601 | 0.97947 | -0.39467 | 0.97837 | -0.41612 | 10.6236
22 | 0.0039535 | 0.00099072 | -0.0039533 | -0.00099078 | 2.2538e-07 | -6.5434e-08 | 0.0060062 | 0.0060062 | 0.0060062 | 0.97947 | -0.39467 | 0.97941 | -0.39587 | 1.6501
23 | 0.003646 | 0.00091361 | -0.0036457 | -0.00091371 | 2.2205e-07 | -9.9698e-08 | 0.0055451 | 0.0055452 | 0.0055452 | 0.97837 | -0.41612 | 0.9783 | -0.4174 | 1.5234
24 | 0.072601 | 0.018318 | -0.072535 | -0.018277 | 6.6323e-05 | 4.081e-05 | 0.11046 | 0.11046 | 0.11046 | 0.97837 | -0.41612 | 0.97739 | -0.43522 | 10.1158
25 | 0.067689 | 0.017063 | -0.067668 | -0.01705 | 2.1033e-05 | 1.2866e-05 | 0.10309 | 0.10309 | 0.10309 | 0.97739 | -0.43522 | 0.97706 | -0.44171 | 9.4403
26 | -0.0065332 | -0.0016374 | 0.0065332 | 0.0016374 | 1.5583e-08 | 4.2726e-09 | 0.0097505 | 0.0097505 | 0.0097505 | 0.99702 | -0.057229 | 0.99702 | -0.057179 | 2.6787
27 | -0.013067 | -0.0032749 | 0.01307 | 0.0032766 | 3.0709e-06 | 1.6845e-06 | 0.019502 | 0.019502 | 0.019502 | 0.99702 | -0.057179 | 0.99728 | -0.052247 | 5.3576
28 | -0.01307 | -0.0032766 | 0.013072 | 0.0032775 | 1.7389e-06 | 9.5376e-07 | 0.019502 | 0.019502 | 0.019502 | 0.99728 | -0.052247 | 0.99743 | -0.049455 | 5.3576
29 | -0.017844 | -0.0044736 | 0.017846 | 0.0044746 | 1.5771e-06 | 9.3187e-07 | 0.026622 | 0.026622 | 0.026622 | 0.99743 | -0.049455 | 0.99752 | -0.0476 | 7.3136
30 | 0.041976 | 0.01054 | -0.041941 | -0.010517 | 3.551e-05 | 2.2413e-05 | 0.062717 | 0.062717 | 0.062717 | 0.99603 | -0.076252 | 0.99511 | -0.094 | 17.2301
31 | -0.041976 | -0.01054 | 0.04201 | 0.010561 | 3.3538e-05 | 2.1168e-05 | 0.062717 | 0.062717 | 0.062717 | 0.99603 | -0.076252 | 0.9969 | -0.059518 | 17.23
32 | 0.025047 | 0.0062814 | -0.025036 | -0.0062746 | 1.1146e-05 | 6.8583e-06 | 0.037455 | 0.037455 | 0.037455 | 0.99511 | -0.094 | 0.99463 | -0.10334 | 10.2898
33 | 0.016894 | 0.0042359 | -0.016888 | -0.0042327 | 5.53e-06 | 3.2391e-06 | 0.025263 | 0.025263 | 0.025263 | 0.99511 | -0.094 | 0.99476 | -0.10087 | 6.9403
34 | -0.048543 | -0.012198 | 0.048543 | 0.012198 | 1.2799e-07 | 8.1069e-08 | 0.072469 | 0.072469 | 0.072469 | 0.9969 | -0.059518 | 0.9969 | -0.059463 | 19.9091
35 | -0.022618 | -0.0056707 | 0.022621 | 0.0056722 | 2.5345e-06 | 1.5446e-06 | 0.033741 | 0.033741 | 0.033741 | 0.99752 | -0.0476 | 0.99764 | -0.045249 | 9.2695
36 | -0.0035485 | -0.00088933 | 0.0035486 | 0.00088925 | 1.2782e-07 | -7.2472e-08 | 0.0053318 | 0.0053317 | 0.0053318 | 0.99032 | -0.18485 | 0.99036 | -0.1841 | 1.4648
37 | -0.0035486 | -0.00088925 | 0.0035487 | 0.00088918 | 1.2795e-07 | -7.2564e-08 | 0.0053317 | 0.0053317 | 0.0053317 | 0.99036 | -0.1841 | 0.99039 | -0.18334 | 1.4648
38 | 0.3062 | 0.078184 | -0.30594 | -0.078023 | 0.00025198 | 0.00016089 | 0.45714 | 0.45714 | 0.45714 | 0.9978 | -0.041742 | 0.9969 | -0.058784 | 41.8629
39 | -0.3166 | -0.080793 | 0.31708 | 0.081094 | 0.00047144 | 0.00030106 | 0.47266 | 0.47266 | 0.47266 | 0.9978 | -0.041742 | 0.99942 | -0.010968 | 43.2842
40 | 0.0084162 | 0.0021093 | -0.0084159 | -0.0021092 | 2.5177e-07 | 1.0614e-07 | 0.012589 | 0.012589 | 0.012589 | 0.99476 | -0.10087 | 0.99472 | -0.1015 | 3.4586
41 | -0.055077 | -0.013836 | 0.055077 | 0.013836 | 1.6476e-07 | 1.046e-07 | 0.082221 | 0.082221 | 0.082221 | 0.9969 | -0.059463 | 0.99691 | -0.0594 | 22.5883
42 | -0.027398 | -0.0068694 | 0.027402 | 0.0068717 | 3.7179e-06 | 2.3019e-06 | 0.040866 | 0.040866 | 0.040866 | 0.99764 | -0.045249 | 0.99779 | -0.042402 | 11.2269
43 | -0.0035487 | -0.00088918 | 0.0035489 | 0.0008891 | 1.3678e-07 | -7.7588e-08 | 0.0053317 | 0.0053316 | 0.0053317 | 0.99039 | -0.18334 | 0.99044 | -0.18253 | 1.4647
44 | 0.2964 | 0.075631 | -0.29612 | -0.075453 | 0.0002792 | 0.00017824 | 0.4429 | 0.4429 | 0.4429 | 0.9969 | -0.058784 | 0.99588 | -0.078304 | 40.5584
45 | -0.32185 | -0.082291 | 0.32202 | 0.0824 | 0.00017089 | 0.00010914 | 0.47977 | 0.47977 | 0.47977 | 0.99942 | -0.010968 | 1 | 0 | 43.9353
46 | -0.06161 | -0.015473 | 0.061611 | 0.015473 | 2.0038e-07 | 1.2742e-07 | 0.091973 | 0.091973 | 0.091973 | 0.99691 | -0.0594 | 0.99691 | -0.059332 | 25.2673
47 | -0.06815 | -0.017113 | 0.068239 | 0.017169 | 8.8409e-05 | 5.6285e-05 | 0.10173 | 0.10173 | 0.10173 | 0.99691 | -0.059332 | 0.99832 | -0.032179 | 27.9491
48 | 0.041742 | 0.010472 | -0.041736 | -0.010469 | 6.0605e-06 | 3.8241e-06 | 0.062221 | 0.062221 | 0.062221 | 0.99832 | -0.032179 | 0.99816 | -0.035224 | 17.0936
49 | -0.10998 | -0.027641 | 0.11002 | 0.027668 | 4.1803e-05 | 2.67e-05 | 0.16396 | 0.16396 | 0.16396 | 0.99832 | -0.032179 | 0.99874 | -0.02422 | 45.0426
50 | 0.036959 | 0.0092714 | -0.036952 | -0.0092672 | 6.7589e-06 | 4.2481e-06 | 0.055099 | 0.055099 | 0.055099 | 0.99816 | -0.035224 | 0.99797 | -0.039061 | 15.1372
51 | -0.1148 | -0.028865 | 0.11486 | 0.028907 | 6.5124e-05 | 4.1601e-05 | 0.17107 | 0.17107 | 0.17107 | 0.99874 | -0.02422 | 0.99936 | -0.012349 | 46.9979
52 | -0.032174 | -0.0080679 | 0.032179 | 0.0080711 | 5.1235e-06 | 3.2015e-06 | 0.047983 | 0.047983 | 0.047983 | 0.99779 | -0.042402 | 0.99797 | -0.039061 | 13.1822
53 | 0.29257 | 0.074563 | -0.29257 | -0.074561 | 4.1737e-06 | 2.6644e-06 | 0.4376 | 0.4376 | 0.4376 | 0.99588 | -0.078304 | 0.99586 | -0.078599 | 40.0729
54 | 0.1197 | 0.030147 | -0.11963 | -0.030102 | 7.0641e-05 | 4.5132e-05 | 0.17817 | 0.17817 | 0.17817 | 1 | 0 | 0.99936 | -0.012349 | 48.9483
55 | -0.0084529 | -0.0021182 | 0.0084532 | 0.0021183 | 3.4627e-07 | 1.4792e-07 | 0.012699 | 0.012699 | 0.012699 | 0.99044 | -0.18253 | 0.99048 | -0.18167 | 3.4888
56 | -0.013357 | -0.0033473 | 0.013358 | 0.0033478 | 8.6452e-07 | 4.796e-07 | 0.020066 | 0.020066 | 0.020066 | 0.99048 | -0.18167 | 0.99055 | -0.18031 | 5.5127
57 | -0.018262 | -0.0045768 | 0.018263 | 0.0045778 | 1.6347e-06 | 9.7161e-07 | 0.027433 | 0.027433 | 0.027433 | 0.99055 | -0.18031 | 0.99065 | -0.17843 | 7.5366
58 | -0.023167 | -0.0058068 | 0.02317 | 0.0058084 | 2.5999e-06 | 1.5902e-06 | 0.034799 | 0.034799 | 0.034799 | 0.99065 | -0.17843 | 0.99077 | -0.17608 | 9.5601
59 | 0.035827 | 0.0090012 | -0.035807 | -0.0089883 | 2.0549e-05 | 1.2911e-05 | 0.053972 | 0.053972 | 0.053972 | 0.9879 | -0.23139 | 0.98729 | -0.24341 | 14.8276
60 | -0.035827 | -0.0090012 | 0.035844 | 0.0090114 | 1.6236e-05 | 1.0201e-05 | 0.053972 | 0.053972 | 0.053972 | 0.9879 | -0.23139 | 0.98839 | -0.2219 | 14.8276
61 | 0.035807 | 0.0089883 | -0.035791 | -0.0089783 | 1.5868e-05 | 9.9696e-06 | 0.053972 | 0.053972 | 0.053972 | 0.98729 | -0.24341 | 0.98681 | -0.25271 | 14.8276
62 | -0.03983 | -0.01001 | 0.039841 | 0.010018 | 1.1652e-05 | 7.3465e-06 | 0.059973 | 0.059973 | 0.059973 | 0.98839 | -0.2219 | 0.98871 | -0.21577 | 16.4762
63 | -0.028074 | -0.0070375 | 0.028081 | 0.007042 | 7.3703e-06 | 4.5746e-06 | 0.042164 | 0.042164 | 0.042164 | 0.99077 | -0.17608 | 0.99105 | -0.17057 | 11.5835
64 | -0.0035485 | -0.00088933 | 0.0035485 | 0.00088929 | 6.3136e-08 | -3.6194e-08 | 0.0053248 | 0.0053248 | 0.0053248 | 0.99161 | -0.15991 | 0.99163 | -0.15954 | 1.4629
65 | -0.0071004 | -0.0017795 | 0.0071007 | 0.0017796 | 2.5278e-07 | 8.5174e-08 | 0.010655 | 0.010655 | 0.010655 | 0.99163 | -0.15954 | 0.99167 | -0.15879 | 2.9271
66 | 0.031805 | 0.0079793 | -0.031798 | -0.0079747 | 7.3481e-06 | 4.594e-06 | 0.047962 | 0.047962 | 0.047962 | 0.98681 | -0.25271 | 0.98656 | -0.25756 | 13.1763
67 | -0.044049 | -0.011072 | 0.044064 | 0.011082 | 1.4563e-05 | 9.2072e-06 | 0.066306 | 0.066306 | 0.066306 | 0.98871 | -0.21577 | 0.98907 | -0.20885 | 18.216
68 | 0.067668 | 0.01705 | -0.067549 | -0.016975 | 0.00011935 | 7.4889e-05 | 0.10309 | 0.10309 | 0.10309 | 0.97706 | -0.44171 | 0.97518 | -0.47866 | 14.1605
69 | -0.2476 | -0.06282 | 0.24781 | 0.062949 | 0.00020248 | 0.00012913 | 0.37204 | 0.37204 | 0.37204 | 0.99105 | -0.17057 | 0.99194 | -0.15358 | 34.0693
70 | 0.21952 | 0.055778 | -0.21943 | -0.055716 | 9.7225e-05 | 6.1948e-05 | 0.32987 | 0.32987 | 0.32987 | 0.99105 | -0.17057 | 0.99057 | -0.17977 | 30.2082
71 | -0.010649 | -0.0026689 | 0.01065 | 0.0026692 | 5.6826e-07 | 2.8711e-07 | 0.015979 | 0.015979 | 0.015979 | 0.99167 | -0.15879 | 0.99173 | -0.15767 | 4.3899
72 | -0.2691 | -0.068288 | 0.26923 | 0.068366 | 0.00012241 | 7.8113e-05 | 0.40399 | 0.40399 | 0.40399 | 0.99194 | -0.15358 | 0.99243 | -0.14413 | 36.995
73 | 0.017749 | 0.0044494 | -0.017747 | -0.0044481 | 2.1941e-06 | 1.2977e-06 | 0.026625 | 0.026625 | 0.026625 | 0.99194 | -0.15358 | 0.9918 | -0.15618 | 7.3147
74 | 0.21452 | 0.054486 | -0.21449 | -0.054466 | 3.1305e-05 | 1.9942e-05 | 0.3225 | 0.3225 | 0.3225 | 0.99057 | -0.17977 | 0.99042 | -0.18281 | 29.533
75 | -0.014197 | -0.0035581 | 0.014198 | 0.0035587 | 1.0104e-06 | 5.7006e-07 | 0.021301 | 0.021301 | 0.021301 | 0.99173 | -0.15767 | 0.9918 | -0.15618 | 5.852
76 | -0.27277 | -0.069255 | 0.2729 | 0.069334 | 0.00012436 | 7.9359e-05 | 0.4093 | 0.4093 | 0.4093 | 0.99243 | -0.14413 | 0.99293 | -0.13466 | 37.482
77 | 0.20921 | 0.053143 | -0.20907 | -0.053052 | 0.0001433 | 9.1262e-05 | 0.31457 | 0.31457 | 0.31457 | 0.99042 | -0.18281 | 0.98968 | -0.19705 | 28.807
78 | -0.27645 | -0.070224 | 0.27657 | 0.070305 | 0.00012761 | 8.1441e-05 | 0.41462 | 0.41462 | 0.41462 | 0.99293 | -0.13466 | 0.99343 | -0.12507 | 37.969
79 | 0.15638 | 0.039798 | -0.15626 | -0.039722 | 0.00012004 | 7.6156e-05 | 0.23534 | 0.23534 | 0.23534 | 0.98968 | -0.19705 | 0.98885 | -0.21298 | 21.551
80 | 0.052688 | 0.013254 | -0.052678 | -0.013247 | 1.0446e-05 | 6.6286e-06 | 0.079236 | 0.079236 | 0.079236 | 0.98968 | -0.19705 | 0.98946 | -0.2012 | 21.7681
81 | 0.15099 | 0.038401 | -0.15093 | -0.038366 | 5.5369e-05 | 3.5107e-05 | 0.22741 | 0.22741 | 0.22741 | 0.98885 | -0.21298 | 0.98845 | -0.2206 | 20.8248
82 | 0.048255 | 0.012139 | -0.048238 | -0.012128 | 1.7639e-05 | 1.1174e-05 | 0.072585 | 0.072585 | 0.072585 | 0.98946 | -0.2012 | 0.98907 | -0.20885 | 19.941
83 | 0.14566 | 0.037045 | -0.14552 | -0.036958 | 0.00013826 | 8.7606e-05 | 0.21947 | 0.21947 | 0.21947 | 0.98845 | -0.2206 | 0.98742 | -0.24032 | 20.0982
84 | 0.14343 | 0.036434 | -0.14338 | -0.036403 | 4.8367e-05 | 3.0638e-05 | 0.21632 | 0.21632 | 0.21632 | 0.98742 | -0.24032 | 0.98706 | -0.24733 | 19.8097
85 | 0.14129 | 0.035879 | -0.14125 | -0.035851 | 4.5414e-05 | 2.8759e-05 | 0.21317 | 0.21317 | 0.21317 | 0.98706 | -0.24733 | 0.98671 | -0.25401 | 19.5212
86 | 0.13916 | 0.035327 | -0.13911 | -0.035298 | 4.5431e-05 | 2.876e-05 | 0.21002 | 0.21002 | 0.21002 | 0.98671 | -0.25401 | 0.98636 | -0.26079 | 19.2325
87 | -0.0055331 | -0.0013867 | 0.0055333 | 0.0013867 | 1.6465e-07 | 2.5922e-08 | 0.0083728 | 0.0083728 | 0.0083728 | 0.98334 | -0.31934 | 0.98338 | -0.31871 | 2.3002
88 | 0.0028927 | 0.0007249 | -0.0028926 | -0.00072496 | 5.6033e-08 | -6.3067e-08 | 0.0043772 | 0.0043773 | 0.0043773 | 0.98334 | -0.31934 | 0.98332 | -0.31974 | 1.2026
89 | -0.0081768 | -0.0020492 | 0.0081771 | 0.0020494 | 3.5955e-07 | 1.5065e-07 | 0.012373 | 0.012373 | 0.012373 | 0.98338 | -0.31871 | 0.98342 | -0.31779 | 3.3991
90 | -0.010818 | -0.0027111 | 0.010818 | 0.0027115 | 6.72e-07 | 3.4521e-07 | 0.016368 | 0.016368 | 0.016368 | 0.98342 | -0.31779 | 0.98349 | -0.31648 | 4.4967
91 | -0.013461 | -0.0033738 | 0.013462 | 0.0033744 | 9.7247e-07 | 5.4304e-07 | 0.020367 | 0.020367 | 0.020367 | 0.98349 | -0.31648 | 0.98357 | -0.31497 | 5.5953
92 | -0.0020898 | -0.00052374 | 0.0020898 | 0.00052366 | 3.1279e-08 | -8.6777e-08 | 0.003155 | 0.003155 | 0.003155 | 0.98561 | -0.276 | 0.98563 | -0.27569 | 0.86676
93 | -0.0041807 | -0.0010477 | 0.0041809 | 0.0010477 | 1.7275e-07 | -3.6827e-08 | 0.0063117 | 0.0063116 | 0.0063117 | 0.98563 | -0.27569 | 0.98567 | -0.27482 | 1.734
94 | 0.027592 | 0.0069208 | -0.027586 | -0.0069172 | 5.7171e-06 | 3.5466e-06 | 0.041619 | 0.041619 | 0.041619 | 0.98656 | -0.25756 | 0.98634 | -0.2619 | 11.4338
95 | 0.02341 | 0.0058705 | -0.023406 | -0.0058679 | 4.2383e-06 | 2.5969e-06 | 0.035318 | 0.035318 | 0.035318 | 0.98634 | -0.2619 | 0.98614 | -0.2657 | 9.7028
96 | 0.018986 | 0.0047602 | -0.018982 | -0.0047581 | 3.6274e-06 | 2.1712e-06 | 0.028649 | 0.028649 | 0.028649 | 0.98614 | -0.2657 | 0.98594 | -0.26971 | 7.8707
97 | 0.014997 | 0.0037591 | -0.014995 | -0.0037581 | 1.6582e-06 | 9.5119e-07 | 0.022634 | 0.022634 | 0.022634 | 0.98594 | -0.26971 | 0.98582 | -0.27203 | 6.2181
98 | -0.0066074 | -0.0016558 | 0.0066078 | 0.0016559 | 3.3826e-07 | 1.0092e-07 | 0.0099748 | 0.0099748 | 0.0099748 | 0.98567 | -0.27482 | 0.98573 | -0.27374 | 2.7403
99 | -0.010786 | -0.0027031 | 0.010787 | 0.0027036 | 8.7869e-07 | 4.4969e-07 | 0.016282 | 0.016282 | 0.016282 | 0.98573 | -0.27374 | 0.98582 | -0.27203 | 4.4732
100 | -0.02026 | -0.0050805 | 0.020274 | 0.0050886 | 1.3375e-05 | 8.0956e-06 | 0.030939 | 0.030938 | 0.030939 | 0.97448 | -0.4925 | 0.97518 | -0.47866 | 8.4996
101 | 0.01691 | 0.0042409 | -0.016907 | -0.0042391 | 3.0194e-06 | 1.782e-06 | 0.025823 | 0.025823 | 0.025823 | 0.97448 | -0.4925 | 0.97429 | -0.49625 | 7.0942
102 | 0.047275 | 0.011887 | -0.047232 | -0.01186 | 4.284e-05 | 2.6323e-05 | 0.07215 | 0.072151 | 0.072151 | 0.97518 | -0.47866 | 0.97422 | -0.49765 | 9.9108
103 | 0.016907 | 0.0042391 | -0.016903 | -0.0042362 | 4.8007e-06 | 2.8335e-06 | 0.025823 | 0.025823 | 0.025823 | 0.97429 | -0.49625 | 0.97399 | -0.50221 | 7.0943
104 | 0.041822 | 0.010505 | -0.0418 | -0.010491 | 2.2079e-05 | 1.3951e-05 | 0.063887 | 0.063887 | 0.063887 | 0.97422 | -0.49765 | 0.97365 | -0.50872 | 17.5515
105 | 0.0054102 | 0.0013557 | -0.00541 | -0.0013557 | 2.7827e-07 | 4.2793e-08 | 0.0082635 | 0.0082636 | 0.0082636 | 0.97422 | -0.49765 | 0.97416 | -0.49873 | 2.2702
106 | 0.013822 | 0.0034642 | -0.013822 | -0.0034642 | 2.1993e-08 | 1.2438e-08 | 0.021117 | 0.021117 | 0.021117 | 0.97399 | -0.50221 | 0.97398 | -0.50224 | 5.8014
107 | 0.0053083 | 0.0013303 | -0.0053079 | -0.0013302 | 3.6836e-07 | 5.0134e-08 | 0.0081125 | 0.0081125 | 0.0081125 | 0.97365 | -0.50872 | 0.97358 | -0.51018 | 2.2287
108 | 0.036492 | 0.0091604 | -0.036478 | -0.0091517 | 1.3839e-05 | 8.7092e-06 | 0.055775 | 0.055775 | 0.055775 | 0.97365 | -0.50872 | 0.97325 | -0.51667 | 15.3228
109 | 0.0030361 | 0.00076073 | -0.0030359 | -0.00076087 | 1.6298e-07 | -1.4727e-07 | 0.0046375 | 0.0046376 | 0.0046376 | 0.97416 | -0.49873 | 0.9741 | -0.49986 | 1.2741
110 | 0.010741 | 0.002692 | -0.010741 | -0.0026919 | 3.1872e-07 | 1.647e-07 | 0.01641 | 0.01641 | 0.01641 | 0.97398 | -0.50224 | 0.97395 | -0.50286 | 4.5082
111 | 0.0026661 | 0.00066812 | -0.0026661 | -0.00066818 | 4.2456e-08 | -5.7616e-08 | 0.0040748 | 0.0040749 | 0.0040749 | 0.97358 | -0.51018 | 0.97356 | -0.51051 | 1.1195
112 | 0.033054 | 0.0082936 | -0.033047 | -0.0082889 | 7.5381e-06 | 4.7266e-06 | 0.05054 | 0.05054 | 0.05054 | 0.97325 | -0.51667 | 0.97301 | -0.52146 | 13.8847
113 | 0.0071486 | 0.0017916 | -0.0071481 | -0.0017914 | 4.8352e-07 | 1.7494e-07 | 0.010922 | 0.010922 | 0.010922 | 0.97395 | -0.50286 | 0.97388 | -0.50428 | 3.0005
114 | 0.0036236 | 0.00090807 | -0.0036235 | -0.00090812 | 1.2231e-07 | -5.4112e-08 | 0.0055365 | 0.0055366 | 0.0055366 | 0.97388 | -0.50428 | 0.97384 | -0.50499 | 1.521
115 | -0.0079029 | -0.0019806 | 0.0079033 | 0.0019808 | 3.8768e-07 | 1.6038e-07 | 0.012092 | 0.012092 | 0.012092 | 0.97251 | -0.5313 | 0.97256 | -0.53027 | 3.322
116 | 0.0056011 | 0.0014037 | -0.0056009 | -0.0014037 | 1.5751e-07 | 2.985e-08 | 0.0085701 | 0.0085701 | 0.0085701 | 0.97251 | -0.5313 | 0.97248 | -0.53189 | 2.3544
117 | -0.010621 | -0.0026619 | 0.010621 | 0.0026621 | 3.5406e-07 | 1.8222e-07 | 0.01625 | 0.01625 | 0.01625 | 0.97256 | -0.53027 | 0.9726 | -0.52957 | 4.4642
118 | 0.01906 | 0.0047791 | -0.019058 | -0.0047781 | 1.7163e-06 | 1.0316e-06 | 0.029161 | 0.029161 | 0.029161 | 0.9726 | -0.52957 | 0.9725 | -0.53146 | 8.0114
119 | -0.029681 | -0.0074411 | 0.029693 | 0.0074483 | 1.1475e-05 | 7.1597e-06 | 0.045411 | 0.045411 | 0.045411 | 0.9726 | -0.52957 | 0.97301 | -0.52146 | 12.4756
120 | 0.016293 | 0.0040849 | -0.016288 | -0.0040824 | 4.2693e-06 | 2.5051e-06 | 0.02493 | 0.02493 | 0.02493 | 0.9725 | -0.53146 | 0.97222 | -0.53696 | 6.8489
121 | 0.013301 | 0.0033337 | -0.013301 | -0.0033337 | 1.5523e-07 | 8.6964e-08 | 0.020358 | 0.020358 | 0.020358 | 0.97222 | -0.53696 | 0.97221 | -0.5372 | 5.5928
122 | 0.011097 | 0.0027813 | -0.011096 | -0.0027807 | 1.0439e-06 | 5.4845e-07 | 0.016984 | 0.016985 | 0.016985 | 0.97221 | -0.5372 | 0.97211 | -0.53918 | 4.6661
123 | 0.0088376 | 0.0022147 | -0.0088372 | -0.0022146 | 4.02e-07 | 1.8466e-07 | 0.013528 | 0.013528 | 0.013528 | 0.97211 | -0.53918 | 0.97206 | -0.54013 | 3.7164
124 | 0.0061436 | 0.0015395 | -0.0061432 | -0.0015394 | 3.2713e-07 | 8.7099e-08 | 0.0094044 | 0.0094044 | 0.0094044 | 0.97206 | -0.54013 | 0.97201 | -0.54125 | 2.5836
125 | -0.0030792 | -0.00077171 | 0.0030794 | 0.00077151 | 2.3088e-07 | -1.9561e-07 | 0.0047142 | 0.0047141 | 0.0047142 | 0.97193 | -0.54283 | 0.97201 | -0.54125 | 1.2951

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44815 | 0.11374

## res_load
| p_mw | q_mvar
0 | 0.0070878 | 0.0017764
1 | 0.0021741 | 0.00054487
2 | 0.011724 | 0.0029384
3 | 0.0046094 | 0.0011552
4 | 0.0068092 | 0.0017066
5 | 0.010404 | 0.0026075
6 | 0.0082585 | 0.0020698
7 | 0.0026427 | 0.00066233
8 | 0.0048477 | 0.0012149
9 | 0.0039533 | 0.00099078
10 | 0.0036457 | 0.00091371
11 | 0.0048453 | 0.0012144
12 | 0.0065332 | 0.0016374
13 | 0.0065337 | 0.0016375
14 | 0.0047726 | 0.0011961
15 | 0.0065332 | 0.0016374
16 | 0.0047726 | 0.0011961
17 | 0.0035485 | 0.00088933
18 | 0.025036 | 0.0062746
19 | 0.0084722 | 0.0021233
20 | 0.0065337 | 0.0016375
21 | 0.004777 | 0.0011972
22 | 0.0084159 | 0.0021092
23 | 0.0095436 | 0.0023919
24 | 0.0047756 | 0.0011969
25 | 0.0065332 | 0.0016374
26 | 0.0065399 | 0.0016391
27 | 0.004777 | 0.0011972
28 | 0.004777 | 0.0011972
29 | 0.0047726 | 0.0011961
30 | 0.0047726 | 0.0011961
31 | 0.0035485 | 0.00088934
32 | 0.004777 | 0.0011972
33 | 0.004768 | 0.001195
34 | 0.004904 | 0.0012291
35 | 0.0049036 | 0.001229
36 | 0.0049041 | 0.0012291
37 | 0.0049036 | 0.001229
38 | 0.0039861 | 0.00099901
39 | 0.0049041 | 0.0012291
40 | 0.0035485 | 0.00088933
41 | 0.0035519 | 0.00089018
42 | 0.0039861 | 0.00099901
43 | 0.0042078 | 0.0010546
44 | 0.0035519 | 0.00089019
45 | 0.0035485 | 0.00088933
46 | 0.0035485 | 0.00088933
47 | 0.0049083 | 0.0012301
48 | 0.003547 | 0.00088897
49 | 0.0035488 | 0.00088941
50 | 0.003547 | 0.00088897
51 | 0.0052771 | 0.0013226
52 | 0.0035488 | 0.00088942
53 | 0.003547 | 0.00088897
54 | 0.0052703 | 0.0013209
55 | 0.0044223 | 0.0011083
56 | 0.0052703 | 0.0013209
57 | 0.0041738 | 0.001046
58 | 0.0020909 | 0.00052404
59 | 0.0020898 | 0.00052374
60 | 0.0020909 | 0.00052404
61 | 0.0020895 | 0.00052369
62 | 0.0026405 | 0.00066176
63 | 0.0026435 | 0.00066252
64 | 0.0028926 | 0.00072496
65 | 0.0026405 | 0.00066176
66 | 0.0026429 | 0.00066238
67 | 0.0026412 | 0.00066196
68 | 0.0020898 | 0.00052374
69 | 0.0020909 | 0.00052404
70 | 0.0042054 | 0.001054
71 | 0.0041766 | 0.0010468
72 | 0.0044195 | 0.0011076
73 | 0.0039859 | 0.00099897
74 | 0.0024265 | 0.00060815
75 | 0.0041785 | 0.0010472
76 | 0.0042078 | 0.0010546
77 | 0.0033501 | 0.00083961
78 | 0.0030804 | 0.00077202
79 | 0.0023739 | 0.00059495
80 | 0.0030811 | 0.00077219
81 | 0.0026418 | 0.0006621
82 | 0.0034237 | 0.00085807
83 | 0.0030359 | 0.00076087
84 | 0.0035922 | 0.0009003
85 | 0.0035245 | 0.00088332
86 | 0.0036235 | 0.00090812
87 | 0.0023018 | 0.00057689
88 | 0.0027175 | 0.00068107
89 | 0.0056009 | 0.0014037
90 | 0.0027657 | 0.00069314
91 | 0.003354 | 0.00084058
92 | 0.0029873 | 0.00074868
93 | 0.002204 | 0.00055237
94 | 0.0022583 | 0.00056599
95 | 0.0026936 | 0.00067508
96 | 0.0026661 | 0.00066818
97 | 0.0030792 | 0.00077171
98 | 0.0030638 | 0.00076787

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1